## General
Interest rate (%) | 3
Currency | CHF
Exchange rate | 1
Optimization speed | medium
Scenario reference | esp-3a05d3f9-6696-4b3c-a413-393d
Solver version | V1
CO2 reduction target (%)
CO2 emissions of existing system (kg-CO2)

## Hubs
Hub number | Hub name
1 | Neighborhood

## Technology Packages
Package number | Package name

## Energy Carriers
Energy Carrier Name | Energy Carrier Code | Energy Carrier Type Code
Heat 60-70 °C | HEAT_7 | HEATING_ENERGY
Wood Pellets | WOOD_PELLETS | FUEL_SOLID
Oil | OIL | FUEL_LIQUID
Heat Ambient Export | HEAT_AMBIENT | HEATING_ENERGY
Heat 0-10 °C | HEAT_1 | HEATING_ENERGY
Heat 30-40 °C | HEAT_4 | HEATING_ENERGY
Gas | GAS | FUEL_GASEOUS
Plant Wast Heat | HEAT_2 | HEATING_ENERGY
Plant Waste Heat Export | HEAT_2 | HEATING_ENERGY
HT DH | HEAT_8 | HEATING_ENERGY
Cooling 10 - 20°C | COOLING_4 | COOLING_ENERGY
Heat Ambient | HEAT_AMBIENT | HEATING_ENERGY
LT RN | HEAT_1 | HEATING_ENERGY
Electricity | ELECTRICITY | ELECTRICAL_ENERGY
Solar Roof | SOLAR_ROOF | ON_SITE_RESOURCE

## Imports
Energy Carrier | Energy Price (CHF/kWh) | Capacity Price (CHF/kW/year) | Capacity Price (CHF/kW/month) | Fixed O&M Price (CHF/year) | CO2 Intensity (kg-CO2/kWh) | Total Annual Energy Available (kWh/year) | Maximum Hourly Energy Available (kWh/h) | Hubs
Gas | 0.06 | 0 | 0 | 0 | 0.245 |  |  | 1
Heat Ambient | 0 | 0 | 0 | 0 | 0 |  |  | 1
Wood Pellets | 0.085 | 0 | 0 | 0 | 0.0273 |  |  | 1
Plant Wast Heat | 0 | 0 | 0 | 0 | 0 |  |  | 1
Oil | 0.08 | 0 | 0 | 0 | 0.3 |  |  | 1
Electricity | 0.24 | 0 | 0 | 0 | 0.11 |  |  | 1

## Exports
Energy Carrier | Energy Price (CHF/kWh) | Capacity Price (CHF/kW/year) | Capacity Price (CHF/kW/month) | Fixed O&M Price (CHF/year) | CO2 Compensation (kg-CO2/kWh) | Hubs
Plant Waste Heat Export | 0 | 0 | 0 | 0 | 0 | 1
Electricity | 0.14 | 0 | 0 | 0 | 0 | 1
Heat Ambient Export | 0 | 0 | 0 | 0 | 0 | 1

## On-site Area
Energy carrier | Solar Roof
Resource type | Area
Technology dimensioning standard value (kW/m2 or kW/kWpeak) | 1
Hub
1 | 6500

## On-site Profiles
Energy carrier | Solar Roof
Hour
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 0
8 | 0
9 | 0.048
10 | 0.096
11 | 0.092
12 | 0.099
13 | 0.1
14 | 0.143
15 | 0.061
16 | 0.013
17 | 0
18 | 0
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
25 | 0
26 | 0
27 | 0
28 | 0
29 | 0
30 | 0
31 | 0
32 | 0
33 | 0.029
34 | 0.068
35 | 0.081
36 | 0.138
37 | 0.115
38 | 0.113
39 | 0.046
40 | 0.008
41 | 0
42 | 0
43 | 0
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0.017
58 | 0.102
59 | 0.073
60 | 0.03
61 | 0.049
62 | 0.043
63 | 0.052
64 | 0.019
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0.066
82 | 0.126
83 | 0.24901
84 | 0.235
85 | 0.201
86 | 0.151
87 | 0.046
88 | 0.018
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
99 | 0
100 | 0
101 | 0
102 | 0
103 | 0
104 | 0
105 | 0.09001
106 | 0.20701
107 | 0.29701
108 | 0.34102
109 | 0.33602
110 | 0.27101
111 | 0.17401
112 | 0.019
113 | 0
114 | 0
115 | 0
116 | 0
117 | 0
118 | 0
119 | 0
120 | 0
121 | 0
122 | 0
123 | 0
124 | 0
125 | 0
126 | 0
127 | 0
128 | 0
129 | 0.08301
130 | 0.19801
131 | 0.29801
132 | 0.32001
133 | 0.29501
134 | 0.22401
135 | 0.126
136 | 0.018
137 | 0
138 | 0
139 | 0
140 | 0
141 | 0
142 | 0
143 | 0
144 | 0
145 | 0
146 | 0
147 | 0
148 | 0
149 | 0
150 | 0
151 | 0
152 | 0
153 | 0.062
154 | 0.156
155 | 0.211
156 | 0.236
157 | 0.28001
158 | 0.27601
159 | 0.18001
160 | 0.022
161 | 0
162 | 0
163 | 0
164 | 0
165 | 0
166 | 0
167 | 0
168 | 0
169 | 0
170 | 0
171 | 0
172 | 0
173 | 0
174 | 0
175 | 0
176 | 0
177 | 0.081
178 | 0.139
179 | 0.206
180 | 0.186
181 | 0.189
182 | 0.28201
183 | 0.137
184 | 0.028
185 | 0
186 | 0
187 | 0
188 | 0
189 | 0
190 | 0
191 | 0
192 | 0
193 | 0
194 | 0
195 | 0
196 | 0
197 | 0
198 | 0
199 | 0
200 | 0
201 | 0.032
202 | 0.087
203 | 0.079
204 | 0.114
205 | 0.077
206 | 0.042
207 | 0.054
208 | 0.025
209 | 0
210 | 0
211 | 0
212 | 0
213 | 0
214 | 0
215 | 0
216 | 0
217 | 0
218 | 0
219 | 0
220 | 0
221 | 0
222 | 0
223 | 0
224 | 0
225 | 0.10001
226 | 0.22301
227 | 0.204
228 | 0.34001
229 | 0.32801
230 | 0.29201
231 | 0.12
232 | 0.032
233 | 0
234 | 0
235 | 0
236 | 0
237 | 0
238 | 0
239 | 0
240 | 0
241 | 0
242 | 0
243 | 0
244 | 0
245 | 0
246 | 0
247 | 0
248 | 0
249 | 0.024
250 | 0.068
251 | 0.186
252 | 0.059
253 | 0.201
254 | 0.21601
255 | 0.067
256 | 0.05404
257 | 0
258 | 0
259 | 0
260 | 0
261 | 0
262 | 0
263 | 0
264 | 0
265 | 0
266 | 0
267 | 0
268 | 0
269 | 0
270 | 0
271 | 0
272 | 0
273 | 0.033
274 | 0.143
275 | 0.136
276 | 0.224
277 | 0.11
278 | 0.23001
279 | 0.137
280 | 0.0278
281 | 0
282 | 0
283 | 0
284 | 0
285 | 0
286 | 0
287 | 0
288 | 0
289 | 0
290 | 0
291 | 0
292 | 0
293 | 0
294 | 0
295 | 0
296 | 0
297 | 0.10101
298 | 0.22501
299 | 0.31801
300 | 0.36802
301 | 0.36202
302 | 0.27801
303 | 0.17901
304 | 0.06859
305 | 0
306 | 0
307 | 0
308 | 0
309 | 0
310 | 0
311 | 0
312 | 0
313 | 0
314 | 0
315 | 0
316 | 0
317 | 0
318 | 0
319 | 0
320 | 0
321 | 0.009
322 | 0.039
323 | 0.05
324 | 0.049
325 | 0.083
326 | 0.077
327 | 0.106
328 | 0.067
329 | 0
330 | 0
331 | 0
332 | 0
333 | 0
334 | 0
335 | 0
336 | 0
337 | 0
338 | 0
339 | 0
340 | 0
341 | 0
342 | 0
343 | 0
344 | 0
345 | 0.05
346 | 0.152
347 | 0.216
348 | 0.167
349 | 0.137
350 | 0.105
351 | 0.17001
352 | 0.069
353 | 0
354 | 0
355 | 0
356 | 0
357 | 0
358 | 0
359 | 0
360 | 0
361 | 0
362 | 0
363 | 0
364 | 0
365 | 0
366 | 0
367 | 0
368 | 0
369 | 0.11301
370 | 0.165
371 | 0.218
372 | 0.29001
373 | 0.18
374 | 0.146
375 | 0.127
376 | 0.052
377 | 0
378 | 0
379 | 0
380 | 0
381 | 0
382 | 0
383 | 0
384 | 0
385 | 0
386 | 0
387 | 0
388 | 0
389 | 0
390 | 0
391 | 0
392 | 0
393 | 0.085
394 | 0.021
395 | 0.117
396 | 0.069
397 | 0.057
398 | 0.083
399 | 0.061
400 | 0.008
401 | 0
402 | 0
403 | 0
404 | 0
405 | 0
406 | 0
407 | 0
408 | 0
409 | 0
410 | 0
411 | 0
412 | 0
413 | 0
414 | 0
415 | 0
416 | 0
417 | 0.058
418 | 0.132
419 | 0.186
420 | 0.19
421 | 0.107
422 | 0.07
423 | 0.079
424 | 0.057
425 | 0
426 | 0
427 | 0
428 | 0
429 | 0
430 | 0
431 | 0
432 | 0
433 | 0
434 | 0
435 | 0
436 | 0
437 | 0
438 | 0
439 | 0
440 | 0
441 | 0.059
442 | 0.094
443 | 0.27501
444 | 0.31801
445 | 0.198
446 | 0.148
447 | 0.078
448 | 0.041
449 | 0
450 | 0
451 | 0
452 | 0
453 | 0
454 | 0
455 | 0
456 | 0
457 | 0
458 | 0
459 | 0
460 | 0
461 | 0
462 | 0
463 | 0
464 | 0
465 | 0.06
466 | 0.066
467 | 0.054
468 | 0.091
469 | 0.101
470 | 0.06
471 | 0.054
472 | 0.037
473 | 0
474 | 0
475 | 0
476 | 0
477 | 0
478 | 0
479 | 0
480 | 0
481 | 0
482 | 0
483 | 0
484 | 0
485 | 0
486 | 0
487 | 0
488 | 0
489 | 0.10601
490 | 0.135
491 | 0.059
492 | 0.133
493 | 0.089
494 | 0.186
495 | 0.032
496 | 0.044
497 | 0
498 | 0
499 | 0
500 | 0
501 | 0
502 | 0
503 | 0
504 | 0
505 | 0
506 | 0
507 | 0
508 | 0
509 | 0
510 | 0
511 | 0
512 | 0
513 | 0.049
514 | 0.043
515 | 0.08
516 | 0.072
517 | 0.062
518 | 0.03
519 | 0.04
520 | 0.033
521 | 0
522 | 0
523 | 0
524 | 0
525 | 0
526 | 0
527 | 0
528 | 0
529 | 0
530 | 0
531 | 0
532 | 0
533 | 0
534 | 0
535 | 0
536 | 0
537 | 0.055
538 | 0.088
539 | 0.057
540 | 0.061
541 | 0.137
542 | 0.056
543 | 0.044
544 | 0.036
545 | 0
546 | 0
547 | 0
548 | 0
549 | 0
550 | 0
551 | 0
552 | 0
553 | 0
554 | 0
555 | 0
556 | 0
557 | 0
558 | 0
559 | 0
560 | 0
561 | 0.053
562 | 0.069
563 | 0.059
564 | 0.088
565 | 0.23
566 | 0.138
567 | 0.071
568 | 0.073
569 | 0
570 | 0
571 | 0
572 | 0
573 | 0
574 | 0
575 | 0
576 | 0
577 | 0
578 | 0
579 | 0
580 | 0
581 | 0
582 | 0
583 | 0
584 | 0
585 | 0.081
586 | 0.109
587 | 0.082
588 | 0.094
589 | 0.113
590 | 0.087
591 | 0.03
592 | 0.011
593 | 0
594 | 0
595 | 0
596 | 0
597 | 0
598 | 0
599 | 0
600 | 0
601 | 0
602 | 0
603 | 0
604 | 0
605 | 0
606 | 0
607 | 0
608 | 0
609 | 0.032
610 | 0.085
611 | 0.06
612 | 0.079
613 | 0.06
614 | 0.06
615 | 0.045
616 | 0.039
617 | 0
618 | 0
619 | 0
620 | 0
621 | 0
622 | 0
623 | 0
624 | 0
625 | 0
626 | 0
627 | 0
628 | 0
629 | 0
630 | 0
631 | 0
632 | 0
633 | 0.048
634 | 0.125
635 | 0.119
636 | 0.169
637 | 0.232
638 | 0.182
639 | 0.085
640 | 0.013
641 | 0
642 | 0
643 | 0
644 | 0
645 | 0
646 | 0
647 | 0
648 | 0
649 | 0
650 | 0
651 | 0
652 | 0
653 | 0
654 | 0
655 | 0
656 | 0
657 | 0.13801
658 | 0.198
659 | 0.174
660 | 0.218
661 | 0.199
662 | 0.14
663 | 0.098
664 | 0.081
665 | 0
666 | 0
667 | 0
668 | 0
669 | 0
670 | 0
671 | 0
672 | 0
673 | 0
674 | 0
675 | 0
676 | 0
677 | 0
678 | 0
679 | 0
680 | 0
681 | 0.063
682 | 0.055
683 | 0.113
684 | 0.094
685 | 0.135
686 | 0.098
687 | 0.086
688 | 0.07
689 | 0
690 | 0
691 | 0
692 | 0
693 | 0
694 | 0
695 | 0
696 | 0
697 | 0
698 | 0
699 | 0
700 | 0
701 | 0
702 | 0
703 | 0
704 | 0
705 | 0.14701
706 | 0.23801
707 | 0.32801
708 | 0.121
709 | 0.211
710 | 0.134
711 | 0.129
712 | 0.12401
713 | 0
714 | 0
715 | 0
716 | 0
717 | 0
718 | 0
719 | 0
720 | 0
721 | 0
722 | 0
723 | 0
724 | 0
725 | 0
726 | 0
727 | 0
728 | 0
729 | 0.117
730 | 0.24301
731 | 0.27
732 | 0.32001
733 | 0.30901
734 | 0.185
735 | 0.127
736 | 0.087
737 | 0
738 | 0
739 | 0
740 | 0
741 | 0
742 | 0
743 | 0
744 | 0
745 | 0
746 | 0
747 | 0
748 | 0
749 | 0
750 | 0
751 | 0
752 | 0
753 | 0.11
754 | 0.189
755 | 0.199
756 | 0.235
757 | 0.12
758 | 0.156
759 | 0.071
760 | 0.032
761 | 0
762 | 0
763 | 0
764 | 0
765 | 0
766 | 0
767 | 0
768 | 0
769 | 0
770 | 0
771 | 0
772 | 0
773 | 0
774 | 0
775 | 0
776 | 0
777 | 0.092
778 | 0.166
779 | 0.075
780 | 0.062
781 | 0.083
782 | 0.135
783 | 0.187
784 | 0.081
785 | 0
786 | 0
787 | 0
788 | 0
789 | 0
790 | 0
791 | 0
792 | 0
793 | 0
794 | 0
795 | 0
796 | 0
797 | 0
798 | 0
799 | 0
800 | 0
801 | 0.082
802 | 0.156
803 | 0.142
804 | 0.17
805 | 0.079
806 | 0.232
807 | 0.152
808 | 0.07
809 | 0
810 | 0
811 | 0
812 | 0
813 | 0
814 | 0
815 | 0
816 | 0
817 | 0
818 | 0
819 | 0
820 | 0
821 | 0
822 | 0
823 | 0
824 | 0.01539
825 | 0.086
826 | 0.103
827 | 0.046
828 | 0.113
829 | 0.218
830 | 0.233
831 | 0.145
832 | 0.07
833 | 0
834 | 0
835 | 0
836 | 0
837 | 0
838 | 0
839 | 0
840 | 0
841 | 0
842 | 0
843 | 0
844 | 0
845 | 0
846 | 0
847 | 0
848 | 0.01463
849 | 0.091
850 | 0.032
851 | 0.06
852 | 0.074
853 | 0.086
854 | 0.042
855 | 0.039
856 | 0.015
857 | 0.002
858 | 0
859 | 0
860 | 0
861 | 0
862 | 0
863 | 0
864 | 0
865 | 0
866 | 0
867 | 0
868 | 0
869 | 0
870 | 0
871 | 0
872 | 0.008
873 | 0.038
874 | 0.16
875 | 0.125
876 | 0.118
877 | 0.041
878 | 0.039
879 | 0.042
880 | 0.022
881 | 0.003
882 | 0
883 | 0
884 | 0
885 | 0
886 | 0
887 | 0
888 | 0
889 | 0
890 | 0
891 | 0
892 | 0
893 | 0
894 | 0
895 | 0
896 | 0.014
897 | 0.074
898 | 0.094
899 | 0.075
900 | 0.081
901 | 0.145
902 | 0.103
903 | 0.074
904 | 0.061
905 | 0.008
906 | 0
907 | 0
908 | 0
909 | 0
910 | 0
911 | 0
912 | 0
913 | 0
914 | 0
915 | 0
916 | 0
917 | 0
918 | 0
919 | 0
920 | 0.006
921 | 0.097
922 | 0.103
923 | 0.066
924 | 0.07
925 | 0.093
926 | 0.116
927 | 0.239
928 | 0.069
929 | 0.006
930 | 0
931 | 0
932 | 0
933 | 0
934 | 0
935 | 0
936 | 0
937 | 0
938 | 0
939 | 0
940 | 0
941 | 0
942 | 0
943 | 0
944 | 0.02332
945 | 0.087
946 | 0.099
947 | 0.085
948 | 0.154
949 | 0.232
950 | 0.233
951 | 0.222
952 | 0.147
953 | 0.02
954 | 0
955 | 0
956 | 0
957 | 0
958 | 0
959 | 0
960 | 0
961 | 0
962 | 0
963 | 0
964 | 0
965 | 0
966 | 0
967 | 0
968 | 0.03065
969 | 0.164
970 | 0.28601
971 | 0.34601
972 | 0.38601
973 | 0.38301
974 | 0.35101
975 | 0.27001
976 | 0.16
977 | 0.023
978 | 0
979 | 0
980 | 0
981 | 0
982 | 0
983 | 0
984 | 0
985 | 0
986 | 0
987 | 0
988 | 0
989 | 0
990 | 0
991 | 0
992 | 0.02456
993 | 0.095
994 | 0.132
995 | 0.155
996 | 0.139
997 | 0.177
998 | 0.36501
999 | 0.29001
1000 | 0.17001
1001 | 0.024
1002 | 0
1003 | 0
1004 | 0
1005 | 0
1006 | 0
1007 | 0
1008 | 0
1009 | 0
1010 | 0
1011 | 0
1012 | 0
1013 | 0
1014 | 0
1015 | 0
1016 | 0.02732
1017 | 0.107
1018 | 0.149
1019 | 0.169
1020 | 0.214
1021 | 0.209
1022 | 0.267
1023 | 0.28401
1024 | 0.159
1025 | 0.03357
1026 | 0
1027 | 0
1028 | 0
1029 | 0
1030 | 0
1031 | 0
1032 | 0
1033 | 0
1034 | 0
1035 | 0
1036 | 0
1037 | 0
1038 | 0
1039 | 0
1040 | 0.03104
1041 | 0.138
1042 | 0.208
1043 | 0.232
1044 | 0.298
1045 | 0.38301
1046 | 0.297
1047 | 0.26
1048 | 0.148
1049 | 0.02479
1050 | 0
1051 | 0
1052 | 0
1053 | 0
1054 | 0
1055 | 0
1056 | 0
1057 | 0
1058 | 0
1059 | 0
1060 | 0
1061 | 0
1062 | 0
1063 | 0
1064 | 0.04088
1065 | 0.175
1066 | 0.33101
1067 | 0.313
1068 | 0.39101
1069 | 0.249
1070 | 0.40201
1071 | 0.13
1072 | 0.19101
1073 | 0.0488
1074 | 0
1075 | 0
1076 | 0
1077 | 0
1078 | 0
1079 | 0
1080 | 0
1081 | 0
1082 | 0
1083 | 0
1084 | 0
1085 | 0
1086 | 0
1087 | 0
1088 | 0.03747
1089 | 0.077
1090 | 0.178
1091 | 0.09
1092 | 0.253
1093 | 0.244
1094 | 0.27
1095 | 0.209
1096 | 0.19901
1097 | 0.0432
1098 | 0
1099 | 0
1100 | 0
1101 | 0
1102 | 0
1103 | 0
1104 | 0
1105 | 0
1106 | 0
1107 | 0
1108 | 0
1109 | 0
1110 | 0
1111 | 0
1112 | 0.03254
1113 | 0.098
1114 | 0.121
1115 | 0.163
1116 | 0.176
1117 | 0.253
1118 | 0.2895
1119 | 0.32601
1120 | 0.18951
1121 | 0.04803
1122 | 0
1123 | 0
1124 | 0
1125 | 0
1126 | 0
1127 | 0
1128 | 0
1129 | 0
1130 | 0
1131 | 0
1132 | 0
1133 | 0
1134 | 0
1135 | 0
1136 | 0.059
1137 | 0.104
1138 | 0.139
1139 | 0.165
1140 | 0.181
1141 | 0.123
1142 | 0.16
1143 | 0.135
1144 | 0.123
1145 | 0.03255
1146 | 0
1147 | 0
1148 | 0
1149 | 0
1150 | 0
1151 | 0
1152 | 0
1153 | 0
1154 | 0
1155 | 0
1156 | 0
1157 | 0
1158 | 0
1159 | 0
1160 | 0.033
1161 | 0.077
1162 | 0.072
1163 | 0.07
1164 | 0.079
1165 | 0.072
1166 | 0.079
1167 | 0.067
1168 | 0.06
1169 | 0.029
1170 | 0
1171 | 0
1172 | 0
1173 | 0
1174 | 0
1175 | 0
1176 | 0
1177 | 0
1178 | 0
1179 | 0
1180 | 0
1181 | 0
1182 | 0
1183 | 0
1184 | 0.049
1185 | 0.141
1186 | 0.235
1187 | 0.40701
1188 | 0.52301
1189 | 0.53401
1190 | 0.47401
1191 | 0.37001
1192 | 0.23201
1193 | 0.077
1194 | 0
1195 | 0
1196 | 0
1197 | 0
1198 | 0
1199 | 0
1200 | 0
1201 | 0
1202 | 0
1203 | 0
1204 | 0
1205 | 0
1206 | 0
1207 | 0
1208 | 0.084
1209 | 0.24401
1210 | 0.38501
1211 | 0.49201
1212 | 0.55501
1213 | 0.54901
1214 | 0.49001
1215 | 0.38801
1216 | 0.24601
1217 | 0.085
1218 | 0
1219 | 0
1220 | 0
1221 | 0
1222 | 0
1223 | 0
1224 | 0
1225 | 0
1226 | 0
1227 | 0
1228 | 0
1229 | 0
1230 | 0
1231 | 0
1232 | 0.076
1233 | 0.118
1234 | 0.157
1235 | 0.293
1236 | 0.25
1237 | 0.11
1238 | 0.132
1239 | 0.102
1240 | 0.076
1241 | 0.014
1242 | 0
1243 | 0
1244 | 0
1245 | 0
1246 | 0
1247 | 0
1248 | 0
1249 | 0
1250 | 0
1251 | 0
1252 | 0
1253 | 0
1254 | 0
1255 | 0
1256 | 0.053
1257 | 0.11
1258 | 0.16
1259 | 0.182
1260 | 0.376
1261 | 0.268
1262 | 0.089
1263 | 0.18
1264 | 0.126
1265 | 0.051
1266 | 0
1267 | 0
1268 | 0
1269 | 0
1270 | 0
1271 | 0
1272 | 0
1273 | 0
1274 | 0
1275 | 0
1276 | 0
1277 | 0
1278 | 0
1279 | 0
1280 | 0.009
1281 | 0.041
1282 | 0.059
1283 | 0.086
1284 | 0.071
1285 | 0.059
1286 | 0.069
1287 | 0.057
1288 | 0.033
1289 | 0.051
1290 | 0
1291 | 0
1292 | 0
1293 | 0
1294 | 0
1295 | 0
1296 | 0
1297 | 0
1298 | 0
1299 | 0
1300 | 0
1301 | 0
1302 | 0
1303 | 0
1304 | 0.017
1305 | 0.07
1306 | 0.131
1307 | 0.141
1308 | 0.175
1309 | 0.193
1310 | 0.241
1311 | 0.251
1312 | 0.127
1313 | 0.063
1314 | 0
1315 | 0
1316 | 0
1317 | 0
1318 | 0
1319 | 0
1320 | 0
1321 | 0
1322 | 0
1323 | 0
1324 | 0
1325 | 0
1326 | 0
1327 | 0
1328 | 0.043
1329 | 0.07
1330 | 0.34201
1331 | 0.38601
1332 | 0.376
1333 | 0.295
1334 | 0.42501
1335 | 0.38901
1336 | 0.26901
1337 | 0.104
1338 | 0
1339 | 0
1340 | 0
1341 | 0
1342 | 0
1343 | 0
1344 | 0
1345 | 0
1346 | 0
1347 | 0
1348 | 0
1349 | 0
1350 | 0
1351 | 0
1352 | 0.122
1353 | 0.28801
1354 | 0.43501
1355 | 0.53601
1356 | 0.60202
1357 | 0.59201
1358 | 0.54501
1359 | 0.43301
1360 | 0.28401
1361 | 0.116
1362 | 0
1363 | 0
1364 | 0
1365 | 0
1366 | 0
1367 | 0
1368 | 0
1369 | 0
1370 | 0
1371 | 0
1372 | 0
1373 | 0
1374 | 0
1375 | 0
1376 | 0.032
1377 | 0.077
1378 | 0.07
1379 | 0.081
1380 | 0.096
1381 | 0.052
1382 | 0.052
1383 | 0.069
1384 | 0.071
1385 | 0.021
1386 | 0
1387 | 0
1388 | 0
1389 | 0
1390 | 0
1391 | 0
1392 | 0
1393 | 0
1394 | 0
1395 | 0
1396 | 0
1397 | 0
1398 | 0
1399 | 0
1400 | 0.07
1401 | 0.138
1402 | 0.18
1403 | 0.136
1404 | 0.232
1405 | 0.189
1406 | 0.171
1407 | 0.205
1408 | 0.186
1409 | 0.062
1410 | 0
1411 | 0
1412 | 0
1413 | 0
1414 | 0
1415 | 0
1416 | 0
1417 | 0
1418 | 0
1419 | 0
1420 | 0
1421 | 0
1422 | 0
1423 | 0
1424 | 0.077
1425 | 0.167
1426 | 0.17
1427 | 0.251
1428 | 0.141
1429 | 0.12
1430 | 0.099
1431 | 0.34801
1432 | 0.175
1433 | 0.071
1434 | 0
1435 | 0
1436 | 0
1437 | 0
1438 | 0
1439 | 0
1440 | 0
1441 | 0
1442 | 0
1443 | 0
1444 | 0
1445 | 0
1446 | 0
1447 | 0
1448 | 0.013
1449 | 0.072
1450 | 0.25
1451 | 0.055
1452 | 0.053
1453 | 0.0715
1454 | 0.09
1455 | 0.061
1456 | 0.175
1457 | 0.087
1458 | 0
1459 | 0
1460 | 0
1461 | 0
1462 | 0
1463 | 0
1464 | 0
1465 | 0
1466 | 0
1467 | 0
1468 | 0
1469 | 0
1470 | 0
1471 | 0
1472 | 0.088
1473 | 0.28401
1474 | 0.282
1475 | 0.53901
1476 | 0.58501
1477 | 0.41551
1478 | 0.246
1479 | 0.197
1480 | 0.223
1481 | 0.118
1482 | 0
1483 | 0
1484 | 0
1485 | 0
1486 | 0
1487 | 0
1488 | 0
1489 | 0
1490 | 0
1491 | 0
1492 | 0
1493 | 0
1494 | 0
1495 | 0
1496 | 0.038
1497 | 0.075
1498 | 0.084
1499 | 0.2
1500 | 0.159
1501 | 0.151
1502 | 0.46701
1503 | 0.39001
1504 | 0.183
1505 | 0.057
1506 | 0
1507 | 0
1508 | 0
1509 | 0
1510 | 0
1511 | 0
1512 | 0
1513 | 0
1514 | 0
1515 | 0
1516 | 0
1517 | 0
1518 | 0
1519 | 0
1520 | 0.092
1521 | 0.228
1522 | 0.334
1523 | 0.314
1524 | 0.171
1525 | 0.088
1526 | 0.393
1527 | 0.267
1528 | 0.175
1529 | 0.106
1530 | 0
1531 | 0
1532 | 0
1533 | 0
1534 | 0
1535 | 0
1536 | 0
1537 | 0
1538 | 0
1539 | 0
1540 | 0
1541 | 0
1542 | 0
1543 | 0
1544 | 0.153
1545 | 0.32101
1546 | 0.45701
1547 | 0.57001
1548 | 0.61401
1549 | 0.58201
1550 | 0.55701
1551 | 0.45701
1552 | 0.30801
1553 | 0.135
1554 | 0
1555 | 0
1556 | 0
1557 | 0
1558 | 0
1559 | 0
1560 | 0
1561 | 0
1562 | 0
1563 | 0
1564 | 0
1565 | 0
1566 | 0
1567 | 0
1568 | 0.159
1569 | 0.31501
1570 | 0.43601
1571 | 0.50101
1572 | 0.55701
1573 | 0.54801
1574 | 0.49701
1575 | 0.38501
1576 | 0.32401
1577 | 0.148
1578 | 0
1579 | 0
1580 | 0
1581 | 0
1582 | 0
1583 | 0
1584 | 0
1585 | 0
1586 | 0
1587 | 0
1588 | 0
1589 | 0
1590 | 0
1591 | 0
1592 | 0.167
1593 | 0.33701
1594 | 0.47201
1595 | 0.56801
1596 | 0.59001
1597 | 0.54401
1598 | 0.49301
1599 | 0.42201
1600 | 0.253
1601 | 0.128
1602 | 0
1603 | 0
1604 | 0
1605 | 0
1606 | 0
1607 | 0
1608 | 0
1609 | 0
1610 | 0
1611 | 0
1612 | 0
1613 | 0
1614 | 0
1615 | 0
1616 | 0.178
1617 | 0.34001
1618 | 0.47901
1619 | 0.59001
1620 | 0.64601
1621 | 0.62301
1622 | 0.58001
1623 | 0.47601
1624 | 0.32601
1625 | 0.157
1626 | 0
1627 | 0
1628 | 0
1629 | 0
1630 | 0
1631 | 0
1632 | 0
1633 | 0
1634 | 0
1635 | 0
1636 | 0
1637 | 0
1638 | 0
1639 | 0.011
1640 | 0.175
1641 | 0.34801
1642 | 0.48801
1643 | 0.59601
1644 | 0.63501
1645 | 0.60201
1646 | 0.49701
1647 | 0.319
1648 | 0.176
1649 | 0.08
1650 | 0
1651 | 0
1652 | 0
1653 | 0
1654 | 0
1655 | 0
1656 | 0
1657 | 0
1658 | 0
1659 | 0
1660 | 0
1661 | 0
1662 | 0
1663 | 0.007
1664 | 0.094
1665 | 0.121
1666 | 0.11
1667 | 0.223
1668 | 0.221
1669 | 0.367
1670 | 0.57301
1671 | 0.48201
1672 | 0.30201
1673 | 0.138
1674 | 0
1675 | 0
1676 | 0
1677 | 0
1678 | 0
1679 | 0
1680 | 0
1681 | 0
1682 | 0
1683 | 0
1684 | 0
1685 | 0
1686 | 0
1687 | 0.018
1688 | 0.195
1689 | 0.37001
1690 | 0.51101
1691 | 0.61501
1692 | 0.66501
1693 | 0.64001
1694 | 0.58801
1695 | 0.49001
1696 | 0.33901
1697 | 0.17
1698 | 0
1699 | 0
1700 | 0
1701 | 0
1702 | 0
1703 | 0
1704 | 0
1705 | 0
1706 | 0
1707 | 0
1708 | 0
1709 | 0
1710 | 0
1711 | 0.02
1712 | 0.194
1713 | 0.37001
1714 | 0.51301
1715 | 0.61901
1716 | 0.67401
1717 | 0.66301
1718 | 0.60601
1719 | 0.49501
1720 | 0.34201
1721 | 0.173
1722 | 0
1723 | 0
1724 | 0
1725 | 0
1726 | 0
1727 | 0
1728 | 0
1729 | 0
1730 | 0
1731 | 0
1732 | 0
1733 | 0
1734 | 0
1735 | 0.022
1736 | 0.189
1737 | 0.36501
1738 | 0.50801
1739 | 0.61301
1740 | 0.67701
1741 | 0.66601
1742 | 0.60301
1743 | 0.48501
1744 | 0.33601
1745 | 0.167
1746 | 0.001
1747 | 0
1748 | 0
1749 | 0
1750 | 0
1751 | 0
1752 | 0
1753 | 0
1754 | 0
1755 | 0
1756 | 0
1757 | 0
1758 | 0
1759 | 0.017
1760 | 0.086
1761 | 0.124
1762 | 0.177
1763 | 0.233
1764 | 0.401
1765 | 0.67201
1766 | 0.48601
1767 | 0.46201
1768 | 0.307
1769 | 0.143
1770 | 0.01605
1771 | 0
1772 | 0
1773 | 0
1774 | 0
1775 | 0
1776 | 0
1777 | 0
1778 | 0
1779 | 0
1780 | 0
1781 | 0
1782 | 0
1783 | 0.016
1784 | 0.056
1785 | 0.202
1786 | 0.234
1787 | 0.61901
1788 | 0.67201
1789 | 0.64201
1790 | 0.48101
1791 | 0.397
1792 | 0.115
1793 | 0.076
1794 | 0.01086
1795 | 0
1796 | 0
1797 | 0
1798 | 0
1799 | 0
1800 | 0
1801 | 0
1802 | 0
1803 | 0
1804 | 0
1805 | 0
1806 | 0
1807 | 0.015
1808 | 0.169
1809 | 0.40801
1810 | 0.51901
1811 | 0.54801
1812 | 0.68201
1813 | 0.67701
1814 | 0.59301
1815 | 0.352
1816 | 0.251
1817 | 0.102
1818 | 0.019
1819 | 0
1820 | 0
1821 | 0
1822 | 0
1823 | 0
1824 | 0
1825 | 0
1826 | 0
1827 | 0
1828 | 0
1829 | 0
1830 | 0
1831 | 0.02581
1832 | 0.192
1833 | 0.39501
1834 | 0.52001
1835 | 0.64801
1836 | 0.70901
1837 | 0.69701
1838 | 0.63101
1839 | 0.51201
1840 | 0.35701
1841 | 0.19
1842 | 0.02174
1843 | 0
1844 | 0
1845 | 0
1846 | 0
1847 | 0
1848 | 0
1849 | 0
1850 | 0
1851 | 0
1852 | 0
1853 | 0
1854 | 0
1855 | 0.051
1856 | 0.22
1857 | 0.39701
1858 | 0.53801
1859 | 0.65101
1860 | 0.70501
1861 | 0.60001
1862 | 0.63701
1863 | 0.51901
1864 | 0.36401
1865 | 0.195
1866 | 0.02908
1867 | 0
1868 | 0
1869 | 0
1870 | 0
1871 | 0
1872 | 0
1873 | 0
1874 | 0
1875 | 0
1876 | 0
1877 | 0
1878 | 0
1879 | 0.057
1880 | 0.229
1881 | 0.40501
1882 | 0.58401
1883 | 0.69101
1884 | 0.72901
1885 | 0.71201
1886 | 0.63901
1887 | 0.52501
1888 | 0.35901
1889 | 0.198
1890 | 0.03248
1891 | 0
1892 | 0
1893 | 0
1894 | 0
1895 | 0
1896 | 0
1897 | 0
1898 | 0
1899 | 0
1900 | 0
1901 | 0
1902 | 0
1903 | 0.007
1904 | 0.023
1905 | 0.194
1906 | 0.054
1907 | 0.106
1908 | 0.191
1909 | 0.141
1910 | 0.096
1911 | 0.099
1912 | 0.095
1913 | 0.075
1914 | 0.01882
1915 | 0
1916 | 0
1917 | 0
1918 | 0
1919 | 0
1920 | 0
1921 | 0
1922 | 0
1923 | 0
1924 | 0
1925 | 0
1926 | 0
1927 | 0.026
1928 | 0.059
1929 | 0.139
1930 | 0.079
1931 | 0.087
1932 | 0.18
1933 | 0.206
1934 | 0.281
1935 | 0.206
1936 | 0.077
1937 | 0.077
1938 | 0.02533
1939 | 0
1940 | 0
1941 | 0
1942 | 0
1943 | 0
1944 | 0
1945 | 0
1946 | 0
1947 | 0
1948 | 0
1949 | 0
1950 | 0
1951 | 0.041
1952 | 0.125
1953 | 0.198
1954 | 0.368
1955 | 0.65801
1956 | 0.75001
1957 | 0.74001
1958 | 0.67501
1959 | 0.55901
1960 | 0.39701
1961 | 0.222
1962 | 0.04115
1963 | 0
1964 | 0
1965 | 0
1966 | 0
1967 | 0
1968 | 0
1969 | 0
1970 | 0
1971 | 0
1972 | 0
1973 | 0
1974 | 0
1975 | 0.062
1976 | 0.175
1977 | 0.43801
1978 | 0.58101
1979 | 0.59201
1980 | 0.71601
1981 | 0.73801
1982 | 0.67401
1983 | 0.55301
1984 | 0.40501
1985 | 0.229
1986 | 0.04706
1987 | 0
1988 | 0
1989 | 0
1990 | 0
1991 | 0
1992 | 0
1993 | 0
1994 | 0
1995 | 0
1996 | 0
1997 | 0
1998 | 0
1999 | 0.038
2000 | 0.171
2001 | 0.165
2002 | 0.183
2003 | 0.252
2004 | 0.282
2005 | 0.303
2006 | 0.244
2007 | 0.144
2008 | 0.113
2009 | 0.104
2010 | 0.008
2011 | 0
2012 | 0
2013 | 0
2014 | 0
2015 | 0
2016 | 0
2017 | 0
2018 | 0
2019 | 0
2020 | 0
2021 | 0
2022 | 0
2023 | 0.046
2024 | 0.139
2025 | 0.12
2026 | 0.102
2027 | 0.126
2028 | 0.203
2029 | 0.126
2030 | 0.084
2031 | 0.102
2032 | 0.126
2033 | 0.147
2034 | 0.023
2035 | 0
2036 | 0
2037 | 0
2038 | 0
2039 | 0
2040 | 0
2041 | 0
2042 | 0
2043 | 0
2044 | 0
2045 | 0
2046 | 0
2047 | 0.042
2048 | 0.097
2049 | 0.41401
2050 | 0.349
2051 | 0.501
2052 | 0.472
2053 | 0.549
2054 | 0.207
2055 | 0.396
2056 | 0.264
2057 | 0.104
2058 | 0.04364
2059 | 0
2060 | 0
2061 | 0
2062 | 0
2063 | 0
2064 | 0
2065 | 0
2066 | 0
2067 | 0
2068 | 0
2069 | 0
2070 | 0
2071 | 0.115
2072 | 0.307
2073 | 0.48701
2074 | 0.62101
2075 | 0.72701
2076 | 0.78001
2077 | 0.75301
2078 | 0.68801
2079 | 0.51301
2080 | 0.201
2081 | 0.076
2082 | 0.021
2083 | 0
2084 | 0
2085 | 0
2086 | 0
2087 | 0
2088 | 0
2089 | 0
2090 | 0
2091 | 0
2092 | 0
2093 | 0
2094 | 0
2095 | 0.065
2096 | 0.132
2097 | 0.159
2098 | 0.383
2099 | 0.096
2100 | 0.118
2101 | 0.11
2102 | 0.103
2103 | 0.092
2104 | 0.097
2105 | 0.038
2106 | 0.008
2107 | 0
2108 | 0
2109 | 0
2110 | 0
2111 | 0
2112 | 0
2113 | 0
2114 | 0
2115 | 0
2116 | 0
2117 | 0
2118 | 0
2119 | 0.012
2120 | 0.078
2121 | 0.13
2122 | 0.099
2123 | 0.228
2124 | 0.127
2125 | 0.252
2126 | 0.476
2127 | 0.255
2128 | 0.054
2129 | 0.067
2130 | 0.02
2131 | 0
2132 | 0
2133 | 0
2134 | 0
2135 | 0
2136 | 0
2137 | 0
2138 | 0
2139 | 0
2140 | 0
2141 | 0
2142 | 0
2143 | 0.083
2144 | 0.181
2145 | 0.071
2146 | 0.105
2147 | 0.112
2148 | 0.244
2149 | 0.124
2150 | 0.236
2151 | 0.093
2152 | 0.059
2153 | 0.039
2154 | 0.075
2155 | 0
2156 | 0
2157 | 0
2158 | 0
2159 | 0
2160 | 0
2161 | 0
2162 | 0
2163 | 0
2164 | 0
2165 | 0
2166 | 0
2167 | 0.119
2168 | 0.075
2169 | 0.076
2170 | 0.095
2171 | 0.124
2172 | 0.58
2173 | 0.524
2174 | 0.66201
2175 | 0.152
2176 | 0.081
2177 | 0.167
2178 | 0.028
2179 | 0
2180 | 0
2181 | 0
2182 | 0
2183 | 0
2184 | 0
2185 | 0
2186 | 0
2187 | 0
2188 | 0
2189 | 0
2190 | 0
2191 | 0.016
2192 | 0.034
2193 | 0.078
2194 | 0.098
2195 | 0.107
2196 | 0.114
2197 | 0.087
2198 | 0.091
2199 | 0.052
2200 | 0.055
2201 | 0.047
2202 | 0.027
2203 | 0
2204 | 0
2205 | 0
2206 | 0
2207 | 0
2208 | 0
2209 | 0
2210 | 0
2211 | 0
2212 | 0
2213 | 0
2214 | 0
2215 | 0.085
2216 | 0.173
2217 | 0.283
2218 | 0.54001
2219 | 0.61501
2220 | 0.63301
2221 | 0.572
2222 | 0.59401
2223 | 0.484
2224 | 0.181
2225 | 0.116
2226 | 0.031
2227 | 0
2228 | 0
2229 | 0
2230 | 0
2231 | 0
2232 | 0
2233 | 0
2234 | 0
2235 | 0
2236 | 0
2237 | 0
2238 | 0
2239 | 0.054
2240 | 0.033
2241 | 0.053
2242 | 0.116
2243 | 0.092
2244 | 0.138
2245 | 0.075
2246 | 0.106
2247 | 0.08
2248 | 0.117
2249 | 0.079
2250 | 0.039
2251 | 0
2252 | 0
2253 | 0
2254 | 0
2255 | 0
2256 | 0
2257 | 0
2258 | 0
2259 | 0
2260 | 0
2261 | 0
2262 | 0
2263 | 0.106
2264 | 0.232
2265 | 0.238
2266 | 0.353
2267 | 0.212
2268 | 0.264
2269 | 0.595
2270 | 0.62001
2271 | 0.463
2272 | 0.367
2273 | 0.108
2274 | 0.081
2275 | 0
2276 | 0
2277 | 0
2278 | 0
2279 | 0
2280 | 0
2281 | 0
2282 | 0
2283 | 0
2284 | 0
2285 | 0
2286 | 0
2287 | 0.161
2288 | 0.348
2289 | 0.51601
2290 | 0.65401
2291 | 0.70401
2292 | 0.595
2293 | 0.118
2294 | 0.208
2295 | 0.092
2296 | 0.085
2297 | 0.074
2298 | 0.043
2299 | 0
2300 | 0
2301 | 0
2302 | 0
2303 | 0
2304 | 0
2305 | 0
2306 | 0
2307 | 0
2308 | 0
2309 | 0
2310 | 0
2311 | 0.167
2312 | 0.351
2313 | 0.52401
2314 | 0.66901
2315 | 0.76001
2316 | 0.80901
2317 | 0.78101
2318 | 0.72301
2319 | 0.61301
2320 | 0.45701
2321 | 0.28
2322 | 0.097
2323 | 0
2324 | 0
2325 | 0
2326 | 0
2327 | 0
2328 | 0
2329 | 0
2330 | 0
2331 | 0
2332 | 0
2333 | 0
2334 | 0
2335 | 0.171
2336 | 0.355
2337 | 0.52801
2338 | 0.66801
2339 | 0.76501
2340 | 0.80601
2341 | 0.79401
2342 | 0.73101
2343 | 0.61701
2344 | 0.46101
2345 | 0.281
2346 | 0.098
2347 | 0
2348 | 0
2349 | 0
2350 | 0
2351 | 0
2352 | 0
2353 | 0
2354 | 0
2355 | 0
2356 | 0
2357 | 0
2358 | 0.01
2359 | 0.179
2360 | 0.364
2361 | 0.53601
2362 | 0.67401
2363 | 0.76701
2364 | 0.81101
2365 | 0.79801
2366 | 0.73501
2367 | 0.62201
2368 | 0.461
2369 | 0.283
2370 | 0.103
2371 | 0
2372 | 0
2373 | 0
2374 | 0
2375 | 0
2376 | 0
2377 | 0
2378 | 0
2379 | 0
2380 | 0
2381 | 0
2382 | 0.013
2383 | 0.184
2384 | 0.361
2385 | 0.52501
2386 | 0.66501
2387 | 0.73501
2388 | 0.78101
2389 | 0.75201
2390 | 0.66201
2391 | 0.407
2392 | 0.423
2393 | 0.268
2394 | 0.076
2395 | 0
2396 | 0
2397 | 0
2398 | 0
2399 | 0
2400 | 0
2401 | 0
2402 | 0
2403 | 0
2404 | 0
2405 | 0
2406 | 0.005
2407 | 0.137
2408 | 0.347
2409 | 0.41
2410 | 0.556
2411 | 0.365
2412 | 0.136
2413 | 0.522
2414 | 0.328
2415 | 0.092
2416 | 0.117
2417 | 0.087
2418 | 0.039
2419 | 0
2420 | 0
2421 | 0
2422 | 0
2423 | 0
2424 | 0
2425 | 0
2426 | 0
2427 | 0
2428 | 0
2429 | 0
2430 | 0.006
2431 | 0.141
2432 | 0.35
2433 | 0.54401
2434 | 0.64701
2435 | 0.77701
2436 | 0.82001
2437 | 0.81201
2438 | 0.74801
2439 | 0.62101
2440 | 0.468
2441 | 0.289
2442 | 0.114
2443 | 0
2444 | 0
2445 | 0
2446 | 0
2447 | 0
2448 | 0
2449 | 0
2450 | 0
2451 | 0
2452 | 0
2453 | 0
2454 | 0.02
2455 | 0.198
2456 | 0.387
2457 | 0.55801
2458 | 0.67301
2459 | 0.69501
2460 | 0.72501
2461 | 0.75601
2462 | 0.67401
2463 | 0.59201
2464 | 0.449
2465 | 0.249
2466 | 0.079
2467 | 0
2468 | 0
2469 | 0
2470 | 0
2471 | 0
2472 | 0
2473 | 0
2474 | 0
2475 | 0
2476 | 0
2477 | 0
2478 | 0.022
2479 | 0.196
2480 | 0.377
2481 | 0.54601
2482 | 0.67801
2483 | 0.77401
2484 | 0.82001
2485 | 0.79901
2486 | 0.74001
2487 | 0.61201
2488 | 0.455
2489 | 0.277
2490 | 0.114
2491 | 0
2492 | 0
2493 | 0
2494 | 0
2495 | 0
2496 | 0
2497 | 0
2498 | 0
2499 | 0
2500 | 0
2501 | 0
2502 | 0.02808
2503 | 0.199
2504 | 0.388
2505 | 0.513
2506 | 0.70801
2507 | 0.80401
2508 | 0.84601
2509 | 0.83301
2510 | 0.76401
2511 | 0.61201
2512 | 0.408
2513 | 0.234
2514 | 0.11
2515 | 0
2516 | 0
2517 | 0
2518 | 0
2519 | 0
2520 | 0
2521 | 0
2522 | 0
2523 | 0
2524 | 0
2525 | 0
2526 | 0.0238
2527 | 0.038
2528 | 0.137
2529 | 0.434
2530 | 0.595
2531 | 0.66601
2532 | 0.74901
2533 | 0.376
2534 | 0.386
2535 | 0.44
2536 | 0.075
2537 | 0.1
2538 | 0.019
2539 | 0
2540 | 0
2541 | 0
2542 | 0
2543 | 0
2544 | 0
2545 | 0
2546 | 0
2547 | 0
2548 | 0
2549 | 0
2550 | 0.012
2551 | 0.06
2552 | 0.053
2553 | 0.115
2554 | 0.108
2555 | 0.09
2556 | 0.161
2557 | 0.118
2558 | 0.076
2559 | 0.066
2560 | 0.057
2561 | 0.028
2562 | 0.078
2563 | 0
2564 | 0
2565 | 0
2566 | 0
2567 | 0
2568 | 0
2569 | 0
2570 | 0
2571 | 0
2572 | 0
2573 | 0
2574 | 0.013
2575 | 0.027
2576 | 0.199
2577 | 0.352
2578 | 0.576
2579 | 0.6
2580 | 0.436
2581 | 0.27
2582 | 0.602
2583 | 0.63401
2584 | 0.488
2585 | 0.321
2586 | 0.138
2587 | 0
2588 | 0
2589 | 0
2590 | 0
2591 | 0
2592 | 0
2593 | 0
2594 | 0
2595 | 0
2596 | 0
2597 | 0
2598 | 0.05
2599 | 0.238
2600 | 0.421
2601 | 0.59501
2602 | 0.73501
2603 | 0.82601
2604 | 0.86701
2605 | 0.85301
2606 | 0.78301
2607 | 0.66701
2608 | 0.504
2609 | 0.326
2610 | 0.144
2611 | 0
2612 | 0
2613 | 0
2614 | 0
2615 | 0
2616 | 0
2617 | 0
2618 | 0
2619 | 0
2620 | 0
2621 | 0
2622 | 0.054
2623 | 0.243
2624 | 0.429
2625 | 0.59701
2626 | 0.73901
2627 | 0.82201
2628 | 0.85401
2629 | 0.75501
2630 | 0.75501
2631 | 0.65801
2632 | 0.508
2633 | 0.329
2634 | 0.148
2635 | 0
2636 | 0
2637 | 0
2638 | 0
2639 | 0
2640 | 0
2641 | 0
2642 | 0
2643 | 0
2644 | 0
2645 | 0
2646 | 0.056
2647 | 0.244
2648 | 0.43
2649 | 0.59901
2650 | 0.74001
2651 | 0.82601
2652 | 0.87501
2653 | 0.86001
2654 | 0.79001
2655 | 0.67201
2656 | 0.509
2657 | 0.331
2658 | 0.151
2659 | 0
2660 | 0
2661 | 0
2662 | 0
2663 | 0
2664 | 0
2665 | 0
2666 | 0
2667 | 0
2668 | 0
2669 | 0
2670 | 0.064
2671 | 0.257
2672 | 0.443
2673 | 0.60701
2674 | 0.74801
2675 | 0.83801
2676 | 0.87901
2677 | 0.86401
2678 | 0.79401
2679 | 0.67501
2680 | 0.513
2681 | 0.336
2682 | 0.154
2683 | 0
2684 | 0
2685 | 0
2686 | 0
2687 | 0
2688 | 0
2689 | 0
2690 | 0
2691 | 0
2692 | 0
2693 | 0
2694 | 0.062
2695 | 0.254
2696 | 0.442
2697 | 0.60801
2698 | 0.74501
2699 | 0.83401
2700 | 0.87901
2701 | 0.86301
2702 | 0.79001
2703 | 0.68201
2704 | 0.516
2705 | 0.336
2706 | 0.155
2707 | 0
2708 | 0
2709 | 0
2710 | 0
2711 | 0
2712 | 0
2713 | 0
2714 | 0
2715 | 0
2716 | 0
2717 | 0
2718 | 0.068
2719 | 0.262
2720 | 0.448
2721 | 0.61001
2722 | 0.75301
2723 | 0.84601
2724 | 0.88701
2725 | 0.87101
2726 | 0.80101
2727 | 0.68501
2728 | 0.523
2729 | 0.333
2730 | 0.14
2731 | 0
2732 | 0
2733 | 0
2734 | 0
2735 | 0
2736 | 0
2737 | 0
2738 | 0
2739 | 0
2740 | 0
2741 | 0
2742 | 0.035
2743 | 0.099
2744 | 0.199
2745 | 0.343
2746 | 0.371
2747 | 0.403
2748 | 0.274
2749 | 0.451
2750 | 0.156
2751 | 0.116
2752 | 0.083
2753 | 0.076
2754 | 0.099
2755 | 0
2756 | 0
2757 | 0
2758 | 0
2759 | 0
2760 | 0
2761 | 0
2762 | 0
2763 | 0
2764 | 0
2765 | 0
2766 | 0.06
2767 | 0.089
2768 | 0.249
2769 | 0.252
2770 | 0.449
2771 | 0.78001
2772 | 0.79301
2773 | 0.77001
2774 | 0.421
2775 | 0.435
2776 | 0.218
2777 | 0.303
2778 | 0.069
2779 | 0
2780 | 0
2781 | 0
2782 | 0
2783 | 0
2784 | 0
2785 | 0
2786 | 0
2787 | 0
2788 | 0
2789 | 0
2790 | 0.055
2791 | 0.162
2792 | 0.317
2793 | 0.271
2794 | 0.239
2795 | 0.649
2796 | 0.169
2797 | 0.431
2798 | 0.73601
2799 | 0.571
2800 | 0.53
2801 | 0.361
2802 | 0.176
2803 | 0.001
2804 | 0
2805 | 0
2806 | 0
2807 | 0
2808 | 0
2809 | 0
2810 | 0
2811 | 0
2812 | 0
2813 | 0
2814 | 0.071
2815 | 0.024
2816 | 0.041
2817 | 0.0915
2818 | 0.142
2819 | 0.109
2820 | 0.158
2821 | 0.128
2822 | 0.098
2823 | 0.061
2824 | 0.171
2825 | 0.122
2826 | 0.1
2827 | 0.002
2828 | 0
2829 | 0
2830 | 0
2831 | 0
2832 | 0
2833 | 0
2834 | 0
2835 | 0
2836 | 0
2837 | 0
2838 | 0.068
2839 | 0.224
2840 | 0.343
2841 | 0.529
2842 | 0.654
2843 | 0.79401
2844 | 0.85401
2845 | 0.82401
2846 | 0.628
2847 | 0.222
2848 | 0.325
2849 | 0.162
2850 | 0.07
2851 | 0.002
2852 | 0
2853 | 0
2854 | 0
2855 | 0
2856 | 0
2857 | 0
2858 | 0
2859 | 0
2860 | 0
2861 | 0
2862 | 0.11
2863 | 0.286
2864 | 0.454
2865 | 0.628
2866 | 0.661
2867 | 0.75201
2868 | 0.81001
2869 | 0.79501
2870 | 0.68501
2871 | 0.377
2872 | 0.179
2873 | 0.169
2874 | 0.03
2875 | 0.003
2876 | 0
2877 | 0
2878 | 0
2879 | 0
2880 | 0
2881 | 0
2882 | 0
2883 | 0
2884 | 0
2885 | 0
2886 | 0.011
2887 | 0.025
2888 | 0.041
2889 | 0.072
2890 | 0.073
2891 | 0.085
2892 | 0.1
2893 | 0.134
2894 | 0.217
2895 | 0.065
2896 | 0.079
2897 | 0.031
2898 | 0.025
2899 | 0.003
2900 | 0
2901 | 0
2902 | 0
2903 | 0
2904 | 0
2905 | 0
2906 | 0
2907 | 0
2908 | 0
2909 | 0
2910 | 0.012
2911 | 0.102
2912 | 0.182
2913 | 0.246
2914 | 0.383
2915 | 0.572
2916 | 0.443
2917 | 0.299
2918 | 0.2
2919 | 0.19
2920 | 0.105
2921 | 0.048
2922 | 0.024
2923 | 0.002
2924 | 0
2925 | 0
2926 | 0
2927 | 0
2928 | 0
2929 | 0
2930 | 0
2931 | 0
2932 | 0
2933 | 0
2934 | 0.016
2935 | 0.041
2936 | 0.071
2937 | 0.14
2938 | 0.14
2939 | 0.157
2940 | 0.124
2941 | 0.172
2942 | 0.337
2943 | 0.172
2944 | 0.224
2945 | 0.196
2946 | 0.065
2947 | 0.01
2948 | 0
2949 | 0
2950 | 0
2951 | 0
2952 | 0
2953 | 0
2954 | 0
2955 | 0
2956 | 0
2957 | 0
2958 | 0.011
2959 | 0.065
2960 | 0.112
2961 | 0.183
2962 | 0.121
2963 | 0.142
2964 | 0.272
2965 | 0.136
2966 | 0.54
2967 | 0.535
2968 | 0.096
2969 | 0.145
2970 | 0.092
2971 | 0.012
2972 | 0
2973 | 0
2974 | 0
2975 | 0
2976 | 0
2977 | 0
2978 | 0
2979 | 0
2980 | 0
2981 | 0
2982 | 0.1
2983 | 0.033
2984 | 0.105
2985 | 0.215
2986 | 0.151
2987 | 0.695
2988 | 0.514
2989 | 0.143
2990 | 0.193
2991 | 0.204
2992 | 0.314
2993 | 0.187
2994 | 0.128
2995 | 0.01683
2996 | 0
2997 | 0
2998 | 0
2999 | 0
3000 | 0
3001 | 0
3002 | 0
3003 | 0
3004 | 0
3005 | 0
3006 | 0.039
3007 | 0.122
3008 | 0.172
3009 | 0.324
3010 | 0.488
3011 | 0.83501
3012 | 0.77901
3013 | 0.82801
3014 | 0.637
3015 | 0.582
3016 | 0.47
3017 | 0.325
3018 | 0.022
3019 | 0.01783
3020 | 0
3021 | 0
3022 | 0
3023 | 0
3024 | 0
3025 | 0
3026 | 0
3027 | 0
3028 | 0
3029 | 0
3030 | 0.047
3031 | 0.262
3032 | 0.212
3033 | 0.387
3034 | 0.68
3035 | 0.79801
3036 | 0.81401
3037 | 0.79401
3038 | 0.82801
3039 | 0.683
3040 | 0.501
3041 | 0.318
3042 | 0.093
3043 | 0.006
3044 | 0
3045 | 0
3046 | 0
3047 | 0
3048 | 0
3049 | 0
3050 | 0
3051 | 0
3052 | 0
3053 | 0
3054 | 0.135
3055 | 0.305
3056 | 0.493
3057 | 0.648
3058 | 0.77501
3059 | 0.88901
3060 | 0.90001
3061 | 0.78701
3062 | 0.71301
3063 | 0.191
3064 | 0.061
3065 | 0.064
3066 | 0.025
3067 | 0.018
3068 | 0
3069 | 0
3070 | 0
3071 | 0
3072 | 0
3073 | 0
3074 | 0
3075 | 0
3076 | 0
3077 | 0
3078 | 0.04
3079 | 0.058
3080 | 0.149
3081 | 0.276
3082 | 0.373
3083 | 0.498
3084 | 0.452
3085 | 0.472
3086 | 0.54
3087 | 0.531
3088 | 0.241
3089 | 0.26
3090 | 0.201
3091 | 0.03401
3092 | 0
3093 | 0
3094 | 0
3095 | 0
3096 | 0
3097 | 0
3098 | 0
3099 | 0
3100 | 0
3101 | 0
3102 | 0.106
3103 | 0.259
3104 | 0.488
3105 | 0.58
3106 | 0.71201
3107 | 0.85901
3108 | 0.90501
3109 | 0.87901
3110 | 0.83601
3111 | 0.70101
3112 | 0.546
3113 | 0.389
3114 | 0.207
3115 | 0.04169
3116 | 0
3117 | 0
3118 | 0
3119 | 0
3120 | 0
3121 | 0
3122 | 0
3123 | 0
3124 | 0
3125 | 0
3126 | 0.098
3127 | 0.275
3128 | 0.473
3129 | 0.617
3130 | 0.666
3131 | 0.667
3132 | 0.81801
3133 | 0.80801
3134 | 0.79201
3135 | 0.623
3136 | 0.505
3137 | 0.318
3138 | 0.188
3139 | 0.03994
3140 | 0
3141 | 0
3142 | 0
3143 | 0
3144 | 0
3145 | 0
3146 | 0
3147 | 0
3148 | 0
3149 | 0
3150 | 0.107
3151 | 0.298
3152 | 0.427
3153 | 0.592
3154 | 0.78201
3155 | 0.76001
3156 | 0.86201
3157 | 0.81001
3158 | 0.75601
3159 | 0.695
3160 | 0.481
3161 | 0.375
3162 | 0.185
3163 | 0.03703
3164 | 0
3165 | 0
3166 | 0
3167 | 0
3168 | 0
3169 | 0
3170 | 0
3171 | 0
3172 | 0
3173 | 0
3174 | 0.103
3175 | 0.257
3176 | 0.46
3177 | 0.598
3178 | 0.78501
3179 | 0.77101
3180 | 0.67
3181 | 0.79801
3182 | 0.79301
3183 | 0.694
3184 | 0.525
3185 | 0.384
3186 | 0.202
3187 | 0.03822
3188 | 0
3189 | 0
3190 | 0
3191 | 0
3192 | 0
3193 | 0
3194 | 0
3195 | 0
3196 | 0
3197 | 0
3198 | 0.119
3199 | 0.26
3200 | 0.494
3201 | 0.662
3202 | 0.79501
3203 | 0.538
3204 | 0.434
3205 | 0.579
3206 | 0.407
3207 | 0.521
3208 | 0.576
3209 | 0.109
3210 | 0.165
3211 | 0.034
3212 | 0
3213 | 0
3214 | 0
3215 | 0
3216 | 0
3217 | 0
3218 | 0
3219 | 0
3220 | 0
3221 | 0
3222 | 0.098
3223 | 0.033
3224 | 0.045
3225 | 0.059
3226 | 0.071
3227 | 0.079
3228 | 0.126
3229 | 0.364
3230 | 0.141
3231 | 0.117
3232 | 0.078
3233 | 0.059
3234 | 0.019
3235 | 0.015
3236 | 0
3237 | 0
3238 | 0
3239 | 0
3240 | 0
3241 | 0
3242 | 0
3243 | 0
3244 | 0
3245 | 0.002
3246 | 0.048
3247 | 0.086
3248 | 0.166
3249 | 0.248
3250 | 0.403
3251 | 0.522
3252 | 0.674
3253 | 0.638
3254 | 0.82501
3255 | 0.585
3256 | 0.532
3257 | 0.399
3258 | 0.152
3259 | 0.038
3260 | 0
3261 | 0
3262 | 0
3263 | 0
3264 | 0
3265 | 0
3266 | 0
3267 | 0
3268 | 0
3269 | 0.01
3270 | 0.041
3271 | 0.149
3272 | 0.358
3273 | 0.435
3274 | 0.556
3275 | 0.448
3276 | 0.461
3277 | 0.559
3278 | 0.512
3279 | 0.523
3280 | 0.424
3281 | 0.353
3282 | 0.194
3283 | 0.055
3284 | 0
3285 | 0
3286 | 0
3287 | 0
3288 | 0
3289 | 0
3290 | 0
3291 | 0
3292 | 0
3293 | 0.014
3294 | 0.165
3295 | 0.336
3296 | 0.527
3297 | 0.678
3298 | 0.82401
3299 | 0.92101
3300 | 0.94501
3301 | 0.91001
3302 | 0.87101
3303 | 0.739
3304 | 0.572
3305 | 0.375
3306 | 0.039
3307 | 0.006
3308 | 0
3309 | 0
3310 | 0
3311 | 0
3312 | 0
3313 | 0
3314 | 0
3315 | 0
3316 | 0
3317 | 0.002
3318 | 0.037
3319 | 0.152
3320 | 0.129
3321 | 0.077
3322 | 0.153
3323 | 0.11
3324 | 0.168
3325 | 0.132
3326 | 0.096
3327 | 0.065
3328 | 0.09
3329 | 0.106
3330 | 0.026
3331 | 0.017
3332 | 0
3333 | 0
3334 | 0
3335 | 0
3336 | 0
3337 | 0
3338 | 0
3339 | 0
3340 | 0
3341 | 0.002
3342 | 0.015
3343 | 0.03
3344 | 0.169
3345 | 0.125
3346 | 0.127
3347 | 0.136
3348 | 0.273
3349 | 0.333
3350 | 0.103
3351 | 0.113
3352 | 0.1
3353 | 0.047
3354 | 0.052
3355 | 0.036
3356 | 0
3357 | 0
3358 | 0
3359 | 0
3360 | 0
3361 | 0
3362 | 0
3363 | 0
3364 | 0
3365 | 0.017
3366 | 0.085
3367 | 0.033
3368 | 0.069
3369 | 0.185
3370 | 0.246
3371 | 0.317
3372 | 0.113
3373 | 0.088
3374 | 0.075
3375 | 0.115
3376 | 0.105
3377 | 0.177
3378 | 0.12
3379 | 0.064
3380 | 0
3381 | 0
3382 | 0
3383 | 0
3384 | 0
3385 | 0
3386 | 0
3387 | 0
3388 | 0
3389 | 0.011
3390 | 0.03
3391 | 0.136
3392 | 0.415
3393 | 0.534
3394 | 0.694
3395 | 0.505
3396 | 0.108
3397 | 0.174
3398 | 0.151
3399 | 0.387
3400 | 0.255
3401 | 0.247
3402 | 0.091
3403 | 0.039
3404 | 0
3405 | 0
3406 | 0
3407 | 0
3408 | 0
3409 | 0
3410 | 0
3411 | 0
3412 | 0
3413 | 0.008
3414 | 0.017
3415 | 0.058
3416 | 0.231
3417 | 0.425
3418 | 0.474
3419 | 0.254
3420 | 0.392
3421 | 0.295
3422 | 0.366
3423 | 0.415
3424 | 0.394
3425 | 0.222
3426 | 0.12
3427 | 0.067
3428 | 0
3429 | 0
3430 | 0
3431 | 0
3432 | 0
3433 | 0
3434 | 0
3435 | 0
3436 | 0
3437 | 0.02
3438 | 0.144
3439 | 0.105
3440 | 0.146
3441 | 0.364
3442 | 0.535
3443 | 0.582
3444 | 0.64
3445 | 0.80201
3446 | 0.82301
3447 | 0.611
3448 | 0.364
3449 | 0.275
3450 | 0.039
3451 | 0.026
3452 | 0
3453 | 0
3454 | 0
3455 | 0
3456 | 0
3457 | 0
3458 | 0
3459 | 0
3460 | 0
3461 | 0.003
3462 | 0.024
3463 | 0.059
3464 | 0.23
3465 | 0.62
3466 | 0.66
3467 | 0.512
3468 | 0.729
3469 | 0.601
3470 | 0.076
3471 | 0.071
3472 | 0.155
3473 | 0.213
3474 | 0.148
3475 | 0.041
3476 | 0
3477 | 0
3478 | 0
3479 | 0
3480 | 0
3481 | 0
3482 | 0
3483 | 0
3484 | 0
3485 | 0.02
3486 | 0.026
3487 | 0.096
3488 | 0.092
3489 | 0.395
3490 | 0.112
3491 | 0.378
3492 | 0.084
3493 | 0.124
3494 | 0.106
3495 | 0.104
3496 | 0.181
3497 | 0.069
3498 | 0.078
3499 | 0.022
3500 | 0
3501 | 0
3502 | 0
3503 | 0
3504 | 0
3505 | 0
3506 | 0
3507 | 0
3508 | 0
3509 | 0.019
3510 | 0.148
3511 | 0.35
3512 | 0.532
3513 | 0.619
3514 | 0.325
3515 | 0.513
3516 | 0.633
3517 | 0.84901
3518 | 0.84501
3519 | 0.753
3520 | 0.595
3521 | 0.446
3522 | 0.26
3523 | 0.093
3524 | 0
3525 | 0
3526 | 0
3527 | 0
3528 | 0
3529 | 0
3530 | 0
3531 | 0
3532 | 0
3533 | 0.022
3534 | 0.18
3535 | 0.362
3536 | 0.531
3537 | 0.699
3538 | 0.781
3539 | 0.86801
3540 | 0.91301
3541 | 0.92101
3542 | 0.89001
3543 | 0.766
3544 | 0.597
3545 | 0.413
3546 | 0.254
3547 | 0.069
3548 | 0
3549 | 0
3550 | 0
3551 | 0
3552 | 0
3553 | 0
3554 | 0
3555 | 0
3556 | 0
3557 | 0.003
3558 | 0.16
3559 | 0.179
3560 | 0.267
3561 | 0.459
3562 | 0.71
3563 | 0.91501
3564 | 0.92801
3565 | 0.91801
3566 | 0.85701
3567 | 0.645
3568 | 0.32
3569 | 0.336
3570 | 0.244
3571 | 0.077
3572 | 0
3573 | 0
3574 | 0
3575 | 0
3576 | 0
3577 | 0
3578 | 0
3579 | 0
3580 | 0
3581 | 0.021
3582 | 0.069
3583 | 0.226
3584 | 0.119
3585 | 0.132
3586 | 0.3
3587 | 0.443
3588 | 0.39
3589 | 0.136
3590 | 0.707
3591 | 0.627
3592 | 0.378
3593 | 0.247
3594 | 0.051
3595 | 0.013
3596 | 0
3597 | 0
3598 | 0
3599 | 0
3600 | 0
3601 | 0
3602 | 0
3603 | 0
3604 | 0
3605 | 0.007
3606 | 0.079
3607 | 0.322
3608 | 0.451
3609 | 0.663
3610 | 0.763
3611 | 0.87601
3612 | 0.84801
3613 | 0.81001
3614 | 0.685
3615 | 0.534
3616 | 0.436
3617 | 0.434
3618 | 0.253
3619 | 0.087
3620 | 0
3621 | 0
3622 | 0
3623 | 0
3624 | 0
3625 | 0
3626 | 0
3627 | 0
3628 | 0
3629 | 0.027
3630 | 0.182
3631 | 0.351
3632 | 0.523
3633 | 0.681
3634 | 0.80601
3635 | 0.89101
3636 | 0.725
3637 | 0.747
3638 | 0.344
3639 | 0.704
3640 | 0.103
3641 | 0.18
3642 | 0.091
3643 | 0.009
3644 | 0
3645 | 0
3646 | 0
3647 | 0
3648 | 0
3649 | 0
3650 | 0
3651 | 0
3652 | 0
3653 | 0.025
3654 | 0.069
3655 | 0.198
3656 | 0.491
3657 | 0.505
3658 | 0.77
3659 | 0.772
3660 | 0.789
3661 | 0.89901
3662 | 0.83101
3663 | 0.744
3664 | 0.578
3665 | 0.423
3666 | 0.26
3667 | 0.095
3668 | 0
3669 | 0
3670 | 0
3671 | 0
3672 | 0
3673 | 0
3674 | 0
3675 | 0
3676 | 0
3677 | 0.027
3678 | 0.184
3679 | 0.353
3680 | 0.525
3681 | 0.683
3682 | 0.81201
3683 | 0.90101
3684 | 0.93801
3685 | 0.91901
3686 | 0.85001
3687 | 0.741
3688 | 0.604
3689 | 0.351
3690 | 0.251
3691 | 0.074
3692 | 0
3693 | 0
3694 | 0
3695 | 0
3696 | 0
3697 | 0
3698 | 0
3699 | 0
3700 | 0
3701 | 0.028
3702 | 0.187
3703 | 0.354
3704 | 0.526
3705 | 0.68
3706 | 0.80801
3707 | 0.89301
3708 | 0.93001
3709 | 0.91501
3710 | 0.84701
3711 | 0.739
3712 | 0.605
3713 | 0.434
3714 | 0.257
3715 | 0.097
3716 | 0
3717 | 0
3718 | 0
3719 | 0
3720 | 0
3721 | 0
3722 | 0
3723 | 0
3724 | 0
3725 | 0.028
3726 | 0.189
3727 | 0.36
3728 | 0.534
3729 | 0.687
3730 | 0.81301
3731 | 0.90301
3732 | 0.94001
3733 | 0.91601
3734 | 0.85201
3735 | 0.744
3736 | 0.604
3737 | 0.435
3738 | 0.259
3739 | 0.096
3740 | 0
3741 | 0
3742 | 0
3743 | 0
3744 | 0
3745 | 0
3746 | 0
3747 | 0
3748 | 0
3749 | 0.027
3750 | 0.194
3751 | 0.354
3752 | 0.535
3753 | 0.688
3754 | 0.81801
3755 | 0.90801
3756 | 0.94001
3757 | 0.92201
3758 | 0.85301
3759 | 0.73
3760 | 0.332
3761 | 0.163
3762 | 0.031
3763 | 0.051
3764 | 0
3765 | 0
3766 | 0
3767 | 0
3768 | 0
3769 | 0
3770 | 0
3771 | 0
3772 | 0
3773 | 0.03
3774 | 0.191
3775 | 0.36
3776 | 0.53
3777 | 0.685
3778 | 0.81401
3779 | 0.90401
3780 | 0.93601
3781 | 0.91801
3782 | 0.85401
3783 | 0.75
3784 | 0.61
3785 | 0.436
3786 | 0.264
3787 | 0.056
3788 | 0
3789 | 0
3790 | 0
3791 | 0
3792 | 0
3793 | 0
3794 | 0
3795 | 0
3796 | 0
3797 | 0.004
3798 | 0.063
3799 | 0.21
3800 | 0.281
3801 | 0.293
3802 | 0.481
3803 | 0.402
3804 | 0.749
3805 | 0.462
3806 | 0.62
3807 | 0.69
3808 | 0.473
3809 | 0.335
3810 | 0.159
3811 | 0.058
3812 | 0
3813 | 0
3814 | 0
3815 | 0
3816 | 0
3817 | 0
3818 | 0
3819 | 0
3820 | 0
3821 | 0.004
3822 | 0.026
3823 | 0.051
3824 | 0.084
3825 | 0.138
3826 | 0.136
3827 | 0.15
3828 | 0.136
3829 | 0.134
3830 | 0.12
3831 | 0.097
3832 | 0.095
3833 | 0.083
3834 | 0.065
3835 | 0.014
3836 | 0
3837 | 0
3838 | 0
3839 | 0
3840 | 0
3841 | 0
3842 | 0
3843 | 0
3844 | 0
3845 | 0.014
3846 | 0.037
3847 | 0.083
3848 | 0.142
3849 | 0.275
3850 | 0.373
3851 | 0.181
3852 | 0.394
3853 | 0.383
3854 | 0.292
3855 | 0.239
3856 | 0.351
3857 | 0.244
3858 | 0.151
3859 | 0.075
3860 | 0
3861 | 0
3862 | 0
3863 | 0
3864 | 0
3865 | 0
3866 | 0
3867 | 0
3868 | 0
3869 | 0.029
3870 | 0.125
3871 | 0.302
3872 | 0.466
3873 | 0.665
3874 | 0.77
3875 | 0.89601
3876 | 0.93801
3877 | 0.93001
3878 | 0.85801
3879 | 0.603
3880 | 0.495
3881 | 0.431
3882 | 0.163
3883 | 0.102
3884 | 0
3885 | 0
3886 | 0
3887 | 0
3888 | 0
3889 | 0
3890 | 0
3891 | 0
3892 | 0
3893 | 0.022
3894 | 0.174
3895 | 0.358
3896 | 0.512
3897 | 0.686
3898 | 0.803
3899 | 0.87301
3900 | 0.519
3901 | 0.85001
3902 | 0.645
3903 | 0.119
3904 | 0.5
3905 | 0.212
3906 | 0.246
3907 | 0.068
3908 | 0
3909 | 0
3910 | 0
3911 | 0
3912 | 0
3913 | 0
3914 | 0
3915 | 0
3916 | 0
3917 | 0.011
3918 | 0.134
3919 | 0.149
3920 | 0.172
3921 | 0.555
3922 | 0.601
3923 | 0.627
3924 | 0.85201
3925 | 0.92201
3926 | 0.85901
3927 | 0.745
3928 | 0.608
3929 | 0.445
3930 | 0.263
3931 | 0.092
3932 | 0
3933 | 0
3934 | 0
3935 | 0
3936 | 0
3937 | 0
3938 | 0
3939 | 0
3940 | 0
3941 | 0.03
3942 | 0.175
3943 | 0.256
3944 | 0.38
3945 | 0.598
3946 | 0.652
3947 | 0.508
3948 | 0.5
3949 | 0.374
3950 | 0.441
3951 | 0.695
3952 | 0.511
3953 | 0.079
3954 | 0.033
3955 | 0.022
3956 | 0
3957 | 0
3958 | 0
3959 | 0
3960 | 0
3961 | 0
3962 | 0
3963 | 0
3964 | 0
3965 | 0.025
3966 | 0.031
3967 | 0.067
3968 | 0.086
3969 | 0.113
3970 | 0.129
3971 | 0.155
3972 | 0.168
3973 | 0.339
3974 | 0.298
3975 | 0.261
3976 | 0.195
3977 | 0.113
3978 | 0.051
3979 | 0.015
3980 | 0
3981 | 0
3982 | 0
3983 | 0
3984 | 0
3985 | 0
3986 | 0
3987 | 0
3988 | 0
3989 | 0.004
3990 | 0.06
3991 | 0.127
3992 | 0.192
3993 | 0.192
3994 | 0.254
3995 | 0.145
3996 | 0.323
3997 | 0.389
3998 | 0.231
3999 | 0.126
4000 | 0.103
4001 | 0.121
4002 | 0.13
4003 | 0.096
4004 | 0
4005 | 0
4006 | 0
4007 | 0
4008 | 0
4009 | 0
4010 | 0
4011 | 0
4012 | 0
4013 | 0.013
4014 | 0.128
4015 | 0.298
4016 | 0.512
4017 | 0.672
4018 | 0.803
4019 | 0.87401
4020 | 0.88701
4021 | 0.775
4022 | 0.688
4023 | 0.682
4024 | 0.481
4025 | 0.395
4026 | 0.225
4027 | 0.108
4028 | 0
4029 | 0
4030 | 0
4031 | 0
4032 | 0
4033 | 0
4034 | 0
4035 | 0
4036 | 0
4037 | 0.026
4038 | 0.117
4039 | 0.288
4040 | 0.252
4041 | 0.464
4042 | 0.307
4043 | 0.122
4044 | 0.445
4045 | 0.166
4046 | 0.117
4047 | 0.136
4048 | 0.165
4049 | 0.198
4050 | 0.085
4051 | 0.084
4052 | 0
4053 | 0
4054 | 0
4055 | 0
4056 | 0
4057 | 0
4058 | 0
4059 | 0
4060 | 0
4061 | 0.017
4062 | 0.026
4063 | 0.101
4064 | 0.303
4065 | 0.489
4066 | 0.735
4067 | 0.85501
4068 | 0.91101
4069 | 0.84301
4070 | 0.747
4071 | 0.714
4072 | 0.524
4073 | 0.361
4074 | 0.186
4075 | 0.062
4076 | 0
4077 | 0
4078 | 0
4079 | 0
4080 | 0
4081 | 0
4082 | 0
4083 | 0
4084 | 0
4085 | 0.008
4086 | 0.034
4087 | 0.052
4088 | 0.133
4089 | 0.21
4090 | 0.253
4091 | 0.465
4092 | 0.334
4093 | 0.728
4094 | 0.525
4095 | 0.291
4096 | 0.264
4097 | 0.218
4098 | 0.268
4099 | 0.057
4100 | 0
4101 | 0
4102 | 0
4103 | 0
4104 | 0
4105 | 0
4106 | 0
4107 | 0
4108 | 0
4109 | 0.009
4110 | 0.017
4111 | 0.138
4112 | 0.133
4113 | 0.221
4114 | 0.195
4115 | 0.2
4116 | 0.505
4117 | 0.102
4118 | 0.166
4119 | 0.195
4120 | 0.48
4121 | 0.216
4122 | 0.157
4123 | 0.043
4124 | 0
4125 | 0
4126 | 0
4127 | 0
4128 | 0
4129 | 0
4130 | 0
4131 | 0
4132 | 0
4133 | 0.008
4134 | 0.175
4135 | 0.288
4136 | 0.447
4137 | 0.609
4138 | 0.726
4139 | 0.813
4140 | 0.795
4141 | 0.45
4142 | 0.236
4143 | 0.148
4144 | 0.207
4145 | 0.102
4146 | 0.042
4147 | 0.053
4148 | 0
4149 | 0
4150 | 0
4151 | 0
4152 | 0
4153 | 0
4154 | 0
4155 | 0
4156 | 0
4157 | 0.004
4158 | 0.103
4159 | 0.11
4160 | 0.391
4161 | 0.484
4162 | 0.437
4163 | 0.522
4164 | 0.619
4165 | 0.655
4166 | 0.779
4167 | 0.422
4168 | 0.186
4169 | 0.229
4170 | 0.129
4171 | 0.052
4172 | 0
4173 | 0
4174 | 0
4175 | 0
4176 | 0
4177 | 0
4178 | 0
4179 | 0
4180 | 0
4181 | 0.03
4182 | 0.196
4183 | 0.363
4184 | 0.538
4185 | 0.689
4186 | 0.817
4187 | 0.90401
4188 | 0.94401
4189 | 0.93301
4190 | 0.86801
4191 | 0.763
4192 | 0.632
4193 | 0.467
4194 | 0.291
4195 | 0.13
4196 | 0
4197 | 0
4198 | 0
4199 | 0
4200 | 0
4201 | 0
4202 | 0
4203 | 0
4204 | 0
4205 | 0.028
4206 | 0.176
4207 | 0.322
4208 | 0.45
4209 | 0.699
4210 | 0.779
4211 | 0.88501
4212 | 0.86201
4213 | 0.86201
4214 | 0.721
4215 | 0.507
4216 | 0.565
4217 | 0.452
4218 | 0.279
4219 | 0.127
4220 | 0
4221 | 0
4222 | 0
4223 | 0
4224 | 0
4225 | 0
4226 | 0
4227 | 0
4228 | 0
4229 | 0.028
4230 | 0.182
4231 | 0.359
4232 | 0.528
4233 | 0.681
4234 | 0.815
4235 | 0.89801
4236 | 0.91901
4237 | 0.89501
4238 | 0.86801
4239 | 0.72
4240 | 0.6
4241 | 0.395
4242 | 0.299
4243 | 0.073
4244 | 0
4245 | 0
4246 | 0
4247 | 0
4248 | 0
4249 | 0
4250 | 0
4251 | 0
4252 | 0
4253 | 0.029
4254 | 0.137
4255 | 0.189
4256 | 0.235
4257 | 0.571
4258 | 0.706
4259 | 0.382
4260 | 0.424
4261 | 0.85201
4262 | 0.608
4263 | 0.61
4264 | 0.601
4265 | 0.45
4266 | 0.287
4267 | 0.123
4268 | 0
4269 | 0
4270 | 0
4271 | 0
4272 | 0
4273 | 0
4274 | 0
4275 | 0
4276 | 0
4277 | 0.008
4278 | 0.173
4279 | 0.354
4280 | 0.526
4281 | 0.679
4282 | 0.785
4283 | 0.83801
4284 | 0.90401
4285 | 0.92301
4286 | 0.86301
4287 | 0.759
4288 | 0.629
4289 | 0.466
4290 | 0.276
4291 | 0.123
4292 | 0
4293 | 0
4294 | 0
4295 | 0
4296 | 0
4297 | 0
4298 | 0
4299 | 0
4300 | 0
4301 | 0.027
4302 | 0.056
4303 | 0.056
4304 | 0.293
4305 | 0.449
4306 | 0.792
4307 | 0.86501
4308 | 0.803
4309 | 0.804
4310 | 0.558
4311 | 0.618
4312 | 0.562
4313 | 0.403
4314 | 0.249
4315 | 0.122
4316 | 0
4317 | 0
4318 | 0
4319 | 0
4320 | 0
4321 | 0
4322 | 0
4323 | 0
4324 | 0
4325 | 0.026
4326 | 0.188
4327 | 0.356
4328 | 0.532
4329 | 0.687
4330 | 0.82
4331 | 0.90901
4332 | 0.94601
4333 | 0.93601
4334 | 0.87201
4335 | 0.763
4336 | 0.632
4337 | 0.469
4338 | 0.292
4339 | 0.13
4340 | 0
4341 | 0
4342 | 0
4343 | 0
4344 | 0
4345 | 0
4346 | 0
4347 | 0
4348 | 0
4349 | 0.025
4350 | 0.191
4351 | 0.36
4352 | 0.529
4353 | 0.684
4354 | 0.809
4355 | 0.90101
4356 | 0.93801
4357 | 0.92401
4358 | 0.87301
4359 | 0.769
4360 | 0.622
4361 | 0.458
4362 | 0.288
4363 | 0.119
4364 | 0
4365 | 0
4366 | 0
4367 | 0
4368 | 0
4369 | 0
4370 | 0
4371 | 0
4372 | 0
4373 | 0.026
4374 | 0.185
4375 | 0.353
4376 | 0.52
4377 | 0.676
4378 | 0.804
4379 | 0.89201
4380 | 0.93301
4381 | 0.91401
4382 | 0.86001
4383 | 0.757
4384 | 0.612
4385 | 0.442
4386 | 0.275
4387 | 0.123
4388 | 0
4389 | 0
4390 | 0
4391 | 0
4392 | 0
4393 | 0
4394 | 0
4395 | 0
4396 | 0
4397 | 0.004
4398 | 0.174
4399 | 0.251
4400 | 0.5
4401 | 0.661
4402 | 0.79
4403 | 0.88201
4404 | 0.92701
4405 | 0.91401
4406 | 0.85501
4407 | 0.745
4408 | 0.602
4409 | 0.421
4410 | 0.276
4411 | 0.072
4412 | 0
4413 | 0
4414 | 0
4415 | 0
4416 | 0
4417 | 0
4418 | 0
4419 | 0
4420 | 0
4421 | 0.024
4422 | 0.161
4423 | 0.335
4424 | 0.507
4425 | 0.66
4426 | 0.802
4427 | 0.86701
4428 | 0.92701
4429 | 0.91801
4430 | 0.85901
4431 | 0.741
4432 | 0.599
4433 | 0.441
4434 | 0.279
4435 | 0.118
4436 | 0
4437 | 0
4438 | 0
4439 | 0
4440 | 0
4441 | 0
4442 | 0
4443 | 0
4444 | 0
4445 | 0.018
4446 | 0.16
4447 | 0.319
4448 | 0.5
4449 | 0.662
4450 | 0.792
4451 | 0.88401
4452 | 0.92101
4453 | 0.90801
4454 | 0.537
4455 | 0.748
4456 | 0.611
4457 | 0.422
4458 | 0.249
4459 | 0.011
4460 | 0
4461 | 0
4462 | 0
4463 | 0
4464 | 0
4465 | 0
4466 | 0
4467 | 0
4468 | 0
4469 | 0.021
4470 | 0.159
4471 | 0.178
4472 | 0.263
4473 | 0.571
4474 | 0.754
4475 | 0.84301
4476 | 0.88701
4477 | 0.87401
4478 | 0.83601
4479 | 0.705
4480 | 0.61
4481 | 0.447
4482 | 0.279
4483 | 0.113
4484 | 0
4485 | 0
4486 | 0
4487 | 0
4488 | 0
4489 | 0
4490 | 0
4491 | 0
4492 | 0
4493 | 0.005
4494 | 0.138
4495 | 0.332
4496 | 0.505
4497 | 0.663
4498 | 0.794
4499 | 0.88701
4500 | 0.88101
4501 | 0.87301
4502 | 0.86201
4503 | 0.759
4504 | 0.613
4505 | 0.442
4506 | 0.045
4507 | 0.098
4508 | 0
4509 | 0
4510 | 0
4511 | 0
4512 | 0
4513 | 0
4514 | 0
4515 | 0
4516 | 0
4517 | 0.003
4518 | 0.061
4519 | 0.041
4520 | 0.073
4521 | 0.284
4522 | 0.128
4523 | 0.315
4524 | 0.355
4525 | 0.182
4526 | 0.165
4527 | 0.244
4528 | 0.491
4529 | 0.233
4530 | 0.133
4531 | 0.083
4532 | 0
4533 | 0
4534 | 0
4535 | 0
4536 | 0
4537 | 0
4538 | 0
4539 | 0
4540 | 0
4541 | 0.015
4542 | 0.075
4543 | 0.227
4544 | 0.439
4545 | 0.616
4546 | 0.283
4547 | 0.504
4548 | 0.528
4549 | 0.346
4550 | 0.603
4551 | 0.527
4552 | 0.545
4553 | 0.392
4554 | 0.188
4555 | 0.073
4556 | 0
4557 | 0
4558 | 0
4559 | 0
4560 | 0
4561 | 0
4562 | 0
4563 | 0
4564 | 0
4565 | 0.018
4566 | 0.165
4567 | 0.339
4568 | 0.513
4569 | 0.668
4570 | 0.798
4571 | 0.88801
4572 | 0.93501
4573 | 0.92201
4574 | 0.86801
4575 | 0.76
4576 | 0.626
4577 | 0.461
4578 | 0.292
4579 | 0.123
4580 | 0
4581 | 0
4582 | 0
4583 | 0
4584 | 0
4585 | 0
4586 | 0
4587 | 0
4588 | 0
4589 | 0.017
4590 | 0.16
4591 | 0.309
4592 | 0.428
4593 | 0.667
4594 | 0.79701
4595 | 0.87301
4596 | 0.92001
4597 | 0.91201
4598 | 0.81901
4599 | 0.701
4600 | 0.613
4601 | 0.453
4602 | 0.281
4603 | 0.106
4604 | 0
4605 | 0
4606 | 0
4607 | 0
4608 | 0
4609 | 0
4610 | 0
4611 | 0
4612 | 0
4613 | 0.017
4614 | 0.164
4615 | 0.331
4616 | 0.502
4617 | 0.648
4618 | 0.779
4619 | 0.87601
4620 | 0.91401
4621 | 0.84501
4622 | 0.83601
4623 | 0.697
4624 | 0.571
4625 | 0.335
4626 | 0.226
4627 | 0.122
4628 | 0
4629 | 0
4630 | 0
4631 | 0
4632 | 0
4633 | 0
4634 | 0
4635 | 0
4636 | 0
4637 | 0.002
4638 | 0.015
4639 | 0.153
4640 | 0.262
4641 | 0.504
4642 | 0.668
4643 | 0.74
4644 | 0.603
4645 | 0.727
4646 | 0.582
4647 | 0.28
4648 | 0.51
4649 | 0.37
4650 | 0.266
4651 | 0.061
4652 | 0
4653 | 0
4654 | 0
4655 | 0
4656 | 0
4657 | 0
4658 | 0
4659 | 0
4660 | 0
4661 | 0.016
4662 | 0.157
4663 | 0.326
4664 | 0.5
4665 | 0.662
4666 | 0.79201
4667 | 0.86901
4668 | 0.91201
4669 | 0.90401
4670 | 0.85101
4671 | 0.741
4672 | 0.607
4673 | 0.438
4674 | 0.27
4675 | 0.107
4676 | 0
4677 | 0
4678 | 0
4679 | 0
4680 | 0
4681 | 0
4682 | 0
4683 | 0
4684 | 0
4685 | 0.011
4686 | 0.151
4687 | 0.324
4688 | 0.498
4689 | 0.656
4690 | 0.78601
4691 | 0.88501
4692 | 0.92401
4693 | 0.91201
4694 | 0.85901
4695 | 0.755
4696 | 0.618
4697 | 0.448
4698 | 0.278
4699 | 0.112
4700 | 0
4701 | 0
4702 | 0
4703 | 0
4704 | 0
4705 | 0
4706 | 0
4707 | 0
4708 | 0
4709 | 0.011
4710 | 0.148
4711 | 0.296
4712 | 0.466
4713 | 0.648
4714 | 0.78101
4715 | 0.87501
4716 | 0.91801
4717 | 0.90601
4718 | 0.85301
4719 | 0.742
4720 | 0.61
4721 | 0.442
4722 | 0.274
4723 | 0.109
4724 | 0
4725 | 0
4726 | 0
4727 | 0
4728 | 0
4729 | 0
4730 | 0
4731 | 0
4732 | 0
4733 | 0.008
4734 | 0.138
4735 | 0.306
4736 | 0.477
4737 | 0.629
4738 | 0.755
4739 | 0.84201
4740 | 0.89401
4741 | 0.81701
4742 | 0.088
4743 | 0.067
4744 | 0.369
4745 | 0.31
4746 | 0.024
4747 | 0.039
4748 | 0
4749 | 0
4750 | 0
4751 | 0
4752 | 0
4753 | 0
4754 | 0
4755 | 0
4756 | 0
4757 | 0.007
4758 | 0.099
4759 | 0.06
4760 | 0.048
4761 | 0.099
4762 | 0.196
4763 | 0.376
4764 | 0.114
4765 | 0.099
4766 | 0.80301
4767 | 0.747
4768 | 0.604
4769 | 0.441
4770 | 0.269
4771 | 0.035
4772 | 0
4773 | 0
4774 | 0
4775 | 0
4776 | 0
4777 | 0
4778 | 0
4779 | 0
4780 | 0
4781 | 0.002
4782 | 0.139
4783 | 0.219
4784 | 0.473
4785 | 0.522
4786 | 0.708
4787 | 0.81301
4788 | 0.90001
4789 | 0.80901
4790 | 0.718
4791 | 0.401
4792 | 0.522
4793 | 0.084
4794 | 0.191
4795 | 0.046
4796 | 0
4797 | 0
4798 | 0
4799 | 0
4800 | 0
4801 | 0
4802 | 0
4803 | 0
4804 | 0
4805 | 0.006
4806 | 0.13
4807 | 0.312
4808 | 0.493
4809 | 0.647
4810 | 0.77401
4811 | 0.86401
4812 | 0.90301
4813 | 0.90101
4814 | 0.85201
4815 | 0.744
4816 | 0.61
4817 | 0.44
4818 | 0.266
4819 | 0.105
4820 | 0
4821 | 0
4822 | 0
4823 | 0
4824 | 0
4825 | 0
4826 | 0
4827 | 0
4828 | 0
4829 | 0
4830 | 0.151
4831 | 0.321
4832 | 0.495
4833 | 0.651
4834 | 0.78301
4835 | 0.87101
4836 | 0.91101
4837 | 0.90401
4838 | 0.85401
4839 | 0.746
4840 | 0.612
4841 | 0.445
4842 | 0.274
4843 | 0.105
4844 | 0
4845 | 0
4846 | 0
4847 | 0
4848 | 0
4849 | 0
4850 | 0
4851 | 0
4852 | 0
4853 | 0
4854 | 0.127
4855 | 0.306
4856 | 0.481
4857 | 0.629
4858 | 0.77401
4859 | 0.84801
4860 | 0.91401
4861 | 0.89801
4862 | 0.83601
4863 | 0.469
4864 | 0.054
4865 | 0.039
4866 | 0.051
4867 | 0.042
4868 | 0
4869 | 0
4870 | 0
4871 | 0
4872 | 0
4873 | 0
4874 | 0
4875 | 0
4876 | 0
4877 | 0
4878 | 0.118
4879 | 0.045
4880 | 0.144
4881 | 0.171
4882 | 0.103
4883 | 0.264
4884 | 0.263
4885 | 0.518
4886 | 0.359
4887 | 0.599
4888 | 0.407
4889 | 0.349
4890 | 0.144
4891 | 0.055
4892 | 0
4893 | 0
4894 | 0
4895 | 0
4896 | 0
4897 | 0
4898 | 0
4899 | 0
4900 | 0
4901 | 0
4902 | 0.127
4903 | 0.296
4904 | 0.474
4905 | 0.635
4906 | 0.76601
4907 | 0.86201
4908 | 0.91001
4909 | 0.89401
4910 | 0.83701
4911 | 0.73
4912 | 0.427
4913 | 0.039
4914 | 0.023
4915 | 0.033
4916 | 0
4917 | 0
4918 | 0
4919 | 0
4920 | 0
4921 | 0
4922 | 0
4923 | 0
4924 | 0
4925 | 0
4926 | 0.114
4927 | 0.173
4928 | 0.089
4929 | 0.17
4930 | 0.49
4931 | 0.192
4932 | 0.081
4933 | 0.102
4934 | 0.091
4935 | 0.088
4936 | 0.132
4937 | 0.078
4938 | 0.149
4939 | 0.092
4940 | 0
4941 | 0
4942 | 0
4943 | 0
4944 | 0
4945 | 0
4946 | 0
4947 | 0
4948 | 0
4949 | 0
4950 | 0.135
4951 | 0.299
4952 | 0.437
4953 | 0.585
4954 | 0.73801
4955 | 0.664
4956 | 0.623
4957 | 0.347
4958 | 0.388
4959 | 0.2
4960 | 0.403
4961 | 0.053
4962 | 0.039
4963 | 0.016
4964 | 0
4965 | 0
4966 | 0
4967 | 0
4968 | 0
4969 | 0
4970 | 0
4971 | 0
4972 | 0
4973 | 0
4974 | 0.016
4975 | 0.271
4976 | 0.374
4977 | 0.58
4978 | 0.72
4979 | 0.653
4980 | 0.87701
4981 | 0.756
4982 | 0.732
4983 | 0.724
4984 | 0.593
4985 | 0.437
4986 | 0.262
4987 | 0.088
4988 | 0
4989 | 0
4990 | 0
4991 | 0
4992 | 0
4993 | 0
4994 | 0
4995 | 0
4996 | 0
4997 | 0
4998 | 0.021
4999 | 0.176
5000 | 0.072
5001 | 0.301
5002 | 0.224
5003 | 0.112
5004 | 0.215
5005 | 0.307
5006 | 0.337
5007 | 0.086
5008 | 0.288
5009 | 0.177
5010 | 0.245
5011 | 0.061
5012 | 0
5013 | 0
5014 | 0
5015 | 0
5016 | 0
5017 | 0
5018 | 0
5019 | 0
5020 | 0
5021 | 0
5022 | 0.067
5023 | 0.086
5024 | 0.14
5025 | 0.181
5026 | 0.236
5027 | 0.208
5028 | 0.128
5029 | 0.167
5030 | 0.162
5031 | 0.117
5032 | 0.078
5033 | 0.135
5034 | 0.116
5035 | 0.034
5036 | 0
5037 | 0
5038 | 0
5039 | 0
5040 | 0
5041 | 0
5042 | 0
5043 | 0
5044 | 0
5045 | 0
5046 | 0.059
5047 | 0.167
5048 | 0.342
5049 | 0.496
5050 | 0.64
5051 | 0.635
5052 | 0.733
5053 | 0.76401
5054 | 0.73901
5055 | 0.62
5056 | 0.445
5057 | 0.246
5058 | 0.119
5059 | 0.052
5060 | 0
5061 | 0
5062 | 0
5063 | 0
5064 | 0
5065 | 0
5066 | 0
5067 | 0
5068 | 0
5069 | 0
5070 | 0.117
5071 | 0.29
5072 | 0.465
5073 | 0.622
5074 | 0.74701
5075 | 0.84301
5076 | 0.87401
5077 | 0.87101
5078 | 0.80501
5079 | 0.614
5080 | 0.272
5081 | 0.38
5082 | 0.149
5083 | 0.015
5084 | 0
5085 | 0
5086 | 0
5087 | 0
5088 | 0
5089 | 0
5090 | 0
5091 | 0
5092 | 0
5093 | 0
5094 | 0.01
5095 | 0.025
5096 | 0.239
5097 | 0.112
5098 | 0.151
5099 | 0.413
5100 | 0.571
5101 | 0.543
5102 | 0.438
5103 | 0.16
5104 | 0.078
5105 | 0.06
5106 | 0.028
5107 | 0.014
5108 | 0
5109 | 0
5110 | 0
5111 | 0
5112 | 0
5113 | 0
5114 | 0
5115 | 0
5116 | 0
5117 | 0
5118 | 0.089
5119 | 0.204
5120 | 0.249
5121 | 0.308
5122 | 0.664
5123 | 0.81501
5124 | 0.722
5125 | 0.89601
5126 | 0.83201
5127 | 0.72201
5128 | 0.579
5129 | 0.411
5130 | 0.24
5131 | 0.074
5132 | 0
5133 | 0
5134 | 0
5135 | 0
5136 | 0
5137 | 0
5138 | 0
5139 | 0
5140 | 0
5141 | 0
5142 | 0.111
5143 | 0.286
5144 | 0.461
5145 | 0.622
5146 | 0.75301
5147 | 0.85101
5148 | 0.89601
5149 | 0.89301
5150 | 0.82501
5151 | 0.71601
5152 | 0.576
5153 | 0.41
5154 | 0.24
5155 | 0.07
5156 | 0
5157 | 0
5158 | 0
5159 | 0
5160 | 0
5161 | 0
5162 | 0
5163 | 0
5164 | 0
5165 | 0
5166 | 0.033
5167 | 0.221
5168 | 0.265
5169 | 0.532
5170 | 0.56
5171 | 0.15
5172 | 0.492
5173 | 0.238
5174 | 0.105
5175 | 0.081
5176 | 0.46
5177 | 0.397
5178 | 0.194
5179 | 0.055
5180 | 0
5181 | 0
5182 | 0
5183 | 0
5184 | 0
5185 | 0
5186 | 0
5187 | 0
5188 | 0
5189 | 0
5190 | 0.009
5191 | 0.274
5192 | 0.446
5193 | 0.598
5194 | 0.74101
5195 | 0.82901
5196 | 0.89101
5197 | 0.88801
5198 | 0.81601
5199 | 0.70701
5200 | 0.564
5201 | 0.399
5202 | 0.227
5203 | 0.058
5204 | 0
5205 | 0
5206 | 0
5207 | 0
5208 | 0
5209 | 0
5210 | 0
5211 | 0
5212 | 0
5213 | 0
5214 | 0.088
5215 | 0.141
5216 | 0.4
5217 | 0.602
5218 | 0.73401
5219 | 0.83501
5220 | 0.88001
5221 | 0.85101
5222 | 0.76801
5223 | 0.70001
5224 | 0.561
5225 | 0.392
5226 | 0.214
5227 | 0.038
5228 | 0
5229 | 0
5230 | 0
5231 | 0
5232 | 0
5233 | 0
5234 | 0
5235 | 0
5236 | 0
5237 | 0
5238 | 0.064
5239 | 0.024
5240 | 0.185
5241 | 0.119
5242 | 0.434
5243 | 0.498
5244 | 0.75701
5245 | 0.86101
5246 | 0.81001
5247 | 0.69701
5248 | 0.558
5249 | 0.391
5250 | 0.22
5251 | 0.05248
5252 | 0
5253 | 0
5254 | 0
5255 | 0
5256 | 0
5257 | 0
5258 | 0
5259 | 0
5260 | 0
5261 | 0
5262 | 0.076
5263 | 0.263
5264 | 0.437
5265 | 0.602
5266 | 0.73301
5267 | 0.82601
5268 | 0.86601
5269 | 0.84501
5270 | 0.79501
5271 | 0.69001
5272 | 0.546
5273 | 0.377
5274 | 0.207
5275 | 0.0442
5276 | 0
5277 | 0
5278 | 0
5279 | 0
5280 | 0
5281 | 0
5282 | 0
5283 | 0
5284 | 0
5285 | 0
5286 | 0.061
5287 | 0.216
5288 | 0.421
5289 | 0.572
5290 | 0.5
5291 | 0.443
5292 | 0.246
5293 | 0.544
5294 | 0.70601
5295 | 0.062
5296 | 0.055
5297 | 0.136
5298 | 0.019
5299 | 0.017
5300 | 0
5301 | 0
5302 | 0
5303 | 0
5304 | 0
5305 | 0
5306 | 0
5307 | 0
5308 | 0
5309 | 0
5310 | 0.046
5311 | 0.115
5312 | 0.396
5313 | 0.524
5314 | 0.574
5315 | 0.669
5316 | 0.624
5317 | 0.569
5318 | 0.513
5319 | 0.567
5320 | 0.446
5321 | 0.339
5322 | 0.018
5323 | 0.004
5324 | 0
5325 | 0
5326 | 0
5327 | 0
5328 | 0
5329 | 0
5330 | 0
5331 | 0
5332 | 0
5333 | 0
5334 | 0.018
5335 | 0.059
5336 | 0.287
5337 | 0.466
5338 | 0.496
5339 | 0.73801
5340 | 0.79601
5341 | 0.85401
5342 | 0.76201
5343 | 0.61
5344 | 0.507
5345 | 0.337
5346 | 0.195
5347 | 0.03707
5348 | 0
5349 | 0
5350 | 0
5351 | 0
5352 | 0
5353 | 0
5354 | 0
5355 | 0
5356 | 0
5357 | 0
5358 | 0.063
5359 | 0.225
5360 | 0.404
5361 | 0.576
5362 | 0.70701
5363 | 0.79001
5364 | 0.83701
5365 | 0.85101
5366 | 0.79101
5367 | 0.68001
5368 | 0.537
5369 | 0.353
5370 | 0.197
5371 | 0.03438
5372 | 0
5373 | 0
5374 | 0
5375 | 0
5376 | 0
5377 | 0
5378 | 0
5379 | 0
5380 | 0
5381 | 0
5382 | 0.069
5383 | 0.239
5384 | 0.414
5385 | 0.582
5386 | 0.71901
5387 | 0.81601
5388 | 0.86101
5389 | 0.85601
5390 | 0.78701
5391 | 0.67001
5392 | 0.528
5393 | 0.298
5394 | 0.188
5395 | 0.0302
5396 | 0
5397 | 0
5398 | 0
5399 | 0
5400 | 0
5401 | 0
5402 | 0
5403 | 0
5404 | 0
5405 | 0
5406 | 0.007
5407 | 0.098
5408 | 0.346
5409 | 0.2
5410 | 0.07
5411 | 0.194
5412 | 0.158
5413 | 0.291
5414 | 0.112
5415 | 0.084
5416 | 0.048
5417 | 0.119
5418 | 0.019
5419 | 0.02331
5420 | 0
5421 | 0
5422 | 0
5423 | 0
5424 | 0
5425 | 0
5426 | 0
5427 | 0
5428 | 0
5429 | 0
5430 | 0.01
5431 | 0.113
5432 | 0.186
5433 | 0.098
5434 | 0.214
5435 | 0.184
5436 | 0.117
5437 | 0.114
5438 | 0.133
5439 | 0.133
5440 | 0.081
5441 | 0.051
5442 | 0.088
5443 | 0.011
5444 | 0
5445 | 0
5446 | 0
5447 | 0
5448 | 0
5449 | 0
5450 | 0
5451 | 0
5452 | 0
5453 | 0
5454 | 0.018
5455 | 0.023
5456 | 0.101
5457 | 0.131
5458 | 0.221
5459 | 0.285
5460 | 0.162
5461 | 0.284
5462 | 0.09
5463 | 0.085
5464 | 0.076
5465 | 0.067
5466 | 0.024
5467 | 0.003
5468 | 0
5469 | 0
5470 | 0
5471 | 0
5472 | 0
5473 | 0
5474 | 0
5475 | 0
5476 | 0
5477 | 0
5478 | 0.014
5479 | 0.192
5480 | 0.207
5481 | 0.383
5482 | 0.331
5483 | 0.383
5484 | 0.662
5485 | 0.607
5486 | 0.387
5487 | 0.297
5488 | 0.179
5489 | 0.132
5490 | 0.055
5491 | 0.009
5492 | 0
5493 | 0
5494 | 0
5495 | 0
5496 | 0
5497 | 0
5498 | 0
5499 | 0
5500 | 0
5501 | 0
5502 | 0.027
5503 | 0.089
5504 | 0.249
5505 | 0.423
5506 | 0.68201
5507 | 0.587
5508 | 0.68101
5509 | 0.407
5510 | 0.278
5511 | 0.094
5512 | 0.123
5513 | 0.14
5514 | 0.11
5515 | 0.012
5516 | 0
5517 | 0
5518 | 0
5519 | 0
5520 | 0
5521 | 0
5522 | 0
5523 | 0
5524 | 0
5525 | 0
5526 | 0.027
5527 | 0.035
5528 | 0.078
5529 | 0.078
5530 | 0.136
5531 | 0.097
5532 | 0.106
5533 | 0.114
5534 | 0.135
5535 | 0.08
5536 | 0.091
5537 | 0.078
5538 | 0.069
5539 | 0.01182
5540 | 0
5541 | 0
5542 | 0
5543 | 0
5544 | 0
5545 | 0
5546 | 0
5547 | 0
5548 | 0
5549 | 0
5550 | 0.049
5551 | 0.193
5552 | 0.337
5553 | 0.479
5554 | 0.64401
5555 | 0.73801
5556 | 0.68401
5557 | 0.71401
5558 | 0.65601
5559 | 0.529
5560 | 0.449
5561 | 0.297
5562 | 0.098
5563 | 0.005
5564 | 0
5565 | 0
5566 | 0
5567 | 0
5568 | 0
5569 | 0
5570 | 0
5571 | 0
5572 | 0
5573 | 0
5574 | 0.044
5575 | 0.193
5576 | 0.393
5577 | 0.563
5578 | 0.69401
5579 | 0.79101
5580 | 0.83001
5581 | 0.82401
5582 | 0.75801
5583 | 0.64801
5584 | 0.499
5585 | 0.334
5586 | 0.161
5587 | 0
5588 | 0
5589 | 0
5590 | 0
5591 | 0
5592 | 0
5593 | 0
5594 | 0
5595 | 0
5596 | 0
5597 | 0
5598 | 0.04531
5599 | 0.22
5600 | 0.398
5601 | 0.55901
5602 | 0.69101
5603 | 0.78701
5604 | 0.82701
5605 | 0.81601
5606 | 0.75001
5607 | 0.64101
5608 | 0.495
5609 | 0.326
5610 | 0.154
5611 | 0
5612 | 0
5613 | 0
5614 | 0
5615 | 0
5616 | 0
5617 | 0
5618 | 0
5619 | 0
5620 | 0
5621 | 0
5622 | 0.03746
5623 | 0.183
5624 | 0.341
5625 | 0.525
5626 | 0.65201
5627 | 0.191
5628 | 0.11
5629 | 0.15
5630 | 0.188
5631 | 0.116
5632 | 0.074
5633 | 0.174
5634 | 0.038
5635 | 0
5636 | 0
5637 | 0
5638 | 0
5639 | 0
5640 | 0
5641 | 0
5642 | 0
5643 | 0
5644 | 0
5645 | 0
5646 | 0.03303
5647 | 0.04
5648 | 0.19
5649 | 0.3963
5650 | 0.484
5651 | 0.5149
5652 | 0.58156
5653 | 0.58556
5654 | 0.5117
5655 | 0.4108
5656 | 0.30365
5657 | 0.214
5658 | 0.10895
5659 | 0.00265
5660 | 0
5661 | 0
5662 | 0
5663 | 0
5664 | 0
5665 | 0
5666 | 0
5667 | 0
5668 | 0
5669 | 0
5670 | 0.03029
5671 | 0.179
5672 | 0.348
5673 | 0.479
5674 | 0.60701
5675 | 0.69001
5676 | 0.76601
5677 | 0.78001
5678 | 0.71801
5679 | 0.62401
5680 | 0.476
5681 | 0.302
5682 | 0.135
5683 | 0
5684 | 0
5685 | 0
5686 | 0
5687 | 0
5688 | 0
5689 | 0
5690 | 0
5691 | 0
5692 | 0
5693 | 0
5694 | 0.03646
5695 | 0.204
5696 | 0.384
5697 | 0.54301
5698 | 0.67701
5699 | 0.76601
5700 | 0.77901
5701 | 0.76401
5702 | 0.73301
5703 | 0.62301
5704 | 0.478
5705 | 0.308
5706 | 0.137
5707 | 0
5708 | 0
5709 | 0
5710 | 0
5711 | 0
5712 | 0
5713 | 0
5714 | 0
5715 | 0
5716 | 0
5717 | 0
5718 | 0.03246
5719 | 0.181
5720 | 0.354
5721 | 0.54001
5722 | 0.67701
5723 | 0.74601
5724 | 0.80001
5725 | 0.73901
5726 | 0.574
5727 | 0.396
5728 | 0.324
5729 | 0.3
5730 | 0.121
5731 | 0
5732 | 0
5733 | 0
5734 | 0
5735 | 0
5736 | 0
5737 | 0
5738 | 0
5739 | 0
5740 | 0
5741 | 0
5742 | 0.026
5743 | 0.184
5744 | 0.362
5745 | 0.328
5746 | 0.64601
5747 | 0.70801
5748 | 0.79201
5749 | 0.78001
5750 | 0.71701
5751 | 0.61001
5752 | 0.463
5753 | 0.301
5754 | 0.116
5755 | 0
5756 | 0
5757 | 0
5758 | 0
5759 | 0
5760 | 0
5761 | 0
5762 | 0
5763 | 0
5764 | 0
5765 | 0
5766 | 0.025
5767 | 0.196
5768 | 0.37
5769 | 0.53301
5770 | 0.66601
5771 | 0.75801
5772 | 0.80401
5773 | 0.78401
5774 | 0.72301
5775 | 0.61101
5776 | 0.463
5777 | 0.293
5778 | 0.119
5779 | 0
5780 | 0
5781 | 0
5782 | 0
5783 | 0
5784 | 0
5785 | 0
5786 | 0
5787 | 0
5788 | 0
5789 | 0
5790 | 0.021
5791 | 0.187
5792 | 0.361
5793 | 0.52901
5794 | 0.65901
5795 | 0.75101
5796 | 0.78801
5797 | 0.77601
5798 | 0.71101
5799 | 0.60001
5800 | 0.453
5801 | 0.284
5802 | 0.113
5803 | 0
5804 | 0
5805 | 0
5806 | 0
5807 | 0
5808 | 0
5809 | 0
5810 | 0
5811 | 0
5812 | 0
5813 | 0
5814 | 0.021
5815 | 0.183
5816 | 0.359
5817 | 0.52001
5818 | 0.64901
5819 | 0.74301
5820 | 0.78001
5821 | 0.76701
5822 | 0.69601
5823 | 0.58601
5824 | 0.438
5825 | 0.273
5826 | 0.105
5827 | 0
5828 | 0
5829 | 0
5830 | 0
5831 | 0
5832 | 0
5833 | 0
5834 | 0
5835 | 0
5836 | 0
5837 | 0
5838 | 0.004
5839 | 0.188
5840 | 0.139
5841 | 0.125
5842 | 0.111
5843 | 0.263
5844 | 0.156
5845 | 0.093
5846 | 0.1
5847 | 0.146
5848 | 0.293
5849 | 0.114
5850 | 0.01
5851 | 0
5852 | 0
5853 | 0
5854 | 0
5855 | 0
5856 | 0
5857 | 0
5858 | 0
5859 | 0
5860 | 0
5861 | 0
5862 | 0.003
5863 | 0.14
5864 | 0.371
5865 | 0.454
5866 | 0.496
5867 | 0.63201
5868 | 0.66201
5869 | 0.448
5870 | 0.168
5871 | 0.338
5872 | 0.344
5873 | 0.142
5874 | 0.042
5875 | 0
5876 | 0
5877 | 0
5878 | 0
5879 | 0
5880 | 0
5881 | 0
5882 | 0
5883 | 0
5884 | 0
5885 | 0
5886 | 0.003
5887 | 0.017
5888 | 0.058
5889 | 0.155
5890 | 0.363
5891 | 0.137
5892 | 0.243
5893 | 0.178
5894 | 0.203
5895 | 0.069
5896 | 0.205
5897 | 0.207
5898 | 0.049
5899 | 0
5900 | 0
5901 | 0
5902 | 0
5903 | 0
5904 | 0
5905 | 0
5906 | 0
5907 | 0
5908 | 0
5909 | 0
5910 | 0.003
5911 | 0.188
5912 | 0.362
5913 | 0.52301
5914 | 0.504
5915 | 0.64401
5916 | 0.71601
5917 | 0.443
5918 | 0.209
5919 | 0.259
5920 | 0.191
5921 | 0.13
5922 | 0.056
5923 | 0
5924 | 0
5925 | 0
5926 | 0
5927 | 0
5928 | 0
5929 | 0
5930 | 0
5931 | 0
5932 | 0
5933 | 0
5934 | 0.003
5935 | 0.074
5936 | 0.197
5937 | 0.263
5938 | 0.508
5939 | 0.398
5940 | 0.131
5941 | 0.21
5942 | 0.25
5943 | 0.107
5944 | 0.121
5945 | 0.189
5946 | 0.033
5947 | 0
5948 | 0
5949 | 0
5950 | 0
5951 | 0
5952 | 0
5953 | 0
5954 | 0
5955 | 0
5956 | 0
5957 | 0
5958 | 0.002
5959 | 0.158
5960 | 0.18
5961 | 0.152
5962 | 0.089
5963 | 0.272
5964 | 0.218
5965 | 0.256
5966 | 0.391
5967 | 0.169
5968 | 0.305
5969 | 0.171
5970 | 0.044
5971 | 0
5972 | 0
5973 | 0
5974 | 0
5975 | 0
5976 | 0
5977 | 0
5978 | 0
5979 | 0
5980 | 0
5981 | 0
5982 | 0.002
5983 | 0.178
5984 | 0.351
5985 | 0.52901
5986 | 0.65501
5987 | 0.75901
5988 | 0.79201
5989 | 0.76101
5990 | 0.69601
5991 | 0.55901
5992 | 0.387
5993 | 0.255
5994 | 0.083
5995 | 0
5996 | 0
5997 | 0
5998 | 0
5999 | 0
6000 | 0
6001 | 0
6002 | 0
6003 | 0
6004 | 0
6005 | 0
6006 | 0
6007 | 0.157
6008 | 0.285
6009 | 0.50001
6010 | 0.65701
6011 | 0.75401
6012 | 0.79101
6013 | 0.78701
6014 | 0.67701
6015 | 0.58501
6016 | 0.419
6017 | 0.243
6018 | 0.074
6019 | 0
6020 | 0
6021 | 0
6022 | 0
6023 | 0
6024 | 0
6025 | 0
6026 | 0
6027 | 0
6028 | 0
6029 | 0
6030 | 0
6031 | 0.166
6032 | 0.331
6033 | 0.50901
6034 | 0.64401
6035 | 0.73901
6036 | 0.77101
6037 | 0.76601
6038 | 0.68501
6039 | 0.49501
6040 | 0.402
6041 | 0.23
6042 | 0.069
6043 | 0
6044 | 0
6045 | 0
6046 | 0
6047 | 0
6048 | 0
6049 | 0
6050 | 0
6051 | 0
6052 | 0
6053 | 0
6054 | 0
6055 | 0.159
6056 | 0.326
6057 | 0.50001
6058 | 0.55401
6059 | 0.66301
6060 | 0.69501
6061 | 0.73501
6062 | 0.68301
6063 | 0.54801
6064 | 0.405
6065 | 0.234
6066 | 0.05635
6067 | 0
6068 | 0
6069 | 0
6070 | 0
6071 | 0
6072 | 0
6073 | 0
6074 | 0
6075 | 0
6076 | 0
6077 | 0
6078 | 0
6079 | 0.116
6080 | 0.268
6081 | 0.49501
6082 | 0.61601
6083 | 0.70801
6084 | 0.59201
6085 | 0.72601
6086 | 0.66401
6087 | 0.49101
6088 | 0.252
6089 | 0.202
6090 | 0.04921
6091 | 0
6092 | 0
6093 | 0
6094 | 0
6095 | 0
6096 | 0
6097 | 0
6098 | 0
6099 | 0
6100 | 0
6101 | 0
6102 | 0
6103 | 0.155
6104 | 0.321
6105 | 0.50101
6106 | 0.55001
6107 | 0.71401
6108 | 0.76401
6109 | 0.75401
6110 | 0.67501
6111 | 0.54501
6112 | 0.39701
6113 | 0.232
6114 | 0.04582
6115 | 0
6116 | 0
6117 | 0
6118 | 0
6119 | 0
6120 | 0
6121 | 0
6122 | 0
6123 | 0
6124 | 0
6125 | 0
6126 | 0
6127 | 0.018
6128 | 0.197
6129 | 0.49001
6130 | 0.237
6131 | 0.112
6132 | 0.327
6133 | 0.343
6134 | 0.464
6135 | 0.52001
6136 | 0.39401
6137 | 0.218
6138 | 0.04659
6139 | 0
6140 | 0
6141 | 0
6142 | 0
6143 | 0
6144 | 0
6145 | 0
6146 | 0
6147 | 0
6148 | 0
6149 | 0
6150 | 0
6151 | 0.072
6152 | 0.335
6153 | 0.49301
6154 | 0.62201
6155 | 0.56601
6156 | 0.304
6157 | 0.69501
6158 | 0.65401
6159 | 0.26
6160 | 0.106
6161 | 0.032
6162 | 0.02278
6163 | 0
6164 | 0
6165 | 0
6166 | 0
6167 | 0
6168 | 0
6169 | 0
6170 | 0
6171 | 0
6172 | 0
6173 | 0
6174 | 0
6175 | 0.078
6176 | 0.237
6177 | 0.266
6178 | 0.251
6179 | 0.62401
6180 | 0.35
6181 | 0.498
6182 | 0.216
6183 | 0.121
6184 | 0.1
6185 | 0.082
6186 | 0.03086
6187 | 0
6188 | 0
6189 | 0
6190 | 0
6191 | 0
6192 | 0
6193 | 0
6194 | 0
6195 | 0
6196 | 0
6197 | 0
6198 | 0
6199 | 0.121
6200 | 0.136
6201 | 0.309
6202 | 0.307
6203 | 0.205
6204 | 0.112
6205 | 0.479
6206 | 0.363
6207 | 0.54901
6208 | 0.37601
6209 | 0.187
6210 | 0.02884
6211 | 0
6212 | 0
6213 | 0
6214 | 0
6215 | 0
6216 | 0
6217 | 0
6218 | 0
6219 | 0
6220 | 0
6221 | 0
6222 | 0
6223 | 0.046
6224 | 0.113
6225 | 0.084
6226 | 0.072
6227 | 0.062
6228 | 0.104
6229 | 0.097
6230 | 0.057
6231 | 0.135
6232 | 0.277
6233 | 0.157
6234 | 0.02578
6235 | 0
6236 | 0
6237 | 0
6238 | 0
6239 | 0
6240 | 0
6241 | 0
6242 | 0
6243 | 0
6244 | 0
6245 | 0
6246 | 0
6247 | 0.13
6248 | 0.185
6249 | 0.42001
6250 | 0.344
6251 | 0.27
6252 | 0.093
6253 | 0.087
6254 | 0.1
6255 | 0.046
6256 | 0.117
6257 | 0.087
6258 | 0.02077
6259 | 0
6260 | 0
6261 | 0
6262 | 0
6263 | 0
6264 | 0
6265 | 0
6266 | 0
6267 | 0
6268 | 0
6269 | 0
6270 | 0
6271 | 0.112
6272 | 0.255
6273 | 0.44701
6274 | 0.58401
6275 | 0.66001
6276 | 0.59001
6277 | 0.29
6278 | 0.456
6279 | 0.379
6280 | 0.324
6281 | 0.151
6282 | 0.01631
6283 | 0
6284 | 0
6285 | 0
6286 | 0
6287 | 0
6288 | 0
6289 | 0
6290 | 0
6291 | 0
6292 | 0
6293 | 0
6294 | 0
6295 | 0.086
6296 | 0.21
6297 | 0.288
6298 | 0.42
6299 | 0.468
6300 | 0.56701
6301 | 0.53001
6302 | 0.52901
6303 | 0.48401
6304 | 0.257
6305 | 0.11
6306 | 0.004
6307 | 0
6308 | 0
6309 | 0
6310 | 0
6311 | 0
6312 | 0
6313 | 0
6314 | 0
6315 | 0
6316 | 0
6317 | 0
6318 | 0
6319 | 0.095
6320 | 0.173
6321 | 0.246
6322 | 0.398
6323 | 0.53501
6324 | 0.58501
6325 | 0.68201
6326 | 0.61001
6327 | 0.51001
6328 | 0.33901
6329 | 0.167
6330 | 0
6331 | 0
6332 | 0
6333 | 0
6334 | 0
6335 | 0
6336 | 0
6337 | 0
6338 | 0
6339 | 0
6340 | 0
6341 | 0
6342 | 0
6343 | 0.079
6344 | 0.169
6345 | 0.208
6346 | 0.193
6347 | 0.348
6348 | 0.187
6349 | 0.219
6350 | 0.088
6351 | 0.088
6352 | 0.094
6353 | 0.044
6354 | 0
6355 | 0
6356 | 0
6357 | 0
6358 | 0
6359 | 0
6360 | 0
6361 | 0
6362 | 0
6363 | 0
6364 | 0
6365 | 0
6366 | 0
6367 | 0.069
6368 | 0.127
6369 | 0.068
6370 | 0.106
6371 | 0.37
6372 | 0.101
6373 | 0.11
6374 | 0.111
6375 | 0.15
6376 | 0.16
6377 | 0.039
6378 | 0
6379 | 0
6380 | 0
6381 | 0
6382 | 0
6383 | 0
6384 | 0
6385 | 0
6386 | 0
6387 | 0
6388 | 0
6389 | 0
6390 | 0
6391 | 0.099
6392 | 0.161
6393 | 0.178
6394 | 0.56001
6395 | 0.64201
6396 | 0.67101
6397 | 0.194
6398 | 0.295
6399 | 0.47901
6400 | 0.31801
6401 | 0.147
6402 | 0
6403 | 0
6404 | 0
6405 | 0
6406 | 0
6407 | 0
6408 | 0
6409 | 0
6410 | 0
6411 | 0
6412 | 0
6413 | 0
6414 | 0
6415 | 0.084
6416 | 0.229
6417 | 0.41701
6418 | 0.54701
6419 | 0.65001
6420 | 0.65901
6421 | 0.59001
6422 | 0.55201
6423 | 0.45301
6424 | 0.296
6425 | 0.134
6426 | 0
6427 | 0
6428 | 0
6429 | 0
6430 | 0
6431 | 0
6432 | 0
6433 | 0
6434 | 0
6435 | 0
6436 | 0
6437 | 0
6438 | 0
6439 | 0.093
6440 | 0.213
6441 | 0.323
6442 | 0.50701
6443 | 0.53101
6444 | 0.219
6445 | 0.205
6446 | 0.292
6447 | 0.266
6448 | 0.149
6449 | 0.064
6450 | 0
6451 | 0
6452 | 0
6453 | 0
6454 | 0
6455 | 0
6456 | 0
6457 | 0
6458 | 0
6459 | 0
6460 | 0
6461 | 0
6462 | 0
6463 | 0.046
6464 | 0.131
6465 | 0.188
6466 | 0.307
6467 | 0.266
6468 | 0.337
6469 | 0.228
6470 | 0.301
6471 | 0.191
6472 | 0.157
6473 | 0.069
6474 | 0
6475 | 0
6476 | 0
6477 | 0
6478 | 0
6479 | 0
6480 | 0
6481 | 0
6482 | 0
6483 | 0
6484 | 0
6485 | 0
6486 | 0
6487 | 0.078
6488 | 0.219
6489 | 0.41201
6490 | 0.54901
6491 | 0.62701
6492 | 0.441
6493 | 0.402
6494 | 0.209
6495 | 0.076
6496 | 0.163
6497 | 0.091
6498 | 0
6499 | 0
6500 | 0
6501 | 0
6502 | 0
6503 | 0
6504 | 0
6505 | 0
6506 | 0
6507 | 0
6508 | 0
6509 | 0
6510 | 0
6511 | 0.089
6512 | 0.251
6513 | 0.42001
6514 | 0.54701
6515 | 0.62501
6516 | 0.64701
6517 | 0.63201
6518 | 0.55401
6519 | 0.45101
6520 | 0.28201
6521 | 0.114
6522 | 0
6523 | 0
6524 | 0
6525 | 0
6526 | 0
6527 | 0
6528 | 0
6529 | 0
6530 | 0
6531 | 0
6532 | 0
6533 | 0
6534 | 0
6535 | 0.04
6536 | 0.097
6537 | 0.126
6538 | 0.091
6539 | 0.109
6540 | 0.059
6541 | 0.176
6542 | 0.415
6543 | 0.299
6544 | 0.237
6545 | 0.067
6546 | 0
6547 | 0
6548 | 0
6549 | 0
6550 | 0
6551 | 0
6552 | 0
6553 | 0
6554 | 0
6555 | 0
6556 | 0
6557 | 0
6558 | 0
6559 | 0.072
6560 | 0.023
6561 | 0.197
6562 | 0.273
6563 | 0.57001
6564 | 0.57801
6565 | 0.65301
6566 | 0.57501
6567 | 0.44801
6568 | 0.28901
6569 | 0.114
6570 | 0
6571 | 0
6572 | 0
6573 | 0
6574 | 0
6575 | 0
6576 | 0
6577 | 0
6578 | 0
6579 | 0
6580 | 0
6581 | 0
6582 | 0
6583 | 0.082
6584 | 0.25601
6585 | 0.41101
6586 | 0.55301
6587 | 0.63901
6588 | 0.66801
6589 | 0.64101
6590 | 0.51101
6591 | 0.172
6592 | 0.072
6593 | 0.068
6594 | 0
6595 | 0
6596 | 0
6597 | 0
6598 | 0
6599 | 0
6600 | 0
6601 | 0
6602 | 0
6603 | 0
6604 | 0
6605 | 0
6606 | 0
6607 | 0.083
6608 | 0.24401
6609 | 0.36601
6610 | 0.54201
6611 | 0.62701
6612 | 0.66501
6613 | 0.60601
6614 | 0.55401
6615 | 0.43401
6616 | 0.27201
6617 | 0.082
6618 | 0
6619 | 0
6620 | 0
6621 | 0
6622 | 0
6623 | 0
6624 | 0
6625 | 0
6626 | 0
6627 | 0
6628 | 0
6629 | 0
6630 | 0
6631 | 0.049
6632 | 0.113
6633 | 0.164
6634 | 0.48201
6635 | 0.61201
6636 | 0.60601
6637 | 0.51901
6638 | 0.53601
6639 | 0.41501
6640 | 0.27201
6641 | 0.098
6642 | 0
6643 | 0
6644 | 0
6645 | 0
6646 | 0
6647 | 0
6648 | 0
6649 | 0
6650 | 0
6651 | 0
6652 | 0
6653 | 0
6654 | 0
6655 | 0.024
6656 | 0.108
6657 | 0.236
6658 | 0.51201
6659 | 0.54301
6660 | 0.58701
6661 | 0.427
6662 | 0.46301
6663 | 0.236
6664 | 0.035
6665 | 0.008
6666 | 0
6667 | 0
6668 | 0
6669 | 0
6670 | 0
6671 | 0
6672 | 0
6673 | 0
6674 | 0
6675 | 0
6676 | 0
6677 | 0
6678 | 0
6679 | 0.065
6680 | 0.113
6681 | 0.198
6682 | 0.50701
6683 | 0.4
6684 | 0.12
6685 | 0.054
6686 | 0.047
6687 | 0.067
6688 | 0.077
6689 | 0.044
6690 | 0
6691 | 0
6692 | 0
6693 | 0
6694 | 0
6695 | 0
6696 | 0
6697 | 0
6698 | 0
6699 | 0
6700 | 0
6701 | 0
6702 | 0
6703 | 0.04644
6704 | 0.15
6705 | 0.302
6706 | 0.251
6707 | 0.295
6708 | 0.313
6709 | 0.095
6710 | 0.163
6711 | 0.104
6712 | 0.071
6713 | 0.032
6714 | 0
6715 | 0
6716 | 0
6717 | 0
6718 | 0
6719 | 0
6720 | 0
6721 | 0
6722 | 0
6723 | 0
6724 | 0
6725 | 0
6726 | 0
6727 | 0.02878
6728 | 0.143
6729 | 0.166
6730 | 0.149
6731 | 0.267
6732 | 0.336
6733 | 0.307
6734 | 0.308
6735 | 0.18
6736 | 0.076
6737 | 0.014
6738 | 0
6739 | 0
6740 | 0
6741 | 0
6742 | 0
6743 | 0
6744 | 0
6745 | 0
6746 | 0
6747 | 0
6748 | 0
6749 | 0
6750 | 0
6751 | 0.03303
6752 | 0.122
6753 | 0.246
6754 | 0.197
6755 | 0.28
6756 | 0.218
6757 | 0.206
6758 | 0.201
6759 | 0.142
6760 | 0.214
6761 | 0.0567
6762 | 0
6763 | 0
6764 | 0
6765 | 0
6766 | 0
6767 | 0
6768 | 0
6769 | 0
6770 | 0
6771 | 0
6772 | 0
6773 | 0
6774 | 0
6775 | 0.0248
6776 | 0.074
6777 | 0.087
6778 | 0.065
6779 | 0.074
6780 | 0.076
6781 | 0.062
6782 | 0.054
6783 | 0.038
6784 | 0.042
6785 | 0.021
6786 | 0
6787 | 0
6788 | 0
6789 | 0
6790 | 0
6791 | 0
6792 | 0
6793 | 0
6794 | 0
6795 | 0
6796 | 0
6797 | 0
6798 | 0
6799 | 0.015
6800 | 0.057
6801 | 0.094
6802 | 0.058
6803 | 0.083
6804 | 0.054
6805 | 0.104
6806 | 0.077
6807 | 0.043
6808 | 0.056
6809 | 0.03398
6810 | 0
6811 | 0
6812 | 0
6813 | 0
6814 | 0
6815 | 0
6816 | 0
6817 | 0
6818 | 0
6819 | 0
6820 | 0
6821 | 0
6822 | 0
6823 | 0.02653
6824 | 0.142
6825 | 0.275
6826 | 0.369
6827 | 0.47801
6828 | 0.50501
6829 | 0.48301
6830 | 0.43501
6831 | 0.37401
6832 | 0.167
6833 | 0.017
6834 | 0
6835 | 0
6836 | 0
6837 | 0
6838 | 0
6839 | 0
6840 | 0
6841 | 0
6842 | 0
6843 | 0
6844 | 0
6845 | 0
6846 | 0
6847 | 0.02278
6848 | 0.087
6849 | 0.171
6850 | 0.062
6851 | 0.159
6852 | 0.053
6853 | 0.05
6854 | 0.043
6855 | 0.032
6856 | 0.04
6857 | 0.019
6858 | 0
6859 | 0
6860 | 0
6861 | 0
6862 | 0
6863 | 0
6864 | 0
6865 | 0
6866 | 0
6867 | 0
6868 | 0
6869 | 0
6870 | 0
6871 | 0.0243
6872 | 0.169
6873 | 0.217
6874 | 0.263
6875 | 0.298
6876 | 0.48601
6877 | 0.41701
6878 | 0.298
6879 | 0.097
6880 | 0.112
6881 | 0.03353
6882 | 0
6883 | 0
6884 | 0
6885 | 0
6886 | 0
6887 | 0
6888 | 0
6889 | 0
6890 | 0
6891 | 0
6892 | 0
6893 | 0
6894 | 0
6895 | 0.009
6896 | 0.022
6897 | 0.031
6898 | 0.069
6899 | 0.108
6900 | 0.138
6901 | 0.1
6902 | 0.045
6903 | 0.035
6904 | 0.037
6905 | 0.02331
6906 | 0
6907 | 0
6908 | 0
6909 | 0
6910 | 0
6911 | 0
6912 | 0
6913 | 0
6914 | 0
6915 | 0
6916 | 0
6917 | 0
6918 | 0
6919 | 0.019
6920 | 0.068
6921 | 0.102
6922 | 0.205
6923 | 0.078
6924 | 0.061
6925 | 0.049
6926 | 0.068
6927 | 0.054
6928 | 0.079
6929 | 0.011
6930 | 0
6931 | 0
6932 | 0
6933 | 0
6934 | 0
6935 | 0
6936 | 0
6937 | 0
6938 | 0
6939 | 0
6940 | 0
6941 | 0
6942 | 0
6943 | 0.017
6944 | 0.108
6945 | 0.146
6946 | 0.122
6947 | 0.155
6948 | 0.125
6949 | 0.091
6950 | 0.062
6951 | 0.034
6952 | 0.067
6953 | 0.009
6954 | 0
6955 | 0
6956 | 0
6957 | 0
6958 | 0
6959 | 0
6960 | 0
6961 | 0
6962 | 0
6963 | 0
6964 | 0
6965 | 0
6966 | 0
6967 | 0.003
6968 | 0.035
6969 | 0.029
6970 | 0.04
6971 | 0.047
6972 | 0.05
6973 | 0.047
6974 | 0.051
6975 | 0.052
6976 | 0.045
6977 | 0.015
6978 | 0
6979 | 0
6980 | 0
6981 | 0
6982 | 0
6983 | 0
6984 | 0
6985 | 0
6986 | 0
6987 | 0
6988 | 0
6989 | 0
6990 | 0
6991 | 0.012
6992 | 0.044
6993 | 0.159
6994 | 0.185
6995 | 0.207
6996 | 0.362
6997 | 0.333
6998 | 0.272
6999 | 0.29301
7000 | 0.154
7001 | 0.014
7002 | 0
7003 | 0
7004 | 0
7005 | 0
7006 | 0
7007 | 0
7008 | 0
7009 | 0
7010 | 0
7011 | 0
7012 | 0
7013 | 0
7014 | 0
7015 | 0.007
7016 | 0.085
7017 | 0.141
7018 | 0.145
7019 | 0.313
7020 | 0.39801
7021 | 0.51701
7022 | 0.44101
7023 | 0.31601
7024 | 0.16401
7025 | 0.013
7026 | 0
7027 | 0
7028 | 0
7029 | 0
7030 | 0
7031 | 0
7032 | 0
7033 | 0
7034 | 0
7035 | 0
7036 | 0
7037 | 0
7038 | 0
7039 | 0.006
7040 | 0.077
7041 | 0.13
7042 | 0.114
7043 | 0.148
7044 | 0.062
7045 | 0.073
7046 | 0.097
7047 | 0.053
7048 | 0.113
7049 | 0
7050 | 0
7051 | 0
7052 | 0
7053 | 0
7054 | 0
7055 | 0
7056 | 0
7057 | 0
7058 | 0
7059 | 0
7060 | 0
7061 | 0
7062 | 0
7063 | 0
7064 | 0.117
7065 | 0.198
7066 | 0.38801
7067 | 0.50001
7068 | 0.45101
7069 | 0.257
7070 | 0.201
7071 | 0.099
7072 | 0.078
7073 | 0
7074 | 0
7075 | 0
7076 | 0
7077 | 0
7078 | 0
7079 | 0
7080 | 0
7081 | 0
7082 | 0
7083 | 0
7084 | 0
7085 | 0
7086 | 0
7087 | 0
7088 | 0.091
7089 | 0.143
7090 | 0.123
7091 | 0.126
7092 | 0.089
7093 | 0.148
7094 | 0.083
7095 | 0.074
7096 | 0.067
7097 | 0
7098 | 0
7099 | 0
7100 | 0
7101 | 0
7102 | 0
7103 | 0
7104 | 0
7105 | 0
7106 | 0
7107 | 0
7108 | 0
7109 | 0
7110 | 0
7111 | 0
7112 | 0.127
7113 | 0.172
7114 | 0.38601
7115 | 0.40301
7116 | 0.50101
7117 | 0.46401
7118 | 0.38901
7119 | 0.169
7120 | 0.09
7121 | 0
7122 | 0
7123 | 0
7124 | 0
7125 | 0
7126 | 0
7127 | 0
7128 | 0
7129 | 0
7130 | 0
7131 | 0
7132 | 0
7133 | 0
7134 | 0
7135 | 0
7136 | 0.023
7137 | 0.117
7138 | 0.192
7139 | 0.306
7140 | 0.341
7141 | 0.44601
7142 | 0.40701
7143 | 0.28501
7144 | 0.131
7145 | 0
7146 | 0
7147 | 0
7148 | 0
7149 | 0
7150 | 0
7151 | 0
7152 | 0
7153 | 0
7154 | 0
7155 | 0
7156 | 0
7157 | 0
7158 | 0
7159 | 0
7160 | 0.061
7161 | 0.093
7162 | 0.08
7163 | 0.145
7164 | 0.275
7165 | 0.48301
7166 | 0.40301
7167 | 0.28501
7168 | 0.132
7169 | 0
7170 | 0
7171 | 0
7172 | 0
7173 | 0
7174 | 0
7175 | 0
7176 | 0
7177 | 0
7178 | 0
7179 | 0
7180 | 0
7181 | 0
7182 | 0
7183 | 0
7184 | 0.054
7185 | 0.093
7186 | 0.08
7187 | 0.117
7188 | 0.157
7189 | 0.156
7190 | 0.159
7191 | 0.168
7192 | 0.117
7193 | 0
7194 | 0
7195 | 0
7196 | 0
7197 | 0
7198 | 0
7199 | 0
7200 | 0
7201 | 0
7202 | 0
7203 | 0
7204 | 0
7205 | 0
7206 | 0
7207 | 0
7208 | 0.115
7209 | 0.132
7210 | 0.36401
7211 | 0.46101
7212 | 0.49101
7213 | 0.46701
7214 | 0.39401
7215 | 0.27001
7216 | 0.12901
7217 | 0
7218 | 0
7219 | 0
7220 | 0
7221 | 0
7222 | 0
7223 | 0
7224 | 0
7225 | 0
7226 | 0
7227 | 0
7228 | 0
7229 | 0
7230 | 0
7231 | 0
7232 | 0.076
7233 | 0.095
7234 | 0.13
7235 | 0.184
7236 | 0.156
7237 | 0.132
7238 | 0.171
7239 | 0.137
7240 | 0.069
7241 | 0
7242 | 0
7243 | 0
7244 | 0
7245 | 0
7246 | 0
7247 | 0
7248 | 0
7249 | 0
7250 | 0
7251 | 0
7252 | 0
7253 | 0
7254 | 0
7255 | 0
7256 | 0.06
7257 | 0.117
7258 | 0.096
7259 | 0.139
7260 | 0.207
7261 | 0.265
7262 | 0.35301
7263 | 0.22901
7264 | 0.104
7265 | 0
7266 | 0
7267 | 0
7268 | 0
7269 | 0
7270 | 0
7271 | 0
7272 | 0
7273 | 0
7274 | 0
7275 | 0
7276 | 0
7277 | 0
7278 | 0
7279 | 0
7280 | 0.047
7281 | 0.085
7282 | 0.074
7283 | 0.114
7284 | 0.145
7285 | 0.34501
7286 | 0.37101
7287 | 0.25401
7288 | 0.108
7289 | 0
7290 | 0
7291 | 0
7292 | 0
7293 | 0
7294 | 0
7295 | 0
7296 | 0
7297 | 0
7298 | 0
7299 | 0
7300 | 0
7301 | 0
7302 | 0
7303 | 0
7304 | 0.067
7305 | 0.123
7306 | 0.141
7307 | 0.236
7308 | 0.47901
7309 | 0.45901
7310 | 0.38301
7311 | 0.26101
7312 | 0.11801
7313 | 0
7314 | 0
7315 | 0
7316 | 0
7317 | 0
7318 | 0
7319 | 0
7320 | 0
7321 | 0
7322 | 0
7323 | 0
7324 | 0
7325 | 0
7326 | 0
7327 | 0
7328 | 0.056
7329 | 0.115
7330 | 0.099
7331 | 0.126
7332 | 0.117
7333 | 0.151
7334 | 0.178
7335 | 0.189
7336 | 0.10501
7337 | 0
7338 | 0
7339 | 0
7340 | 0
7341 | 0
7342 | 0
7343 | 0
7344 | 0
7345 | 0
7346 | 0
7347 | 0
7348 | 0
7349 | 0
7350 | 0
7351 | 0
7352 | 0.031
7353 | 0.143
7354 | 0.257
7355 | 0.316
7356 | 0.271
7357 | 0.173
7358 | 0.24
7359 | 0.094
7360 | 0.033
7361 | 0
7362 | 0
7363 | 0
7364 | 0
7365 | 0
7366 | 0
7367 | 0
7368 | 0
7369 | 0
7370 | 0
7371 | 0
7372 | 0
7373 | 0
7374 | 0
7375 | 0
7376 | 0.10801
7377 | 0.25101
7378 | 0.36801
7379 | 0.46502
7380 | 0.47201
7381 | 0.43301
7382 | 0.36701
7383 | 0.24701
7384 | 0.10501
7385 | 0
7386 | 0
7387 | 0
7388 | 0
7389 | 0
7390 | 0
7391 | 0
7392 | 0
7393 | 0
7394 | 0
7395 | 0
7396 | 0
7397 | 0
7398 | 0
7399 | 0
7400 | 0.10401
7401 | 0.24701
7402 | 0.37401
7403 | 0.44501
7404 | 0.47102
7405 | 0.44101
7406 | 0.36501
7407 | 0.24501
7408 | 0.10001
7409 | 0
7410 | 0
7411 | 0
7412 | 0
7413 | 0
7414 | 0
7415 | 0
7416 | 0
7417 | 0
7418 | 0
7419 | 0
7420 | 0
7421 | 0
7422 | 0
7423 | 0
7424 | 0.086
7425 | 0.24801
7426 | 0.35601
7427 | 0.43301
7428 | 0.46602
7429 | 0.43201
7430 | 0.37101
7431 | 0.23801
7432 | 0.09501
7433 | 0
7434 | 0
7435 | 0
7436 | 0
7437 | 0
7438 | 0
7439 | 0
7440 | 0
7441 | 0
7442 | 0
7443 | 0
7444 | 0
7445 | 0
7446 | 0
7447 | 0
7448 | 0.09001
7449 | 0.184
7450 | 0.35801
7451 | 0.43201
7452 | 0.46302
7453 | 0.42601
7454 | 0.33501
7455 | 0.23201
7456 | 0.08901
7457 | 0
7458 | 0
7459 | 0
7460 | 0
7461 | 0
7462 | 0
7463 | 0
7464 | 0
7465 | 0
7466 | 0
7467 | 0
7468 | 0
7469 | 0
7470 | 0
7471 | 0
7472 | 0.09101
7473 | 0.20901
7474 | 0.34201
7475 | 0.42301
7476 | 0.45001
7477 | 0.42101
7478 | 0.34501
7479 | 0.22701
7480 | 0.08701
7481 | 0
7482 | 0
7483 | 0
7484 | 0
7485 | 0
7486 | 0
7487 | 0
7488 | 0
7489 | 0
7490 | 0
7491 | 0
7492 | 0
7493 | 0
7494 | 0
7495 | 0
7496 | 0.09001
7497 | 0.22501
7498 | 0.197
7499 | 0.41501
7500 | 0.32501
7501 | 0.34501
7502 | 0.28101
7503 | 0.158
7504 | 0.07
7505 | 0
7506 | 0
7507 | 0
7508 | 0
7509 | 0
7510 | 0
7511 | 0
7512 | 0
7513 | 0
7514 | 0
7515 | 0
7516 | 0
7517 | 0
7518 | 0
7519 | 0
7520 | 0.057
7521 | 0.19401
7522 | 0.33901
7523 | 0.41201
7524 | 0.44202
7525 | 0.41101
7526 | 0.33301
7527 | 0.21601
7528 | 0.076
7529 | 0
7530 | 0
7531 | 0
7532 | 0
7533 | 0
7534 | 0
7535 | 0
7536 | 0
7537 | 0
7538 | 0
7539 | 0
7540 | 0
7541 | 0
7542 | 0
7543 | 0
7544 | 0.067
7545 | 0.13
7546 | 0.134
7547 | 0.155
7548 | 0.43501
7549 | 0.40201
7550 | 0.32901
7551 | 0.21101
7552 | 0.074
7553 | 0
7554 | 0
7555 | 0
7556 | 0
7557 | 0
7558 | 0
7559 | 0
7560 | 0
7561 | 0
7562 | 0
7563 | 0
7564 | 0
7565 | 0
7566 | 0
7567 | 0
7568 | 0.037
7569 | 0.096
7570 | 0.094
7571 | 0.127
7572 | 0.161
7573 | 0.155
7574 | 0.132
7575 | 0.097
7576 | 0.017
7577 | 0
7578 | 0
7579 | 0
7580 | 0
7581 | 0
7582 | 0
7583 | 0
7584 | 0
7585 | 0
7586 | 0
7587 | 0
7588 | 0
7589 | 0
7590 | 0
7591 | 0
7592 | 0.04806
7593 | 0.157
7594 | 0.29901
7595 | 0.33701
7596 | 0.40501
7597 | 0.34701
7598 | 0.27801
7599 | 0.156
7600 | 0.05119
7601 | 0
7602 | 0
7603 | 0
7604 | 0
7605 | 0
7606 | 0
7607 | 0
7608 | 0
7609 | 0
7610 | 0
7611 | 0
7612 | 0
7613 | 0
7614 | 0
7615 | 0
7616 | 0.02779
7617 | 0.112
7618 | 0.128
7619 | 0.158
7620 | 0.202
7621 | 0.246
7622 | 0.24301
7623 | 0.152
7624 | 0.04942
7625 | 0
7626 | 0
7627 | 0
7628 | 0
7629 | 0
7630 | 0
7631 | 0
7632 | 0
7633 | 0
7634 | 0
7635 | 0
7636 | 0
7637 | 0
7638 | 0
7639 | 0
7640 | 0.03719
7641 | 0.142
7642 | 0.29601
7643 | 0.32501
7644 | 0.268
7645 | 0.258
7646 | 0.31001
7647 | 0.18801
7648 | 0.032
7649 | 0
7650 | 0
7651 | 0
7652 | 0
7653 | 0
7654 | 0
7655 | 0
7656 | 0
7657 | 0
7658 | 0
7659 | 0
7660 | 0
7661 | 0
7662 | 0
7663 | 0
7664 | 0.02579
7665 | 0.18101
7666 | 0.23401
7667 | 0.31701
7668 | 0.34501
7669 | 0.35101
7670 | 0.30601
7671 | 0.17301
7672 | 0.031
7673 | 0
7674 | 0
7675 | 0
7676 | 0
7677 | 0
7678 | 0
7679 | 0
7680 | 0
7681 | 0
7682 | 0
7683 | 0
7684 | 0
7685 | 0
7686 | 0
7687 | 0
7688 | 0.04522
7689 | 0.15
7690 | 0.101
7691 | 0.053
7692 | 0.163
7693 | 0.143
7694 | 0.086
7695 | 0.065
7696 | 0.013
7697 | 0
7698 | 0
7699 | 0
7700 | 0
7701 | 0
7702 | 0
7703 | 0
7704 | 0
7705 | 0
7706 | 0
7707 | 0
7708 | 0
7709 | 0
7710 | 0
7711 | 0
7712 | 0.04341
7713 | 0.17801
7714 | 0.30301
7715 | 0.37301
7716 | 0.40201
7717 | 0.37501
7718 | 0.29801
7719 | 0.18501
7720 | 0.026
7721 | 0
7722 | 0
7723 | 0
7724 | 0
7725 | 0
7726 | 0
7727 | 0
7728 | 0
7729 | 0
7730 | 0
7731 | 0
7732 | 0
7733 | 0
7734 | 0
7735 | 0
7736 | 0.04083
7737 | 0.16501
7738 | 0.29101
7739 | 0.35701
7740 | 0.38301
7741 | 0.37801
7742 | 0.29301
7743 | 0.126
7744 | 0.025
7745 | 0
7746 | 0
7747 | 0
7748 | 0
7749 | 0
7750 | 0
7751 | 0
7752 | 0
7753 | 0
7754 | 0
7755 | 0
7756 | 0
7757 | 0
7758 | 0
7759 | 0
7760 | 0.004
7761 | 0.022
7762 | 0.04
7763 | 0.05
7764 | 0.05
7765 | 0.053
7766 | 0.04
7767 | 0.027
7768 | 0.01
7769 | 0
7770 | 0
7771 | 0
7772 | 0
7773 | 0
7774 | 0
7775 | 0
7776 | 0
7777 | 0
7778 | 0
7779 | 0
7780 | 0
7781 | 0
7782 | 0
7783 | 0
7784 | 0.03177
7785 | 0.022
7786 | 0.205
7787 | 0.34901
7788 | 0.183
7789 | 0.064
7790 | 0.133
7791 | 0.04
7792 | 0.005
7793 | 0
7794 | 0
7795 | 0
7796 | 0
7797 | 0
7798 | 0
7799 | 0
7800 | 0
7801 | 0
7802 | 0
7803 | 0
7804 | 0
7805 | 0
7806 | 0
7807 | 0
7808 | 0.0223
7809 | 0.058
7810 | 0.107
7811 | 0.244
7812 | 0.067
7813 | 0.16
7814 | 0.194
7815 | 0.079
7816 | 0.021
7817 | 0
7818 | 0
7819 | 0
7820 | 0
7821 | 0
7822 | 0
7823 | 0
7824 | 0
7825 | 0
7826 | 0
7827 | 0
7828 | 0
7829 | 0
7830 | 0
7831 | 0
7832 | 0.01955
7833 | 0.088
7834 | 0.052
7835 | 0.136
7836 | 0.206
7837 | 0.132
7838 | 0.197
7839 | 0.137
7840 | 0.024
7841 | 0
7842 | 0
7843 | 0
7844 | 0
7845 | 0
7846 | 0
7847 | 0
7848 | 0
7849 | 0
7850 | 0
7851 | 0
7852 | 0
7853 | 0
7854 | 0
7855 | 0
7856 | 0.02105
7857 | 0.14401
7858 | 0.26301
7859 | 0.34201
7860 | 0.36501
7861 | 0.34601
7862 | 0.22901
7863 | 0.14601
7864 | 0.021
7865 | 0
7866 | 0
7867 | 0
7868 | 0
7869 | 0
7870 | 0
7871 | 0
7872 | 0
7873 | 0
7874 | 0
7875 | 0
7876 | 0
7877 | 0
7878 | 0
7879 | 0
7880 | 0.003
7881 | 0.061
7882 | 0.11
7883 | 0.062
7884 | 0.066
7885 | 0.093
7886 | 0.035
7887 | 0.024
7888 | 0.017
7889 | 0
7890 | 0
7891 | 0
7892 | 0
7893 | 0
7894 | 0
7895 | 0
7896 | 0
7897 | 0
7898 | 0
7899 | 0
7900 | 0
7901 | 0
7902 | 0
7903 | 0
7904 | 0.004
7905 | 0.05
7906 | 0.045
7907 | 0.091
7908 | 0.128
7909 | 0.069
7910 | 0.064
7911 | 0.024
7912 | 0.012
7913 | 0
7914 | 0
7915 | 0
7916 | 0
7917 | 0
7918 | 0
7919 | 0
7920 | 0
7921 | 0
7922 | 0
7923 | 0
7924 | 0
7925 | 0
7926 | 0
7927 | 0
7928 | 0.008
7929 | 0.101
7930 | 0.135
7931 | 0.138
7932 | 0.121
7933 | 0.091
7934 | 0.062
7935 | 0.03
7936 | 0.013
7937 | 0
7938 | 0
7939 | 0
7940 | 0
7941 | 0
7942 | 0
7943 | 0
7944 | 0
7945 | 0
7946 | 0
7947 | 0
7948 | 0
7949 | 0
7950 | 0
7951 | 0
7952 | 0.01
7953 | 0.06
7954 | 0.093
7955 | 0.052
7956 | 0.059
7957 | 0.173
7958 | 0.049
7959 | 0.065
7960 | 0.017
7961 | 0
7962 | 0
7963 | 0
7964 | 0
7965 | 0
7966 | 0
7967 | 0
7968 | 0
7969 | 0
7970 | 0
7971 | 0
7972 | 0
7973 | 0
7974 | 0
7975 | 0
7976 | 0
7977 | 0.021
7978 | 0.038
7979 | 0.091
7980 | 0.083
7981 | 0.059
7982 | 0.081
7983 | 0.086
7984 | 0.015
7985 | 0
7986 | 0
7987 | 0
7988 | 0
7989 | 0
7990 | 0
7991 | 0
7992 | 0
7993 | 0
7994 | 0
7995 | 0
7996 | 0
7997 | 0
7998 | 0
7999 | 0
8000 | 0
8001 | 0.023
8002 | 0.05
8003 | 0.094
8004 | 0.175
8005 | 0.175
8006 | 0.23601
8007 | 0.097
8008 | 0.006
8009 | 0
8010 | 0
8011 | 0
8012 | 0
8013 | 0
8014 | 0
8015 | 0
8016 | 0
8017 | 0
8018 | 0
8019 | 0
8020 | 0
8021 | 0
8022 | 0
8023 | 0
8024 | 0
8025 | 0.048
8026 | 0.061
8027 | 0.103
8028 | 0.155
8029 | 0.176
8030 | 0.15
8031 | 0.096
8032 | 0.015
8033 | 0
8034 | 0
8035 | 0
8036 | 0
8037 | 0
8038 | 0
8039 | 0
8040 | 0
8041 | 0
8042 | 0
8043 | 0
8044 | 0
8045 | 0
8046 | 0
8047 | 0
8048 | 0
8049 | 0.14001
8050 | 0.25201
8051 | 0.32401
8052 | 0.35902
8053 | 0.33401
8054 | 0.26801
8055 | 0.15801
8056 | 0.012
8057 | 0
8058 | 0
8059 | 0
8060 | 0
8061 | 0
8062 | 0
8063 | 0
8064 | 0
8065 | 0
8066 | 0
8067 | 0
8068 | 0
8069 | 0
8070 | 0
8071 | 0
8072 | 0
8073 | 0.084
8074 | 0.134
8075 | 0.14
8076 | 0.181
8077 | 0.14
8078 | 0.11
8079 | 0.076
8080 | 0.014
8081 | 0
8082 | 0
8083 | 0
8084 | 0
8085 | 0
8086 | 0
8087 | 0
8088 | 0
8089 | 0
8090 | 0
8091 | 0
8092 | 0
8093 | 0
8094 | 0
8095 | 0
8096 | 0
8097 | 0.066
8098 | 0.158
8099 | 0.092
8100 | 0.11
8101 | 0.059
8102 | 0.039
8103 | 0.035
8104 | 0.005
8105 | 0
8106 | 0
8107 | 0
8108 | 0
8109 | 0
8110 | 0
8111 | 0
8112 | 0
8113 | 0
8114 | 0
8115 | 0
8116 | 0
8117 | 0
8118 | 0
8119 | 0
8120 | 0
8121 | 0.088
8122 | 0.127
8123 | 0.141
8124 | 0.182
8125 | 0.135
8126 | 0.133
8127 | 0.08
8128 | 0.011
8129 | 0
8130 | 0
8131 | 0
8132 | 0
8133 | 0
8134 | 0
8135 | 0
8136 | 0
8137 | 0
8138 | 0
8139 | 0
8140 | 0
8141 | 0
8142 | 0
8143 | 0
8144 | 0
8145 | 0.099
8146 | 0.146
8147 | 0.181
8148 | 0.239
8149 | 0.28801
8150 | 0.24301
8151 | 0.14601
8152 | 0.011
8153 | 0
8154 | 0
8155 | 0
8156 | 0
8157 | 0
8158 | 0
8159 | 0
8160 | 0
8161 | 0
8162 | 0
8163 | 0
8164 | 0
8165 | 0
8166 | 0
8167 | 0
8168 | 0
8169 | 0.12401
8170 | 0.22501
8171 | 0.30901
8172 | 0.34602
8173 | 0.32201
8174 | 0.25901
8175 | 0.15001
8176 | 0.011
8177 | 0
8178 | 0
8179 | 0
8180 | 0
8181 | 0
8182 | 0
8183 | 0
8184 | 0
8185 | 0
8186 | 0
8187 | 0
8188 | 0
8189 | 0
8190 | 0
8191 | 0
8192 | 0
8193 | 0.078
8194 | 0.119
8195 | 0.167
8196 | 0.227
8197 | 0.23001
8198 | 0.23201
8199 | 0.13601
8200 | 0.014
8201 | 0
8202 | 0
8203 | 0
8204 | 0
8205 | 0
8206 | 0
8207 | 0
8208 | 0
8209 | 0
8210 | 0
8211 | 0
8212 | 0
8213 | 0
8214 | 0
8215 | 0
8216 | 0
8217 | 0.031
8218 | 0.051
8219 | 0.071
8220 | 0.088
8221 | 0.118
8222 | 0.042
8223 | 0.024
8224 | 0.009
8225 | 0
8226 | 0
8227 | 0
8228 | 0
8229 | 0
8230 | 0
8231 | 0
8232 | 0
8233 | 0
8234 | 0
8235 | 0
8236 | 0
8237 | 0
8238 | 0
8239 | 0
8240 | 0
8241 | 0.054
8242 | 0.068
8243 | 0.094
8244 | 0.111
8245 | 0.119
8246 | 0.117
8247 | 0.076
8248 | 0.012
8249 | 0
8250 | 0
8251 | 0
8252 | 0
8253 | 0
8254 | 0
8255 | 0
8256 | 0
8257 | 0
8258 | 0
8259 | 0
8260 | 0
8261 | 0
8262 | 0
8263 | 0
8264 | 0
8265 | 0.053
8266 | 0.18301
8267 | 0.192
8268 | 0.32501
8269 | 0.28101
8270 | 0.19301
8271 | 0.111
8272 | 0.013
8273 | 0
8274 | 0
8275 | 0
8276 | 0
8277 | 0
8278 | 0
8279 | 0
8280 | 0
8281 | 0
8282 | 0
8283 | 0
8284 | 0
8285 | 0
8286 | 0
8287 | 0
8288 | 0
8289 | 0.09601
8290 | 0.19901
8291 | 0.25601
8292 | 0.31401
8293 | 0.26701
8294 | 0.21801
8295 | 0.13301
8296 | 0.012
8297 | 0
8298 | 0
8299 | 0
8300 | 0
8301 | 0
8302 | 0
8303 | 0
8304 | 0
8305 | 0
8306 | 0
8307 | 0
8308 | 0
8309 | 0
8310 | 0
8311 | 0
8312 | 0
8313 | 0.10701
8314 | 0.22101
8315 | 0.29501
8316 | 0.33001
8317 | 0.28701
8318 | 0.22001
8319 | 0.108
8320 | 0.014
8321 | 0
8322 | 0
8323 | 0
8324 | 0
8325 | 0
8326 | 0
8327 | 0
8328 | 0
8329 | 0
8330 | 0
8331 | 0
8332 | 0
8333 | 0
8334 | 0
8335 | 0
8336 | 0
8337 | 0.076
8338 | 0.124
8339 | 0.151
8340 | 0.18
8341 | 0.25401
8342 | 0.24401
8343 | 0.14301
8344 | 0.012
8345 | 0
8346 | 0
8347 | 0
8348 | 0
8349 | 0
8350 | 0
8351 | 0
8352 | 0
8353 | 0
8354 | 0
8355 | 0
8356 | 0
8357 | 0
8358 | 0
8359 | 0
8360 | 0
8361 | 0.066
8362 | 0.136
8363 | 0.26701
8364 | 0.206
8365 | 0.092
8366 | 0.129
8367 | 0.076
8368 | 0.011
8369 | 0
8370 | 0
8371 | 0
8372 | 0
8373 | 0
8374 | 0
8375 | 0
8376 | 0
8377 | 0
8378 | 0
8379 | 0
8380 | 0
8381 | 0
8382 | 0
8383 | 0
8384 | 0
8385 | 0.067
8386 | 0.039
8387 | 0.198
8388 | 0.28101
8389 | 0.12
8390 | 0.043
8391 | 0.013
8392 | 0.014
8393 | 0
8394 | 0
8395 | 0
8396 | 0
8397 | 0
8398 | 0
8399 | 0
8400 | 0
8401 | 0
8402 | 0
8403 | 0
8404 | 0
8405 | 0
8406 | 0
8407 | 0
8408 | 0
8409 | 0.08901
8410 | 0.20101
8411 | 0.29501
8412 | 0.33402
8413 | 0.31502
8414 | 0.25101
8415 | 0.14601
8416 | 0.012
8417 | 0
8418 | 0
8419 | 0
8420 | 0
8421 | 0
8422 | 0
8423 | 0
8424 | 0
8425 | 0
8426 | 0
8427 | 0
8428 | 0
8429 | 0
8430 | 0
8431 | 0
8432 | 0
8433 | 0.08701
8434 | 0.17301
8435 | 0.051
8436 | 0.052
8437 | 0.148
8438 | 0.075
8439 | 0.079
8440 | 0.009
8441 | 0
8442 | 0
8443 | 0
8444 | 0
8445 | 0
8446 | 0
8447 | 0
8448 | 0
8449 | 0
8450 | 0
8451 | 0
8452 | 0
8453 | 0
8454 | 0
8455 | 0
8456 | 0
8457 | 0.09001
8458 | 0.19501
8459 | 0.24501
8460 | 0.31901
8461 | 0.30801
8462 | 0.24701
8463 | 0.13601
8464 | 0.013
8465 | 0
8466 | 0
8467 | 0
8468 | 0
8469 | 0
8470 | 0
8471 | 0
8472 | 0
8473 | 0
8474 | 0
8475 | 0
8476 | 0
8477 | 0
8478 | 0
8479 | 0
8480 | 0
8481 | 0.075
8482 | 0.156
8483 | 0.23001
8484 | 0.29701
8485 | 0.31001
8486 | 0.24801
8487 | 0.14501
8488 | 0.01
8489 | 0
8490 | 0
8491 | 0
8492 | 0
8493 | 0
8494 | 0
8495 | 0
8496 | 0
8497 | 0
8498 | 0
8499 | 0
8500 | 0
8501 | 0
8502 | 0
8503 | 0
8504 | 0
8505 | 0.034
8506 | 0.116
8507 | 0.105
8508 | 0.029
8509 | 0.034
8510 | 0.059
8511 | 0.034
8512 | 0.013
8513 | 0
8514 | 0
8515 | 0
8516 | 0
8517 | 0
8518 | 0
8519 | 0
8520 | 0
8521 | 0
8522 | 0
8523 | 0
8524 | 0
8525 | 0
8526 | 0
8527 | 0
8528 | 0
8529 | 0.08801
8530 | 0.21001
8531 | 0.28801
8532 | 0.32702
8533 | 0.29201
8534 | 0.24001
8535 | 0.11901
8536 | 0.012
8537 | 0
8538 | 0
8539 | 0
8540 | 0
8541 | 0
8542 | 0
8543 | 0
8544 | 0
8545 | 0
8546 | 0
8547 | 0
8548 | 0
8549 | 0
8550 | 0
8551 | 0
8552 | 0
8553 | 0.09201
8554 | 0.20401
8555 | 0.28401
8556 | 0.33002
8557 | 0.31201
8558 | 0.171
8559 | 0.07
8560 | 0.015
8561 | 0
8562 | 0
8563 | 0
8564 | 0
8565 | 0
8566 | 0
8567 | 0
8568 | 0
8569 | 0
8570 | 0
8571 | 0
8572 | 0
8573 | 0
8574 | 0
8575 | 0
8576 | 0
8577 | 0.08501
8578 | 0.20401
8579 | 0.29401
8580 | 0.31701
8581 | 0.30101
8582 | 0.24901
8583 | 0.13801
8584 | 0.016
8585 | 0
8586 | 0
8587 | 0
8588 | 0
8589 | 0
8590 | 0
8591 | 0
8592 | 0
8593 | 0
8594 | 0
8595 | 0
8596 | 0
8597 | 0
8598 | 0
8599 | 0
8600 | 0
8601 | 0.09001
8602 | 0.20601
8603 | 0.28401
8604 | 0.32201
8605 | 0.29001
8606 | 0.22501
8607 | 0.13901
8608 | 0.017
8609 | 0
8610 | 0
8611 | 0
8612 | 0
8613 | 0
8614 | 0
8615 | 0
8616 | 0
8617 | 0
8618 | 0
8619 | 0
8620 | 0
8621 | 0
8622 | 0
8623 | 0
8624 | 0
8625 | 0.09001
8626 | 0.20601
8627 | 0.28601
8628 | 0.32902
8629 | 0.31201
8630 | 0.25401
8631 | 0.15301
8632 | 0.013
8633 | 0
8634 | 0
8635 | 0
8636 | 0
8637 | 0
8638 | 0
8639 | 0
8640 | 0
8641 | 0
8642 | 0
8643 | 0
8644 | 0
8645 | 0
8646 | 0
8647 | 0
8648 | 0
8649 | 0.09001
8650 | 0.20401
8651 | 0.199
8652 | 0.31301
8653 | 0.26901
8654 | 0.25501
8655 | 0.15501
8656 | 0.013
8657 | 0
8658 | 0
8659 | 0
8660 | 0
8661 | 0
8662 | 0
8663 | 0
8664 | 0
8665 | 0
8666 | 0
8667 | 0
8668 | 0
8669 | 0
8670 | 0
8671 | 0
8672 | 0
8673 | 0.075
8674 | 0.155
8675 | 0.199
8676 | 0.25401
8677 | 0.24901
8678 | 0.21201
8679 | 0.13401
8680 | 0.016
8681 | 0
8682 | 0
8683 | 0
8684 | 0
8685 | 0
8686 | 0
8687 | 0
8688 | 0
8689 | 0
8690 | 0
8691 | 0
8692 | 0
8693 | 0
8694 | 0
8695 | 0
8696 | 0
8697 | 0.068
8698 | 0.141
8699 | 0.21001
8700 | 0.27201
8701 | 0.26901
8702 | 0.22601
8703 | 0.14701
8704 | 0.018
8705 | 0
8706 | 0
8707 | 0
8708 | 0
8709 | 0
8710 | 0
8711 | 0
8712 | 0
8713 | 0
8714 | 0
8715 | 0
8716 | 0
8717 | 0
8718 | 0
8719 | 0
8720 | 0
8721 | 0.068
8722 | 0.134
8723 | 0.152
8724 | 0.164
8725 | 0.126
8726 | 0.117
8727 | 0.062
8728 | 0.018
8729 | 0
8730 | 0
8731 | 0
8732 | 0
8733 | 0
8734 | 0
8735 | 0
8736 | 0
8737 | 0
8738 | 0
8739 | 0
8740 | 0
8741 | 0
8742 | 0
8743 | 0
8744 | 0
8745 | 0.053
8746 | 0.032
8747 | 0.099
8748 | 0.051
8749 | 0.097
8750 | 0.063
8751 | 0.042
8752 | 0.02
8753 | 0
8754 | 0
8755 | 0
8756 | 0
8757 | 0
8758 | 0
8759 | 0
8760 | 0

## Demand
Energy carrier | Electricity | Heat 60-70 °C | Heat 60-70 °C | Heat 30-40 °C | Heat 60-70 °C | Electricity | Cooling 10 - 20°C | Cooling 10 - 20°C | Cooling 10 - 20°C | Heat 30-40 °C | Heat 30-40 °C | Electricity
Hub | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Demand Sale Price (CHF/kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Period
1 | 25.4449 | 0 | 0 | 26.3 | 0 | 12.7225 | 0 | 0 | 0 | 0 | 182.3 | 103.2986
2 | 34.3685 | 0 | 0 | 27.2 | 0 | 17.1843 | 0 | 0 | 0 | 0 | 175.2 | 89.551
3 | 43.0606 | 0 | 0 | 40.7 | 0 | 21.5303 | 0 | 0 | 0 | 0 | 201.7 | 86.6997
4 | 40.9789 | 0 | 0 | 51.9 | 0 | 20.4894 | 0 | 0 | 0 | 0.6 | 224.5 | 87.7643
5 | 40.6426 | 0 | 0 | 61.1 | 0 | 20.3213 | 0 | 0 | 0 | 1.3 | 243.6 | 87.2924
6 | 41.3052 | 0 | 0 | 69.6 | 0 | 20.6526 | 0 | 0 | 0 | 2.3 | 258.2 | 86.3447
7 | 50.1324 | 0 | 42.9 | 230.7 | 56.3 | 25.0662 | 0 | 0 | 0 | 17.2 | 795 | 86.6968
8 | 71.5329 | 0.7 | 43 | 270.1 | 37.6 | 35.7665 | 0 | 0 | 0 | 66 | 757.2 | 106.0598
9 | 77.8141 | 2.1 | 43.2 | 258.6 | 0 | 38.9071 | 0 | 0 | 0 | 70.7 | 244.7 | 131.9003
10 | 73.1612 | 3.5 | 43.4 | 230 | 0 | 36.5806 | 0 | 0 | 0 | 89.2 | 268.5 | 131.9285
11 | 69.9975 | 3.5 | 43.4 | 193.8 | 0 | 34.9988 | 0 | 0 | 0 | 85.9 | 240.4 | 169.2141
12 | 67.0331 | 2.8 | 43.3 | 161.5 | 0 | 33.5166 | 0 | 0 | 0 | 70.9 | 214.6 | 334.6982
13 | 65.8905 | 1.4 | 43.1 | 138.6 | 75.1 | 32.9452 | 0 | 0 | 0 | 47.9 | 649.1 | 197.2367
14 | 64.5854 | 2.1 | 43.2 | 124.3 | 37.6 | 32.2927 | 0 | 0 | 0 | 47.8 | 570.3 | 182.9113
15 | 60.6119 | 3.5 | 43.4 | 120.4 | 0 | 30.3059 | 0 | 0 | 0 | 63.2 | 99.4 | 150.8067
16 | 67.8104 | 2.8 | 43.3 | 121.9 | 0 | 33.9052 | 0 | 0 | 0 | 63.5 | 144.3 | 166.4978
17 | 81.0057 | 2.1 | 43.2 | 131.2 | 0 | 40.5028 | 0 | 0 | 0 | 54.3 | 171.3 | 158.479
18 | 78.7773 | 0.7 | 43 | 141.1 | 37.6 | 39.3887 | 0 | 0 | 0 | 36.7 | 659.2 | 212.3448
19 | 77.6945 | 0 | 42.9 | 104.5 | 75.1 | 38.8472 | 0 | 0 | 0 | 0 | 590.8 | 215.9418
20 | 62.1354 | 0 | 42.9 | 77.7 | 75.1 | 31.0677 | 0 | 0 | 0 | 0 | 515.8 | 170.5223
21 | 48.5518 | 0 | 42.9 | 95.3 | 75.1 | 24.2759 | 0 | 0 | 0 | 0 | 567.7 | 210.2904
22 | 43.7567 | 0 | 42.9 | 108.5 | 93.9 | 21.8784 | 0 | 0 | 0 | 0 | 595.5 | 189.4975
23 | 42.5214 | 0 | 0 | 10.5 | 0 | 21.2607 | 0 | 0 | 0 | 0 | 133.1 | 218.2839
24 | 41.2928 | 0 | 0 | 32.7 | 0 | 20.6464 | 0 | 0 | 0 | 0 | 211.3 | 149.9869
25 | 41.6108 | 0 | 0 | 50.9 | 0 | 20.8054 | 0 | 0 | 0 | 0.5 | 244.8 | 106.302
26 | 44.4962 | 0 | 0 | 67.7 | 0 | 22.2481 | 0 | 0 | 0 | 2.4 | 277.6 | 99.2296
27 | 43.0194 | 0 | 0 | 82.9 | 0 | 21.5097 | 0 | 0 | 0 | 7.3 | 308.5 | 85.8644
28 | 40.7263 | 0 | 0 | 95 | 0 | 20.3631 | 0 | 0 | 0 | 11.9 | 333.7 | 78.526
29 | 42.0645 | 0 | 0 | 105.3 | 0 | 21.0323 | 0 | 0 | 0 | 15.9 | 356.3 | 79.7153
30 | 41.4063 | 0 | 0 | 114.7 | 0 | 20.7031 | 0 | 0 | 0 | 19.5 | 373.9 | 86.3412
31 | 46.7425 | 0 | 0 | 257.9 | 0 | 23.3713 | 0 | 0 | 0 | 35.7 | 878.7 | 89.3047
32 | 57.5325 | 0.7 | 43 | 331.8 | 37.6 | 28.7662 | 0 | 0 | 0 | 88.3 | 886 | 135.27
33 | 68.3237 | 2.1 | 43.2 | 323.6 | 0 | 34.1618 | 0 | 0 | 0 | 102.3 | 350.7 | 193.8048
34 | 67.5622 | 3.5 | 43.4 | 285.9 | 0 | 33.7811 | 0 | 0 | 0 | 123.9 | 367.6 | 156.1381
35 | 69.0312 | 3.5 | 43.4 | 227.3 | 0 | 34.5156 | 0 | 0 | 0 | 114.1 | 320.3 | 164.1223
36 | 68.2607 | 2.8 | 43.3 | 170 | 0 | 34.1304 | 0 | 0 | 0 | 83.2 | 269.2 | 178.571
37 | 64.0796 | 1.4 | 43.1 | 124 | 75.1 | 32.0398 | 0 | 0 | 0 | 47.3 | 687.5 | 177.1656
38 | 63.0218 | 2.1 | 43.2 | 96.2 | 37.6 | 31.5109 | 0 | 0 | 0 | 45.3 | 568.6 | 189.4099
39 | 59.5941 | 3.5 | 43.4 | 98.8 | 0 | 29.797 | 0 | 0 | 0 | 59.9 | 99.2 | 161.9338
40 | 66.6151 | 2.8 | 43.3 | 110.7 | 0 | 33.3075 | 0 | 0 | 0 | 65.2 | 157.4 | 351.5018
41 | 70.4897 | 2.1 | 43.2 | 132.1 | 0 | 35.2449 | 0 | 0 | 0 | 60.1 | 200.1 | 240.7779
42 | 70.7795 | 0.7 | 43 | 147.5 | 37.6 | 35.3897 | 0 | 0 | 0 | 38.7 | 692.2 | 382.966
43 | 64.0424 | 0 | 42.9 | 101.2 | 75.1 | 32.0212 | 0 | 0 | 0 | 0 | 620.6 | 279.154
44 | 50.7628 | 0 | 42.9 | 70.9 | 75.1 | 25.3814 | 0 | 0 | 0 | 0 | 545.7 | 242.3682
45 | 40.6212 | 0 | 42.9 | 91.7 | 75.1 | 20.3106 | 0 | 0 | 0 | 0 | 597.8 | 234.4924
46 | 41.745 | 0 | 42.9 | 107.4 | 93.9 | 20.8725 | 0 | 0 | 0 | 0 | 628.2 | 190.7334
47 | 38.22 | 0 | 0 | 6.6 | 0 | 19.11 | 0 | 0 | 0 | 0 | 155.4 | 183.9149
48 | 40.8218 | 0 | 0 | 24.4 | 0 | 20.4109 | 0 | 0 | 0 | 1 | 237.2 | 143.8375
49 | 40.068 | 0 | 0 | 44.6 | 0 | 20.034 | 0 | 0 | 0 | 2.3 | 270.3 | 108.1249
50 | 40.3101 | 0 | 0 | 61.7 | 0 | 20.155 | 0 | 0 | 0 | 3.6 | 298.4 | 94.2064
51 | 43.3107 | 0 | 0 | 77.4 | 0 | 21.6554 | 0 | 0 | 0 | 6 | 325.8 | 93.3687
52 | 41.48 | 0 | 0 | 89.8 | 0 | 20.74 | 0 | 0 | 0 | 9.4 | 347.1 | 78.4042
53 | 40.2912 | 0 | 0 | 100.3 | 0 | 20.1456 | 0 | 0 | 0 | 12.5 | 366.3 | 82.4346
54 | 40.7675 | 0 | 0 | 110.1 | 0 | 20.3838 | 0 | 0 | 0 | 15.2 | 381.6 | 90.9793
55 | 60.1296 | 0 | 42.9 | 277.8 | 56.3 | 30.0648 | 0 | 0 | 0 | 31.8 | 925.3 | 108.4857
56 | 96.5055 | 0.7 | 43 | 325.6 | 37.6 | 48.2528 | 0 | 0 | 0 | 84.4 | 881.1 | 188.936
57 | 184.2083 | 2.1 | 43.2 | 315 | 0 | 92.1042 | 0 | 0 | 0 | 94.8 | 347.2 | 107.0291
58 | 282.6186 | 3.5 | 43.4 | 264.2 | 0 | 141.3093 | 0 | 0 | 0 | 105.4 | 345.8 | 129.6015
59 | 354.3105 | 3.5 | 43.4 | 184.9 | 0 | 177.1553 | 0 | 0 | 0 | 82.6 | 271.8 | 219.699
60 | 319.3494 | 2.8 | 43.3 | 118.1 | 0 | 159.6747 | 0 | 0 | 0 | 47.4 | 204.4 | 268.7748
61 | 295.9664 | 1.4 | 43.1 | 70.5 | 75.1 | 147.9832 | 0 | 0 | 0 | 13.5 | 603 | 251.5628
62 | 283.7009 | 2.1 | 43.2 | 38.3 | 37.6 | 141.8504 | 0 | 0 | 0 | 4.6 | 480.2 | 164.5037
63 | 274.5424 | 3.5 | 43.4 | 26.7 | 0 | 137.2712 | 0 | 0 | 0 | 6.1 | 29.6 | 126.8697
64 | 288.3172 | 2.8 | 43.3 | 37.9 | 0 | 144.1586 | 0 | 0 | 0 | 11 | 65.4 | 145.8566
65 | 257.6826 | 2.1 | 43.2 | 69.3 | 0 | 128.8413 | 0 | 0 | 0 | 19.5 | 111.6 | 187.5475
66 | 167.4998 | 0.7 | 43 | 93 | 37.6 | 83.7499 | 0 | 0 | 0 | 10.7 | 599.3 | 286.3638
67 | 108.8683 | 0 | 42.9 | 53.4 | 75.1 | 54.4342 | 0 | 0 | 0 | 0 | 521 | 260.7426
68 | 61.0008 | 0 | 42.9 | 27.9 | 75.1 | 30.5004 | 0 | 0 | 0 | 0 | 454.7 | 217.1901
69 | 45.694 | 0 | 42.9 | 51.8 | 75.1 | 22.847 | 0 | 0 | 0 | 0 | 512.1 | 164.1973
70 | 40.4548 | 0 | 42.9 | 72.7 | 93.9 | 20.2274 | 0 | 0 | 0 | 0 | 548.1 | 150.0109
71 | 38.4276 | 0 | 0 | 0 | 0 | 19.2138 | 0 | 0 | 0 | 0 | 101.5 | 168.6003
72 | 41.6505 | 0 | 0 | 2.6 | 0 | 20.8252 | 0 | 0 | 0 | 0 | 176.7 | 157.4599
73 | 41.3465 | 0 | 0 | 17.5 | 0 | 20.6732 | 0 | 0 | 0 | 0 | 217.1 | 105.5774
74 | 41.7249 | 0 | 0 | 39.2 | 0 | 20.8624 | 0 | 0 | 0 | 0 | 257.3 | 80.4263
75 | 39.9382 | 0 | 0 | 62.1 | 0 | 19.9691 | 0 | 0 | 0 | 0.1 | 299.1 | 77.6854
76 | 40.3119 | 0 | 0 | 80.6 | 0 | 20.156 | 0 | 0 | 0 | 1.8 | 333.3 | 77.2078
77 | 41.6511 | 0 | 0 | 95.7 | 0 | 20.8256 | 0 | 0 | 0 | 3.9 | 361.7 | 81.6093
78 | 42.7436 | 0 | 0 | 109.6 | 0 | 21.3718 | 0 | 0 | 0 | 7.9 | 384.3 | 149.68
79 | 50.9692 | 0 | 42.9 | 283.4 | 56.3 | 25.4846 | 0 | 0 | 0 | 28.7 | 924.7 | 110.8997
80 | 83.5508 | 0.7 | 43 | 334.7 | 37.6 | 41.7754 | 0 | 0 | 0 | 85.4 | 885.4 | 120.3667
81 | 196.0282 | 2.1 | 43.2 | 335.1 | 0 | 98.0141 | 0 | 0 | 0 | 99.8 | 373 | 177.7705
82 | 330.9501 | 3.5 | 43.4 | 333.6 | 0 | 165.4751 | 0 | 0 | 0 | 125.5 | 426.4 | 144.8963
83 | 399.4092 | 3.5 | 43.4 | 312.9 | 0 | 199.7046 | 0 | 0 | 0 | 116.5 | 415.5 | 154.4857
84 | 406.9323 | 2.8 | 43.3 | 282.7 | 0 | 203.4661 | 0 | 0 | 0 | 81.9 | 400.2 | 179.0419
85 | 392.2984 | 1.4 | 43.1 | 254.7 | 75.1 | 196.1492 | 0 | 0 | 0 | 44 | 887.9 | 168.0423
86 | 379.8658 | 2.1 | 43.2 | 245.2 | 37.6 | 189.9329 | 0 | 0 | 0 | 41.3 | 801.6 | 213.1783
87 | 383.9004 | 3.5 | 43.4 | 256.2 | 0 | 191.9502 | 0 | 0 | 0 | 67.7 | 292.3 | 155.5492
88 | 365.9639 | 2.8 | 43.3 | 255.5 | 0 | 182.982 | 0 | 0 | 0 | 74.1 | 364.1 | 150.5869
89 | 316.7678 | 2.1 | 43.2 | 256.1 | 0 | 158.3839 | 0 | 0 | 0 | 65 | 393.1 | 144.2016
90 | 223.5009 | 0.7 | 43 | 259.4 | 37.6 | 111.7505 | 0 | 0 | 0 | 39 | 914.8 | 154.3252
91 | 150.7671 | 0 | 42.9 | 205.1 | 75.1 | 75.3835 | 0 | 0 | 0 | 0 | 866.9 | 272.7876
92 | 85.6434 | 0 | 42.9 | 173.9 | 75.1 | 42.8217 | 0 | 0 | 0 | 0 | 783 | 248.7643
93 | 55.6342 | 0 | 42.9 | 188.6 | 75.1 | 27.8171 | 0 | 0 | 0 | 0 | 832.1 | 321.5819
94 | 42.5644 | 0 | 42.9 | 198.2 | 93.9 | 21.2822 | 0 | 0 | 0 | 0 | 864.3 | 225.2205
95 | 42.8846 | 0 | 0 | 86.6 | 0 | 21.4423 | 0 | 0 | 0 | 0.1 | 338.2 | 161.5223
96 | 41.5377 | 0 | 0 | 113.8 | 0 | 20.7688 | 0 | 0 | 0 | 1.5 | 430.7 | 139.4573
97 | 42.4346 | 0 | 0 | 128.5 | 0 | 21.2173 | 0 | 0 | 0 | 3.4 | 460.3 | 94.6781
98 | 43.1211 | 0 | 0 | 142.6 | 0 | 21.5605 | 0 | 0 | 0 | 6.6 | 490.8 | 73.3552
99 | 40.0751 | 0 | 0 | 149.2 | 0 | 20.0376 | 0 | 0 | 0 | 10.7 | 504.3 | 73.7018
100 | 41.5984 | 0 | 0 | 151.8 | 0 | 20.7992 | 0 | 0 | 0 | 14.3 | 507.5 | 75.7959
101 | 41.2067 | 0 | 0 | 156.5 | 0 | 20.6033 | 0 | 0 | 0 | 18.6 | 516.4 | 77.6817
102 | 43.3702 | 0 | 0 | 161.9 | 0 | 21.6851 | 0 | 0 | 0 | 21.9 | 523.3 | 93.6029
103 | 58.2199 | 0 | 42.9 | 332.7 | 56.3 | 29.1099 | 0 | 0 | 0 | 39.6 | 1093.4 | 102.2193
104 | 94.117 | 0.7 | 43 | 385.2 | 37.6 | 47.0585 | 0 | 0 | 0 | 93.2 | 1059.7 | 226.4006
105 | 207.2049 | 2.1 | 43.2 | 382.4 | 0 | 103.6024 | 0 | 0 | 0 | 109.2 | 475.7 | 188.3702
106 | 350.046 | 3.5 | 43.4 | 389.6 | 0 | 175.023 | 0 | 0 | 0 | 146.2 | 531.1 | 146.5532
107 | 349.5771 | 3.5 | 43.4 | 375.4 | 0 | 174.7885 | 0 | 0 | 0 | 149.4 | 529.2 | 205.7583
108 | 304.6033 | 2.8 | 43.3 | 353.9 | 0 | 152.3017 | 0 | 0 | 0 | 124.3 | 526.9 | 121.5124
109 | 278.3665 | 1.4 | 43.1 | 331.4 | 75.1 | 139.1833 | 0 | 0 | 0 | 88.1 | 1093.3 | 239.0689
110 | 282.5904 | 2.1 | 43.2 | 323.3 | 37.6 | 141.2952 | 0 | 0 | 0 | 93.8 | 1010.3 | 141.4071
111 | 352.2077 | 3.5 | 43.4 | 332.6 | 0 | 176.1039 | 0 | 0 | 0 | 126.1 | 427.7 | 127.3514
112 | 372.0158 | 2.8 | 43.3 | 327.1 | 0 | 186.0079 | 0 | 0 | 0 | 125.2 | 494.5 | 134.6134
113 | 305.9543 | 2.1 | 43.2 | 318.4 | 0 | 152.9771 | 0 | 0 | 0 | 104.1 | 516.3 | 149.4164
114 | 229.2642 | 0.7 | 43 | 315.5 | 37.6 | 114.6321 | 0 | 0 | 0 | 64.5 | 1096.8 | 180.8326
115 | 126.2398 | 0 | 42.9 | 246.5 | 75.1 | 63.1199 | 0 | 0 | 0 | 14 | 1045.8 | 270.2337
116 | 87.5382 | 0 | 42.9 | 212.3 | 75.1 | 43.7691 | 0 | 0 | 0 | 6.3 | 949.9 | 348.1909
117 | 59.3598 | 0 | 42.9 | 221.1 | 75.1 | 29.6799 | 0 | 0 | 0 | 11.9 | 980.5 | 272.6904
118 | 41.9248 | 0 | 42.9 | 226.2 | 93.9 | 20.9624 | 0 | 0 | 0 | 16.4 | 998.3 | 366.6148
119 | 40.2208 | 0 | 0 | 122.6 | 0 | 20.1104 | 0 | 0 | 0 | 21.1 | 435.4 | 233.852
120 | 39.7345 | 0 | 0 | 159.5 | 0 | 19.8673 | 0 | 0 | 0 | 26.3 | 548.7 | 149.4062
121 | 41.2953 | 0 | 0 | 162 | 0 | 20.6477 | 0 | 0 | 0 | 28.9 | 549.9 | 109.6918
122 | 42.839 | 0 | 0 | 163.8 | 0 | 21.4195 | 0 | 0 | 0 | 31.3 | 550.1 | 77.6812
123 | 43.3721 | 0 | 0 | 172.9 | 0 | 21.6861 | 0 | 0 | 0 | 34.4 | 572.1 | 75.9129
124 | 39.7119 | 0 | 0 | 180.9 | 0 | 19.856 | 0 | 0 | 0 | 36.9 | 592.9 | 78.2872
125 | 43.0445 | 0 | 0 | 186.9 | 0 | 21.5223 | 0 | 0 | 0 | 39 | 610.5 | 78.7679
126 | 43.126 | 0 | 0 | 192.7 | 0 | 21.563 | 0 | 0 | 0 | 40.9 | 624.2 | 78.4047
127 | 48.2097 | 0 | 42.9 | 371.4 | 56.3 | 24.1048 | 0 | 0 | 0 | 54.2 | 1250.8 | 176.4662
128 | 62.3372 | 0 | 42.9 | 404 | 37.6 | 31.1686 | 0 | 0 | 0 | 55.7 | 1200.5 | 207.1305
129 | 72.4837 | 0 | 42.9 | 397.7 | 0 | 36.2419 | 0 | 0 | 0 | 56.5 | 579.7 | 401.594
130 | 70.5195 | 0 | 42.9 | 398.8 | 0 | 35.2597 | 0 | 0 | 0 | 55.5 | 633 | 157.239
131 | 71.3677 | 0 | 42.9 | 378.4 | 0 | 35.6839 | 0 | 0 | 0 | 54.6 | 625.8 | 116.0903
132 | 69.9294 | 0 | 42.9 | 354 | 0 | 34.9647 | 0 | 0 | 0 | 54.6 | 617.8 | 243.3355
133 | 61.021 | 0 | 42.9 | 340 | 75.1 | 30.5105 | 0 | 0 | 0 | 55.1 | 1210.4 | 165.5969
134 | 60.874 | 0 | 42.9 | 325.2 | 37.6 | 30.437 | 0 | 0 | 0 | 56.1 | 1113.7 | 202.4734
135 | 56.4056 | 0 | 42.9 | 331.6 | 0 | 28.2028 | 0 | 0 | 0 | 57.1 | 502.4 | 343.4194
136 | 60.9054 | 0 | 42.9 | 327.3 | 0 | 30.4527 | 0 | 0 | 0 | 58.5 | 570.5 | 190.534
137 | 72.7698 | 0 | 42.9 | 328.2 | 0 | 36.3849 | 0 | 0 | 0 | 59.5 | 593.3 | 157.6872
138 | 73.7417 | 0 | 42.9 | 331.9 | 37.6 | 36.8709 | 0 | 0 | 0 | 59.5 | 1196.3 | 251.4922
139 | 68.8313 | 0 | 42.9 | 285.5 | 75.1 | 34.4157 | 0 | 0 | 0 | 57.6 | 1140.7 | 422.2083
140 | 52.8443 | 0 | 42.9 | 241.6 | 75.1 | 26.4221 | 0 | 0 | 0 | 44.7 | 1034.8 | 208.7551
141 | 45.4291 | 0 | 42.9 | 253.1 | 75.1 | 22.7145 | 0 | 0 | 0 | 48.3 | 1071.5 | 243.6579
142 | 40.6342 | 0 | 42.9 | 260.6 | 93.9 | 20.3171 | 0 | 0 | 0 | 49.8 | 1096 | 384.9639
143 | 42.1237 | 0 | 0 | 147.8 | 0 | 21.0619 | 0 | 0 | 0 | 51 | 497 | 196.2143
144 | 44.0459 | 0 | 0 | 177.2 | 0 | 22.0229 | 0 | 0 | 0 | 52.9 | 587.1 | 116.2343
145 | 39.9276 | 0 | 0 | 183.7 | 0 | 19.9638 | 0 | 0 | 0 | 53.8 | 600.4 | 81.9649
146 | 43.069 | 0 | 0 | 188.5 | 0 | 21.5345 | 0 | 0 | 0 | 54.4 | 612.1 | 76.38
147 | 40.4824 | 0 | 0 | 195.5 | 0 | 20.2412 | 0 | 0 | 0 | 55.4 | 631.7 | 75.3255
148 | 38.7914 | 0 | 0 | 202.7 | 0 | 19.3957 | 0 | 0 | 0 | 57.4 | 654 | 76.4963
149 | 41.8532 | 0 | 0 | 204.3 | 0 | 20.9266 | 0 | 0 | 0 | 57.8 | 663.4 | 81.4914
150 | 43.1756 | 0 | 0 | 205.8 | 0 | 21.5878 | 0 | 0 | 0 | 57.8 | 667.2 | 98.2723
151 | 52.1448 | 0 | 42.9 | 391.7 | 56.3 | 26.0724 | 0 | 0 | 0 | 74.3 | 1303.6 | 122.4281
152 | 73.5446 | 0 | 42.9 | 393.7 | 37.6 | 36.7723 | 0 | 0 | 0 | 75.2 | 1245.5 | 138.527
153 | 78.1993 | 0 | 42.9 | 373.8 | 0 | 39.0997 | 0 | 0 | 0 | 74.9 | 607.3 | 133.7218
154 | 75.5281 | 0 | 42.9 | 366.2 | 0 | 37.7641 | 0 | 0 | 0 | 73.5 | 667.2 | 127.4552
155 | 72.4245 | 0 | 42.9 | 357.9 | 0 | 36.2123 | 0 | 0 | 0 | 71.7 | 672.9 | 187.4217
156 | 70.2972 | 0 | 42.9 | 350.4 | 0 | 35.1486 | 0 | 0 | 0 | 70.1 | 677 | 338.6461
157 | 65.2653 | 0 | 42.9 | 350.5 | 75.1 | 32.6327 | 0 | 0 | 0 | 68.6 | 1290.6 | 187.927
158 | 61.1899 | 0 | 42.9 | 292.1 | 37.6 | 30.5949 | 0 | 0 | 0 | 68.2 | 1125.3 | 153.2332
159 | 57.8238 | 0 | 42.9 | 262.8 | 0 | 28.9119 | 0 | 0 | 0 | 68.2 | 466.9 | 137.2016
160 | 65.8616 | 0 | 42.9 | 255 | 0 | 32.9308 | 0 | 0 | 0 | 68.4 | 517.6 | 129.207
161 | 78.2142 | 0 | 42.9 | 266.7 | 0 | 39.1071 | 0 | 0 | 0 | 69.2 | 539.4 | 152.6086
162 | 76.814 | 0 | 42.9 | 285.8 | 37.6 | 38.407 | 0 | 0 | 0 | 70.2 | 1131.6 | 260.2923
163 | 78.1002 | 0 | 42.9 | 270.6 | 75.1 | 39.0501 | 0 | 0 | 0 | 68.5 | 1072.9 | 277.5398
164 | 58.5304 | 0 | 42.9 | 226 | 75.1 | 29.2652 | 0 | 0 | 0 | 53.5 | 968.5 | 519.0525
165 | 47.6466 | 0 | 42.9 | 238.1 | 75.1 | 23.8233 | 0 | 0 | 0 | 56.9 | 1006.4 | 327.6229
166 | 43.1263 | 0 | 42.9 | 245.8 | 93.9 | 21.5632 | 0 | 0 | 0 | 58.3 | 1028.9 | 255.4433
167 | 43.5007 | 0 | 0 | 135.3 | 0 | 21.7504 | 0 | 0 | 0 | 60.2 | 447.5 | 213.7059
168 | 41.7019 | 0 | 0 | 163.4 | 0 | 20.851 | 0 | 0 | 0 | 61.3 | 535 | 147.5208
169 | 44.0961 | 0 | 0 | 175.1 | 0 | 22.048 | 0 | 0 | 0 | 62.5 | 560.9 | 120.8676
170 | 42.0218 | 0 | 0 | 186.6 | 0 | 21.0109 | 0 | 0 | 0 | 64.2 | 588.3 | 106.7937
171 | 40.1272 | 0 | 0 | 197.8 | 0 | 20.0636 | 0 | 0 | 0 | 66.4 | 617.9 | 97.7981
172 | 41.0601 | 0 | 0 | 206.6 | 0 | 20.53 | 0 | 0 | 0 | 67.6 | 643.9 | 83.1472
173 | 43.4756 | 0 | 0 | 214 | 0 | 21.7378 | 0 | 0 | 0 | 68.3 | 667.6 | 78.6484
174 | 44.1017 | 0 | 0 | 220.6 | 0 | 22.0508 | 0 | 0 | 0 | 69.4 | 684.7 | 78.8864
175 | 69.144 | 0 | 42.9 | 412.2 | 56.3 | 34.572 | 0 | 0 | 0 | 87.6 | 1324.4 | 99.5905
176 | 109.8176 | 0.7 | 43 | 476.6 | 37.6 | 54.9088 | 0 | 0 | 0 | 159.6 | 1275.1 | 112.9649
177 | 202.2136 | 2.1 | 43.2 | 466.8 | 0 | 101.1068 | 0 | 0 | 0 | 170.8 | 633.5 | 118.4831
178 | 306.4625 | 3.5 | 43.4 | 457.7 | 0 | 153.2313 | 0 | 0 | 0 | 220.9 | 667.9 | 121.8449
179 | 339.7863 | 3.5 | 43.4 | 418.6 | 0 | 169.8932 | 0 | 0 | 0 | 225.9 | 641.4 | 117.3935
180 | 306.103 | 2.8 | 43.3 | 352.8 | 0 | 153.0515 | 0 | 0 | 0 | 195.4 | 593.9 | 177.1599
181 | 246.9831 | 1.4 | 43.1 | 315.1 | 75.1 | 123.4916 | 0 | 0 | 0 | 141.5 | 1148.4 | 123.7257
182 | 238.9657 | 2.1 | 43.2 | 324.5 | 37.6 | 119.4829 | 0 | 0 | 0 | 138.3 | 1077 | 175.7742
183 | 231.2691 | 3.5 | 43.4 | 340.8 | 0 | 115.6346 | 0 | 0 | 0 | 167.5 | 481.9 | 172.2543
184 | 270.0212 | 2.8 | 43.3 | 335.2 | 0 | 135.0106 | 0 | 0 | 0 | 160.9 | 547.4 | 187.7937
185 | 278.369 | 2.1 | 43.2 | 333 | 0 | 139.1845 | 0 | 0 | 0 | 137.9 | 576 | 201.6828
186 | 189.7026 | 0.7 | 43 | 334.5 | 37.6 | 94.8513 | 0 | 0 | 0 | 92.5 | 1170.4 | 326.447
187 | 113.3377 | 0 | 42.9 | 266.6 | 75.1 | 56.6689 | 0 | 0 | 0 | 36.2 | 1124.5 | 311.6202
188 | 66.9941 | 0 | 42.9 | 234.5 | 75.1 | 33.497 | 0 | 0 | 0 | 31.9 | 1027.8 | 338.4763
189 | 47.6407 | 0 | 42.9 | 248.9 | 75.1 | 23.8203 | 0 | 0 | 0 | 38.4 | 1071.1 | 249.3246
190 | 41.9657 | 0 | 42.9 | 258.4 | 93.9 | 20.9828 | 0 | 0 | 0 | 43.5 | 1103.2 | 269.9731
191 | 40.6758 | 0 | 0 | 147.6 | 0 | 20.3379 | 0 | 0 | 0 | 47.8 | 516.8 | 254.8062
192 | 42.1823 | 0 | 0 | 175.2 | 0 | 21.0912 | 0 | 0 | 0 | 51.7 | 609.8 | 125.1289
193 | 40.4768 | 0 | 0 | 188.8 | 0 | 20.2384 | 0 | 0 | 0 | 54.7 | 637.7 | 101.7432
194 | 40.7746 | 0 | 0 | 200 | 0 | 20.3873 | 0 | 0 | 0 | 57.7 | 660.1 | 89.0702
195 | 42.1395 | 0 | 0 | 209.4 | 0 | 21.0698 | 0 | 0 | 0 | 60.7 | 681.6 | 76.4953
196 | 41.1586 | 0 | 0 | 218.1 | 0 | 20.5793 | 0 | 0 | 0 | 63 | 703.5 | 73.0087
197 | 43.7133 | 0 | 0 | 225.3 | 0 | 21.8567 | 0 | 0 | 0 | 64.9 | 723.7 | 77.8033
198 | 41.5274 | 0 | 0 | 231.6 | 0 | 20.7637 | 0 | 0 | 0 | 66.5 | 739.5 | 81.6088
199 | 55.6509 | 0 | 42.9 | 419.3 | 56.3 | 27.8255 | 0 | 0 | 0 | 84.2 | 1382.3 | 98.2737
200 | 97.3718 | 0.7 | 43 | 485.9 | 37.6 | 48.6859 | 0 | 0 | 0 | 156.9 | 1328.4 | 149.506
201 | 196.8767 | 2.1 | 43.2 | 483.8 | 0 | 98.4384 | 0 | 0 | 0 | 172.6 | 686.4 | 117.1864
202 | 280.5778 | 3.5 | 43.4 | 498.6 | 0 | 140.2889 | 0 | 0 | 0 | 221.8 | 747.3 | 123.7595
203 | 302.6756 | 3.5 | 43.4 | 490 | 0 | 151.3378 | 0 | 0 | 0 | 218 | 752.7 | 130.1929
204 | 292.821 | 2.8 | 43.3 | 469.2 | 0 | 146.4105 | 0 | 0 | 0 | 176.9 | 759.1 | 187.6107
205 | 294.0089 | 1.4 | 43.1 | 437.5 | 75.1 | 147.0045 | 0 | 0 | 0 | 120.3 | 1394.8 | 156.9512
206 | 298.377 | 2.1 | 43.2 | 380.1 | 37.6 | 149.1885 | 0 | 0 | 0 | 123.5 | 1209.5 | 135.1482
207 | 286.294 | 3.5 | 43.4 | 363.1 | 0 | 143.147 | 0 | 0 | 0 | 159.2 | 540.5 | 119.1909
208 | 324.9745 | 2.8 | 43.3 | 347.1 | 0 | 162.4873 | 0 | 0 | 0 | 157.6 | 596.1 | 104.6177
209 | 299.8299 | 2.1 | 43.2 | 345.1 | 0 | 149.9149 | 0 | 0 | 0 | 135.4 | 624.1 | 121.4858
210 | 208.9656 | 0.7 | 43 | 347 | 37.6 | 104.4828 | 0 | 0 | 0 | 89.4 | 1226.5 | 183.5566
211 | 134.556 | 0 | 42.9 | 275.7 | 75.1 | 67.278 | 0 | 0 | 0 | 34.5 | 1174.7 | 248.4004
212 | 78.8886 | 0 | 42.9 | 240.8 | 75.1 | 39.4443 | 0 | 0 | 0 | 30.2 | 1068.4 | 222.8638
213 | 55.0159 | 0 | 42.9 | 253.2 | 75.1 | 27.5079 | 0 | 0 | 0 | 36.8 | 1105.4 | 350.6825
214 | 40.4691 | 0 | 42.9 | 260.6 | 93.9 | 20.2345 | 0 | 0 | 0 | 41.2 | 1130.7 | 266.3082
215 | 40.9913 | 0 | 0 | 147.3 | 0 | 20.4956 | 0 | 0 | 0 | 45 | 531.5 | 202.0051
216 | 39.3121 | 0 | 0 | 173.1 | 0 | 19.6561 | 0 | 0 | 0 | 48.7 | 617.4 | 146.8402
217 | 39.87 | 0 | 0 | 184.6 | 0 | 19.935 | 0 | 0 | 0 | 51.9 | 638.4 | 111.5057
218 | 42.2663 | 0 | 0 | 194.3 | 0 | 21.1332 | 0 | 0 | 0 | 55.7 | 657.8 | 80.5431
219 | 42.7668 | 0 | 0 | 203.1 | 0 | 21.3834 | 0 | 0 | 0 | 58.4 | 678 | 80.1862
220 | 42.4495 | 0 | 0 | 210.6 | 0 | 21.2247 | 0 | 0 | 0 | 59.9 | 697.4 | 78.8869
221 | 40.532 | 0 | 0 | 216.2 | 0 | 20.266 | 0 | 0 | 0 | 62.2 | 713.6 | 81.7273
222 | 42.3983 | 0 | 0 | 221.3 | 0 | 21.1992 | 0 | 0 | 0 | 65 | 726 | 90.2639
223 | 54.2054 | 0 | 42.9 | 407.3 | 56.3 | 27.1027 | 0 | 0 | 0 | 81.4 | 1371.2 | 106.4336
224 | 90.3889 | 0.7 | 43 | 470.9 | 37.6 | 45.1944 | 0 | 0 | 0 | 152.6 | 1313.9 | 132.052
225 | 181.2281 | 2.1 | 43.2 | 467.7 | 0 | 90.6141 | 0 | 0 | 0 | 168.1 | 669.3 | 147.6628
226 | 303.7457 | 3.5 | 43.4 | 480.8 | 0 | 151.8729 | 0 | 0 | 0 | 210.9 | 727.9 | 138.8419
227 | 345.3578 | 3.5 | 43.4 | 468 | 0 | 172.6789 | 0 | 0 | 0 | 200.3 | 726.9 | 180.445
228 | 319.1563 | 2.8 | 43.3 | 440.6 | 0 | 159.5782 | 0 | 0 | 0 | 149.3 | 721.6 | 163.4582
229 | 282.0323 | 1.4 | 43.1 | 407.3 | 75.1 | 141.0161 | 0 | 0 | 0 | 97.6 | 1337.9 | 176.7798
230 | 277.31 | 2.1 | 43.2 | 395.5 | 37.6 | 138.655 | 0 | 0 | 0 | 103.7 | 1229 | 145.9189
231 | 245.9247 | 3.5 | 43.4 | 409.9 | 0 | 122.9624 | 0 | 0 | 0 | 134.5 | 595.4 | 134.9475
232 | 303.884 | 2.8 | 43.3 | 395.7 | 0 | 151.942 | 0 | 0 | 0 | 135.1 | 655 | 135.5046
233 | 332.7753 | 2.1 | 43.2 | 378.8 | 0 | 166.3876 | 0 | 0 | 0 | 119.6 | 670.6 | 148.1666
234 | 251.1441 | 0.7 | 43 | 374.1 | 37.6 | 125.5721 | 0 | 0 | 0 | 78.1 | 1295 | 150.1839
235 | 164.7489 | 0 | 42.9 | 302 | 75.1 | 82.3745 | 0 | 0 | 0 | 23.9 | 1250 | 217.2694
236 | 96.2387 | 0 | 42.9 | 263.2 | 75.1 | 48.1193 | 0 | 0 | 0 | 17.9 | 1143.9 | 322.4583
237 | 58.4071 | 0 | 42.9 | 276.6 | 75.1 | 29.2035 | 0 | 0 | 0 | 24.8 | 1182.1 | 297.2604
238 | 43.5605 | 0 | 42.9 | 286.7 | 93.9 | 21.7803 | 0 | 0 | 0 | 28.7 | 1213.3 | 245.8463
239 | 42.4702 | 0 | 0 | 174.4 | 0 | 21.2351 | 0 | 0 | 0 | 32.5 | 595.3 | 197.2731
240 | 41.8984 | 0 | 0 | 204.3 | 0 | 20.9492 | 0 | 0 | 0 | 36.8 | 685.1 | 108.366
241 | 43.546 | 0 | 0 | 216.7 | 0 | 21.773 | 0 | 0 | 0 | 40.3 | 714.8 | 106.0572
242 | 41.9728 | 0 | 0 | 228.3 | 0 | 20.9864 | 0 | 0 | 0 | 43.3 | 744.8 | 83.5014
243 | 41.5185 | 0 | 0 | 239 | 0 | 20.7592 | 0 | 0 | 0 | 46.2 | 775.1 | 78.0471
244 | 41.1754 | 0 | 0 | 246.9 | 0 | 20.5877 | 0 | 0 | 0 | 48.5 | 800.6 | 77.9244
245 | 42.3999 | 0 | 0 | 252.9 | 0 | 21.1999 | 0 | 0 | 0 | 50.3 | 821.5 | 77.5629
246 | 44.3133 | 0 | 0 | 259.4 | 0 | 22.1567 | 0 | 0 | 0 | 52.7 | 838.7 | 93.2449
247 | 63.9649 | 0 | 42.9 | 458.5 | 56.3 | 31.9825 | 0 | 0 | 0 | 67.9 | 1506.6 | 111.3866
248 | 102.1037 | 0.7 | 43 | 525.9 | 37.6 | 51.0518 | 0 | 0 | 0 | 133.7 | 1445.9 | 165.8331
249 | 183.2838 | 2.1 | 43.2 | 513.5 | 0 | 91.6419 | 0 | 0 | 0 | 150.4 | 768.6 | 122.304
250 | 306.4718 | 3.5 | 43.4 | 469.1 | 0 | 153.2359 | 0 | 0 | 0 | 194.6 | 757.5 | 115.3777
251 | 334.5124 | 3.5 | 43.4 | 375.7 | 0 | 167.2562 | 0 | 0 | 0 | 189.4 | 669.8 | 113.2036
252 | 290.2567 | 2.8 | 43.3 | 281.2 | 0 | 145.1283 | 0 | 0 | 0 | 151.9 | 578.2 | 82.7895
253 | 261.8535 | 1.4 | 43.1 | 202.4 | 75.1 | 130.9268 | 0 | 0 | 0 | 104.4 | 1052.7 | 151.0555
254 | 241.6432 | 2.1 | 43.2 | 155.4 | 37.6 | 120.8216 | 0 | 0 | 0 | 106.4 | 881.5 | 146.0648
255 | 242.3891 | 3.5 | 43.4 | 139 | 0 | 121.1946 | 0 | 0 | 0 | 139.1 | 286 | 164.0098
256 | 303.6444 | 2.8 | 43.3 | 138.3 | 0 | 151.8222 | 0 | 0 | 0 | 140.7 | 346.7 | 124.0455
257 | 326.747 | 2.1 | 43.2 | 157.8 | 0 | 163.3735 | 0 | 0 | 0 | 121.3 | 392.1 | 112.2393
258 | 213.1532 | 0.7 | 43 | 201.1 | 37.6 | 106.5766 | 0 | 0 | 0 | 79.3 | 951.9 | 207.0143
259 | 109.1767 | 0 | 42.9 | 159.1 | 75.1 | 54.5884 | 0 | 0 | 0 | 26.6 | 918.5 | 254.2286
260 | 63.8409 | 0 | 42.9 | 132.5 | 75.1 | 31.9205 | 0 | 0 | 0 | 22.3 | 842 | 287.7671
261 | 46.7379 | 0 | 42.9 | 162.2 | 75.1 | 23.3689 | 0 | 0 | 0 | 29.2 | 903.7 | 315.942
262 | 42.9667 | 0 | 42.9 | 185.6 | 93.9 | 21.4834 | 0 | 0 | 0 | 34.1 | 952.7 | 212.5751
263 | 42.1321 | 0 | 0 | 70.6 | 0 | 21.0661 | 0 | 0 | 0 | 38.6 | 426.8 | 162.7861
264 | 40.5366 | 0 | 0 | 110.9 | 0 | 20.2683 | 0 | 0 | 0 | 43.1 | 536.5 | 128.5558
265 | 41.4785 | 0 | 0 | 139.3 | 0 | 20.7392 | 0 | 0 | 0 | 48.7 | 585 | 101.9792
266 | 40.3978 | 0 | 0 | 166.9 | 0 | 20.1989 | 0 | 0 | 0 | 53.9 | 637.7 | 91.5805
267 | 41.7001 | 0 | 0 | 192.9 | 0 | 20.85 | 0 | 0 | 0 | 58.3 | 690.4 | 90.505
268 | 42.2387 | 0 | 0 | 214 | 0 | 21.1194 | 0 | 0 | 0 | 61.4 | 733.4 | 91.0962
269 | 40.8912 | 0 | 0 | 232.3 | 0 | 20.4456 | 0 | 0 | 0 | 64.4 | 771.9 | 92.5326
270 | 41.648 | 0 | 0 | 248.7 | 0 | 20.824 | 0 | 0 | 0 | 67.5 | 805.9 | 99.1103
271 | 54.3812 | 0 | 42.9 | 443.6 | 56.3 | 27.1906 | 0 | 0 | 0 | 85.6 | 1443.9 | 109.2079
272 | 87.8739 | 0.7 | 43 | 521.1 | 37.6 | 43.9369 | 0 | 0 | 0 | 158.9 | 1414.4 | 129.085
273 | 208.7074 | 2.1 | 43.2 | 526.6 | 0 | 104.3537 | 0 | 0 | 0 | 180.4 | 785 | 165.3282
274 | 342.8022 | 3.5 | 43.4 | 524.5 | 0 | 171.4011 | 0 | 0 | 0 | 243.4 | 827.2 | 111.0264
275 | 415.89 | 3.5 | 43.4 | 479.8 | 0 | 207.945 | 0 | 0 | 0 | 251.6 | 799.1 | 114.408
276 | 373.9131 | 2.8 | 43.3 | 419.3 | 0 | 186.9566 | 0 | 0 | 0 | 211.8 | 761.7 | 96.83
277 | 337.0618 | 1.4 | 43.1 | 368.8 | 75.1 | 168.5309 | 0 | 0 | 0 | 149.2 | 1334.3 | 183.9586
278 | 308.6624 | 2.1 | 43.2 | 351.4 | 37.6 | 154.3312 | 0 | 0 | 0 | 163 | 1194.2 | 102.1013
279 | 306.6634 | 3.5 | 43.4 | 373.6 | 0 | 153.3317 | 0 | 0 | 0 | 219 | 600.8 | 137.7638
280 | 378.283 | 2.8 | 43.3 | 383.9 | 0 | 189.1415 | 0 | 0 | 0 | 218 | 696 | 154.9996
281 | 349.521 | 2.1 | 43.2 | 389.2 | 0 | 174.7605 | 0 | 0 | 0 | 178.4 | 736.2 | 173.995
282 | 240.4493 | 0.7 | 43 | 401.4 | 37.6 | 120.2247 | 0 | 0 | 0 | 118.9 | 1330.2 | 337.8045
283 | 157.0495 | 0 | 42.9 | 328.3 | 75.1 | 78.5248 | 0 | 0 | 0 | 57.6 | 1336.5 | 192.7755
284 | 92.8432 | 0 | 42.9 | 294.4 | 75.1 | 46.4216 | 0 | 0 | 0 | 53.7 | 1252.1 | 252.5167
285 | 63.2319 | 0 | 42.9 | 315.6 | 75.1 | 31.616 | 0 | 0 | 0 | 59.3 | 1310.3 | 392.3617
286 | 42.6534 | 0 | 42.9 | 332 | 93.9 | 21.3267 | 0 | 0 | 0 | 62.8 | 1369 | 199.2978
287 | 42.3305 | 0 | 0 | 209.8 | 0 | 21.1652 | 0 | 0 | 0 | 66 | 765.2 | 176.9128
288 | 41.3833 | 0 | 0 | 244.6 | 0 | 20.6917 | 0 | 0 | 0 | 69.1 | 873.3 | 146.5207
289 | 42.187 | 0 | 0 | 259 | 0 | 21.0935 | 0 | 0 | 0 | 71 | 896.8 | 111.1502
290 | 40.9665 | 0 | 0 | 266.8 | 0 | 20.4832 | 0 | 0 | 0 | 72.3 | 906.6 | 91.9384
291 | 42.5567 | 0 | 0 | 273.1 | 0 | 21.2783 | 0 | 0 | 0 | 73.8 | 917.7 | 84.924
292 | 41.6111 | 0 | 0 | 279.7 | 0 | 20.8056 | 0 | 0 | 0 | 76.3 | 933.5 | 80.3045
293 | 38.678 | 0 | 0 | 285.5 | 0 | 19.339 | 0 | 0 | 0 | 77.8 | 949.4 | 92.6489
294 | 42.1758 | 0 | 0 | 289.6 | 0 | 21.0879 | 0 | 0 | 0 | 79.3 | 958.5 | 101.2625
295 | 49.4962 | 0 | 42.9 | 481.7 | 56.3 | 24.7481 | 0 | 0 | 0 | 97.6 | 1622.7 | 93.366
296 | 76.3448 | 0 | 42.9 | 521.3 | 37.6 | 38.1724 | 0 | 0 | 0 | 100 | 1557.2 | 131.4213
297 | 77.5504 | 0 | 42.9 | 513.2 | 0 | 38.7752 | 0 | 0 | 0 | 99.7 | 877.8 | 126.6583
298 | 71.3897 | 0 | 42.9 | 498 | 0 | 35.6949 | 0 | 0 | 0 | 95.7 | 906.8 | 126.0888
299 | 65.7947 | 0 | 42.9 | 450.9 | 0 | 32.8973 | 0 | 0 | 0 | 89.7 | 862.2 | 199.9632
300 | 63.1966 | 0 | 42.9 | 395.9 | 0 | 31.5983 | 0 | 0 | 0 | 83.7 | 811.4 | 151.1591
301 | 57.4401 | 0 | 42.9 | 352.2 | 75.1 | 28.7201 | 0 | 0 | 0 | 78.4 | 1393.2 | 134.1408
302 | 57.3211 | 0 | 42.9 | 310.2 | 37.6 | 28.6605 | 0 | 0 | 0 | 75.5 | 1227.8 | 191.5245
303 | 55.7489 | 0 | 42.9 | 301.3 | 0 | 27.8744 | 0 | 0 | 0 | 74.2 | 565.2 | 179.4996
304 | 60.6444 | 0 | 42.9 | 295.1 | 0 | 30.3222 | 0 | 0 | 0 | 75.4 | 626.2 | 207.2651
305 | 74.758 | 0 | 42.9 | 304 | 0 | 37.379 | 0 | 0 | 0 | 79.4 | 659.4 | 131.0668
306 | 76.959 | 0 | 42.9 | 328.8 | 37.6 | 38.4795 | 0 | 0 | 0 | 82.2 | 1297.5 | 182.7014
307 | 74.6907 | 0 | 42.9 | 288.6 | 75.1 | 37.3454 | 0 | 0 | 0 | 82.2 | 1252 | 165.1997
308 | 60.9038 | 0 | 42.9 | 249.1 | 75.1 | 30.4519 | 0 | 0 | 0 | 67.9 | 1138.3 | 268.651
309 | 46.772 | 0 | 42.9 | 259.3 | 75.1 | 23.386 | 0 | 0 | 0 | 71.4 | 1167.7 | 172.7261
310 | 42.2592 | 0 | 42.9 | 264.8 | 93.9 | 21.1296 | 0 | 0 | 0 | 73 | 1186.9 | 202.185
311 | 41.1518 | 0 | 0 | 150.6 | 0 | 20.5759 | 0 | 0 | 0 | 76 | 568.7 | 220.1843
312 | 40.2478 | 0 | 0 | 175.3 | 0 | 20.1239 | 0 | 0 | 0 | 77.9 | 649.8 | 148.5756
313 | 40.2586 | 0 | 0 | 188.9 | 0 | 20.1293 | 0 | 0 | 0 | 80 | 678 | 89.4263
314 | 42.3159 | 0 | 0 | 202.5 | 0 | 21.1579 | 0 | 0 | 0 | 82.8 | 708.9 | 83.8508
315 | 42.3497 | 0 | 0 | 215.3 | 0 | 21.1748 | 0 | 0 | 0 | 84.9 | 739.8 | 82.913
316 | 42.6391 | 0 | 0 | 226.1 | 0 | 21.3196 | 0 | 0 | 0 | 86.7 | 767.9 | 79.003
317 | 42.5003 | 0 | 0 | 234.5 | 0 | 21.2501 | 0 | 0 | 0 | 88.6 | 791.5 | 78.0447
318 | 41.1943 | 0 | 0 | 242.2 | 0 | 20.5971 | 0 | 0 | 0 | 90.6 | 810.9 | 112.3645
319 | 43.1152 | 0 | 42.9 | 432.7 | 56.3 | 21.5576 | 0 | 0 | 0 | 110.5 | 1474.1 | 133.1605
320 | 52.4336 | 0 | 42.9 | 443.3 | 37.6 | 26.2168 | 0 | 0 | 0 | 113.1 | 1416.5 | 161.4049
321 | 54.591 | 0 | 42.9 | 425.3 | 0 | 27.2955 | 0 | 0 | 0 | 111.7 | 757.9 | 174.3781
322 | 57.6041 | 0 | 42.9 | 413.6 | 0 | 28.802 | 0 | 0 | 0 | 100.7 | 814.1 | 130.142
323 | 52.5852 | 0 | 42.9 | 395.8 | 0 | 26.2926 | 0 | 0 | 0 | 86.7 | 805.4 | 269.4201
324 | 52.8464 | 0 | 42.9 | 381.7 | 0 | 26.4232 | 0 | 0 | 0 | 72.1 | 799 | 141.6408
325 | 49.0635 | 0 | 42.9 | 380.5 | 75.1 | 24.5318 | 0 | 0 | 0 | 61.1 | 1432.5 | 204.4364
326 | 49.8213 | 0 | 42.9 | 354.2 | 37.6 | 24.9106 | 0 | 0 | 0 | 50.5 | 1312.7 | 96.4648
327 | 49.8436 | 0 | 42.9 | 348.9 | 0 | 24.9218 | 0 | 0 | 0 | 46.1 | 659.1 | 150.8324
328 | 50.3156 | 0 | 42.9 | 350 | 0 | 25.1578 | 0 | 0 | 0 | 49.2 | 726.4 | 117.4141
329 | 57.2789 | 0 | 42.9 | 357.7 | 0 | 28.6395 | 0 | 0 | 0 | 59.7 | 750.8 | 153.1843
330 | 58.9814 | 0 | 42.9 | 381.1 | 37.6 | 29.4907 | 0 | 0 | 0 | 65 | 1394.6 | 319.1305
331 | 56.0315 | 0 | 42.9 | 362.1 | 75.1 | 28.0158 | 0 | 0 | 0 | 65.3 | 1354.3 | 216.2079
332 | 48.6625 | 0 | 42.9 | 317.3 | 75.1 | 24.3312 | 0 | 0 | 0 | 55 | 1258.5 | 327.8103
333 | 42.0611 | 0 | 42.9 | 332.5 | 75.1 | 21.0306 | 0 | 0 | 0 | 61.5 | 1303.6 | 259.8987
334 | 42.998 | 0 | 42.9 | 342.9 | 93.9 | 21.499 | 0 | 0 | 0 | 65 | 1341.3 | 422.8146
335 | 44.1987 | 0 | 0 | 225.2 | 0 | 22.0993 | 0 | 0 | 0 | 68.3 | 704.5 | 325.1185
336 | 42.5084 | 0 | 0 | 257.7 | 0 | 21.2542 | 0 | 0 | 0 | 71.5 | 803.4 | 144.9579
337 | 43.8931 | 0 | 0 | 270.3 | 0 | 21.9465 | 0 | 0 | 0 | 74.6 | 840.9 | 100.0679
338 | 42.9218 | 0 | 0 | 281.1 | 0 | 21.4609 | 0 | 0 | 0 | 78.1 | 875.4 | 91.2201
339 | 42.094 | 0 | 0 | 291.2 | 0 | 21.047 | 0 | 0 | 0 | 81.7 | 908.3 | 80.8997
340 | 42.4603 | 0 | 0 | 300.9 | 0 | 21.2302 | 0 | 0 | 0 | 85.3 | 939 | 78.5304
341 | 41.1977 | 0 | 0 | 309.5 | 0 | 20.5988 | 0 | 0 | 0 | 88.5 | 966 | 77.8042
342 | 42.0822 | 0 | 0 | 317.6 | 0 | 21.0411 | 0 | 0 | 0 | 91.2 | 986.6 | 100.4269
343 | 58.7077 | 0 | 42.9 | 533.1 | 56.3 | 29.3538 | 0 | 0 | 0 | 111.4 | 1676.9 | 129.8315
344 | 102.4849 | 0.7 | 43 | 607.4 | 37.6 | 51.2424 | 0 | 0 | 0 | 190.5 | 1616.9 | 217.9412
345 | 177.9941 | 2.1 | 43.2 | 594.3 | 0 | 88.997 | 0 | 0 | 0 | 207.9 | 910.9 | 166.1662
346 | 271.2411 | 3.5 | 43.4 | 597.7 | 0 | 135.6205 | 0 | 0 | 0 | 261.7 | 956.7 | 141.3524
347 | 275.1802 | 3.5 | 43.4 | 559.5 | 0 | 137.5901 | 0 | 0 | 0 | 257.5 | 929.2 | 126.0852
348 | 261.2919 | 2.8 | 43.3 | 516 | 0 | 130.646 | 0 | 0 | 0 | 209.7 | 906.6 | 176.6294
349 | 188.3325 | 1.4 | 43.1 | 477.6 | 75.1 | 94.1662 | 0 | 0 | 0 | 145 | 1565.7 | 421.3437
350 | 168.843 | 2.1 | 43.2 | 410.6 | 37.6 | 84.4215 | 0 | 0 | 0 | 152.8 | 1350.2 | 157.354
351 | 171.3236 | 3.5 | 43.4 | 400.2 | 0 | 85.6618 | 0 | 0 | 0 | 201.2 | 651.7 | 118.3852
352 | 205.3122 | 2.8 | 43.3 | 383.3 | 0 | 102.6561 | 0 | 0 | 0 | 202.8 | 708.9 | 113.923
353 | 210.4535 | 2.1 | 43.2 | 377.3 | 0 | 105.2267 | 0 | 0 | 0 | 171.2 | 741.5 | 146.5284
354 | 138.7675 | 0.7 | 43 | 393.7 | 37.6 | 69.3837 | 0 | 0 | 0 | 117.2 | 1392.4 | 141.757
355 | 75.6797 | 0 | 42.9 | 324.1 | 75.1 | 37.8398 | 0 | 0 | 0 | 56.5 | 1356.5 | 204.7636
356 | 51.6941 | 0 | 42.9 | 288.1 | 75.1 | 25.8471 | 0 | 0 | 0 | 54.2 | 1246.4 | 180.3403
357 | 47.1848 | 0 | 42.9 | 301.7 | 75.1 | 23.5924 | 0 | 0 | 0 | 61 | 1283.3 | 283.9771
358 | 41.6923 | 0 | 42.9 | 310.3 | 93.9 | 20.8462 | 0 | 0 | 0 | 65.6 | 1314.9 | 203.8388
359 | 43.236 | 0 | 0 | 192.6 | 0 | 21.618 | 0 | 0 | 0 | 69.5 | 683 | 167.9526
360 | 44.0462 | 0 | 0 | 221.5 | 0 | 22.0231 | 0 | 0 | 0 | 72.3 | 773.2 | 127.7544
361 | 44.5656 | 0 | 0 | 233.8 | 0 | 22.2828 | 0 | 0 | 0 | 74.7 | 798.4 | 96.3459
362 | 42.279 | 0 | 0 | 244.2 | 0 | 21.1395 | 0 | 0 | 0 | 77.5 | 822.3 | 82.7906
363 | 40.7375 | 0 | 0 | 253.5 | 0 | 20.3687 | 0 | 0 | 0 | 79.7 | 845.7 | 80.4248
364 | 43.4325 | 0 | 0 | 260.4 | 0 | 21.7163 | 0 | 0 | 0 | 80.6 | 866.3 | 79.8325
365 | 43.5863 | 0 | 0 | 265.6 | 0 | 21.7931 | 0 | 0 | 0 | 81.8 | 884.5 | 75.7923
366 | 41.9201 | 0 | 0 | 270.5 | 0 | 20.9601 | 0 | 0 | 0 | 84.2 | 897.7 | 81.0191
367 | 57.6949 | 0 | 42.9 | 466.8 | 56.3 | 28.8474 | 0 | 0 | 0 | 104.1 | 1571.1 | 111.8777
368 | 95.6777 | 0.7 | 43 | 535.9 | 37.6 | 47.8389 | 0 | 0 | 0 | 182.2 | 1506.4 | 149.6028
369 | 197.5279 | 2.1 | 43.2 | 528 | 0 | 98.7639 | 0 | 0 | 0 | 198.3 | 822.4 | 119.9033
370 | 263.5779 | 3.5 | 43.4 | 510.4 | 0 | 131.789 | 0 | 0 | 0 | 239.6 | 841.2 | 125.6517
371 | 234.8794 | 3.5 | 43.4 | 467.9 | 0 | 117.4397 | 0 | 0 | 0 | 214.5 | 801.3 | 112.1152
372 | 221.9061 | 2.8 | 43.3 | 415.3 | 0 | 110.953 | 0 | 0 | 0 | 154.1 | 761.9 | 138.3851
373 | 219.7936 | 1.4 | 43.1 | 368.4 | 75.1 | 109.8968 | 0 | 0 | 0 | 91.4 | 1354.3 | 246.5151
374 | 246.6029 | 2.1 | 43.2 | 354.3 | 37.6 | 123.3014 | 0 | 0 | 0 | 81.3 | 1232.1 | 158.6734
375 | 252.7375 | 3.5 | 43.4 | 371.5 | 0 | 126.3687 | 0 | 0 | 0 | 103.2 | 593.7 | 98.635
376 | 304.409 | 2.8 | 43.3 | 376.3 | 0 | 152.2045 | 0 | 0 | 0 | 104.4 | 672.8 | 102.3382
377 | 285.817 | 2.1 | 43.2 | 374.6 | 0 | 142.9085 | 0 | 0 | 0 | 91.8 | 707.3 | 126.3666
378 | 202.4848 | 0.7 | 43 | 379.2 | 37.6 | 101.2424 | 0 | 0 | 0 | 64.9 | 1350 | 121.2438
379 | 107.063 | 0 | 42.9 | 305.4 | 75.1 | 53.5315 | 0 | 0 | 0 | 9.4 | 1300.9 | 196.8305
380 | 70.6038 | 0 | 42.9 | 266.7 | 75.1 | 35.3019 | 0 | 0 | 0 | 6.9 | 1186.2 | 321.8523
381 | 46.0216 | 0 | 42.9 | 277.9 | 75.1 | 23.0108 | 0 | 0 | 0 | 10.1 | 1217 | 257.2437
382 | 40.2035 | 0 | 42.9 | 284.2 | 93.9 | 20.1017 | 0 | 0 | 0 | 15.1 | 1238.1 | 305.0305
383 | 39.8914 | 0 | 0 | 168.2 | 0 | 19.9457 | 0 | 0 | 0 | 21.9 | 605 | 357.9871
384 | 41.7903 | 0 | 0 | 194.6 | 0 | 20.8951 | 0 | 0 | 0 | 28.1 | 686.9 | 186.9279
385 | 42.0599 | 0 | 0 | 206.2 | 0 | 21.0299 | 0 | 0 | 0 | 34.1 | 712.5 | 108.2472
386 | 41.6201 | 0 | 0 | 216.8 | 0 | 20.8101 | 0 | 0 | 0 | 39.9 | 737.5 | 83.7352
387 | 43.162 | 0 | 0 | 225.8 | 0 | 21.581 | 0 | 0 | 0 | 45.2 | 760.9 | 77.5653
388 | 44.0381 | 0 | 0 | 232.9 | 0 | 22.0191 | 0 | 0 | 0 | 49.2 | 781.6 | 77.2083
389 | 40.112 | 0 | 0 | 239.3 | 0 | 20.056 | 0 | 0 | 0 | 52.1 | 802.1 | 77.685
390 | 42.6689 | 0 | 0 | 245 | 0 | 21.3344 | 0 | 0 | 0 | 54.6 | 816.4 | 88.481
391 | 57.6298 | 0 | 42.9 | 438 | 56.3 | 28.8149 | 0 | 0 | 0 | 70.3 | 1481.1 | 101.5
392 | 103.7791 | 0.7 | 43 | 503.9 | 37.6 | 51.8895 | 0 | 0 | 0 | 138.1 | 1417.5 | 122.9201
393 | 178.9713 | 2.1 | 43.2 | 498.2 | 0 | 89.4856 | 0 | 0 | 0 | 156.9 | 749.7 | 202.3222
394 | 285.6509 | 3.5 | 43.4 | 485 | 0 | 142.8255 | 0 | 0 | 0 | 191.9 | 773.7 | 131.5151
395 | 290.9952 | 3.5 | 43.4 | 436.7 | 0 | 145.4976 | 0 | 0 | 0 | 166.7 | 727.6 | 114.4069
396 | 281.5847 | 2.8 | 43.3 | 383.8 | 0 | 140.7924 | 0 | 0 | 0 | 114 | 685.3 | 100.665
397 | 287.5975 | 1.4 | 43.1 | 338 | 75.1 | 143.7988 | 0 | 0 | 0 | 61.9 | 1258.3 | 159.333
398 | 264.7665 | 2.1 | 43.2 | 317.1 | 37.6 | 132.3832 | 0 | 0 | 0 | 53.7 | 1132 | 270.9789
399 | 222.2321 | 3.5 | 43.4 | 318.8 | 0 | 111.116 | 0 | 0 | 0 | 73.5 | 496.1 | 191.8341
400 | 242.674 | 2.8 | 43.3 | 309 | 0 | 121.337 | 0 | 0 | 0 | 73.8 | 553.5 | 180.2916
401 | 312.7487 | 2.1 | 43.2 | 304.8 | 0 | 156.3743 | 0 | 0 | 0 | 64.8 | 580.4 | 148.4999
402 | 214.2792 | 0.7 | 43 | 319.3 | 37.6 | 107.1396 | 0 | 0 | 0 | 47.3 | 1200.1 | 172.1185
403 | 115.1381 | 0 | 42.9 | 256.9 | 75.1 | 57.569 | 0 | 0 | 0 | 2.2 | 1150.1 | 296.8347
404 | 70.5672 | 0 | 42.9 | 222.2 | 75.1 | 35.2836 | 0 | 0 | 0 | 0.1 | 1038.8 | 249.6121
405 | 47.3723 | 0 | 42.9 | 233.2 | 75.1 | 23.6861 | 0 | 0 | 0 | 1.8 | 1070.2 | 171.3607
406 | 42.2902 | 0 | 42.9 | 239.9 | 93.9 | 21.1451 | 0 | 0 | 0 | 3.8 | 1090.4 | 215.1062
407 | 41.666 | 0 | 0 | 126.9 | 0 | 20.833 | 0 | 0 | 0 | 5.6 | 491.9 | 307.7262
408 | 40.929 | 0 | 0 | 152 | 0 | 20.4645 | 0 | 0 | 0 | 7.4 | 574.8 | 175.1031
409 | 41.0818 | 0 | 0 | 162.6 | 0 | 20.5409 | 0 | 0 | 0 | 10.5 | 593 | 97.3131
410 | 41.8656 | 0 | 0 | 171.6 | 0 | 20.9328 | 0 | 0 | 0 | 14 | 610.3 | 81.0186
411 | 40.1229 | 0 | 0 | 179.7 | 0 | 20.0614 | 0 | 0 | 0 | 18.1 | 627.7 | 77.2055
412 | 42.4324 | 0 | 0 | 186.1 | 0 | 21.2162 | 0 | 0 | 0 | 21.2 | 642.9 | 78.41
413 | 40.5871 | 0 | 0 | 191.3 | 0 | 20.2936 | 0 | 0 | 0 | 23.9 | 656.6 | 75.6734
414 | 39.7993 | 0 | 0 | 195.7 | 0 | 19.8997 | 0 | 0 | 0 | 27.4 | 665.4 | 141.5313
415 | 57.8585 | 0 | 42.9 | 374.9 | 56.3 | 28.9293 | 0 | 0 | 0 | 43.3 | 1301.8 | 119.305
416 | 85.7267 | 0.7 | 43 | 433.7 | 37.6 | 42.8634 | 0 | 0 | 0 | 99.9 | 1244.1 | 110.177
417 | 149.673 | 2.1 | 43.2 | 429.9 | 0 | 74.8365 | 0 | 0 | 0 | 117.4 | 608 | 154.8654
418 | 222.1026 | 3.5 | 43.4 | 438.6 | 0 | 111.0513 | 0 | 0 | 0 | 154.6 | 660.6 | 119.3801
419 | 280.4027 | 3.5 | 43.4 | 420.2 | 0 | 140.2013 | 0 | 0 | 0 | 155.4 | 652.7 | 132.8932
420 | 285.7668 | 2.8 | 43.3 | 394.4 | 0 | 142.8834 | 0 | 0 | 0 | 129.1 | 645.4 | 125.8718
421 | 275.0007 | 1.4 | 43.1 | 366.7 | 75.1 | 137.5004 | 0 | 0 | 0 | 91 | 1248.5 | 146.5675
422 | 244.566 | 2.1 | 43.2 | 304.6 | 37.6 | 122.283 | 0 | 0 | 0 | 94.6 | 1067.9 | 181.7337
423 | 242.1366 | 3.5 | 43.4 | 266.6 | 0 | 121.0683 | 0 | 0 | 0 | 124.7 | 400.3 | 257.4984
424 | 311.6869 | 2.8 | 43.3 | 240.6 | 0 | 155.8434 | 0 | 0 | 0 | 124.6 | 434.2 | 117.7802
425 | 313.7491 | 2.1 | 43.2 | 234.1 | 0 | 156.8746 | 0 | 0 | 0 | 104.4 | 449.2 | 232.2319
426 | 220.6608 | 0.7 | 43 | 251.9 | 37.6 | 110.3304 | 0 | 0 | 0 | 66.2 | 1027.5 | 186.8257
427 | 114.7215 | 0 | 42.9 | 199.7 | 75.1 | 57.3608 | 0 | 0 | 0 | 14.8 | 971.7 | 167.6831
428 | 76.672 | 0 | 42.9 | 165.4 | 75.1 | 38.336 | 0 | 0 | 0 | 7.6 | 864.4 | 206.8037
429 | 54.7692 | 0 | 42.9 | 178.5 | 75.1 | 27.3846 | 0 | 0 | 0 | 13.6 | 898 | 283.7257
430 | 43.7397 | 0 | 42.9 | 186.6 | 93.9 | 21.8698 | 0 | 0 | 0 | 17.2 | 914.3 | 208.3155
431 | 40.4796 | 0 | 0 | 75.1 | 0 | 20.2398 | 0 | 0 | 0 | 20.1 | 355.8 | 171.5478
432 | 42.0125 | 0 | 0 | 99.3 | 0 | 21.0062 | 0 | 0 | 0 | 22.8 | 437.3 | 153.2883
433 | 43.4471 | 0 | 0 | 112.6 | 0 | 21.7236 | 0 | 0 | 0 | 25.5 | 459.7 | 196.2312
434 | 42.658 | 0 | 0 | 124.6 | 0 | 21.329 | 0 | 0 | 0 | 27.3 | 480.3 | 104.7394
435 | 40.6668 | 0 | 0 | 135.3 | 0 | 20.3334 | 0 | 0 | 0 | 28.6 | 499.7 | 75.795
436 | 42.1653 | 0 | 0 | 143.8 | 0 | 21.0826 | 0 | 0 | 0 | 29.8 | 516.6 | 77.0896
437 | 41.097 | 0 | 0 | 150.7 | 0 | 20.5485 | 0 | 0 | 0 | 31.2 | 531.8 | 78.6508
438 | 41.339 | 0 | 0 | 157.7 | 0 | 20.6695 | 0 | 0 | 0 | 32.3 | 544.1 | 85.3958
439 | 61.916 | 0 | 42.9 | 333.3 | 56.3 | 30.958 | 0 | 0 | 0 | 44.9 | 1157.7 | 112.604
440 | 100.9718 | 0.7 | 43 | 385.3 | 37.6 | 50.4859 | 0 | 0 | 0 | 103 | 1109.1 | 161.221
441 | 161.6484 | 2.1 | 43.2 | 378.7 | 0 | 80.8242 | 0 | 0 | 0 | 114.7 | 498.9 | 141.3332
442 | 231.7817 | 3.5 | 43.4 | 352.8 | 0 | 115.8909 | 0 | 0 | 0 | 146.3 | 519.2 | 134.7936
443 | 236.7572 | 3.5 | 43.4 | 276.9 | 0 | 118.3786 | 0 | 0 | 0 | 141.1 | 455.2 | 125.2269
444 | 223.293 | 2.8 | 43.3 | 199.4 | 0 | 111.6465 | 0 | 0 | 0 | 114.2 | 380.3 | 269.3145
445 | 225.8951 | 1.4 | 43.1 | 185.2 | 75.1 | 112.9475 | 0 | 0 | 0 | 79.6 | 877.6 | 148.8283
446 | 223.3162 | 2.1 | 43.2 | 201.4 | 37.6 | 111.6581 | 0 | 0 | 0 | 79.9 | 835 | 98.0377
447 | 226.5044 | 3.5 | 43.4 | 217.2 | 0 | 113.2522 | 0 | 0 | 0 | 102 | 301.2 | 157.4188
448 | 271.0173 | 2.8 | 43.3 | 226.8 | 0 | 135.5087 | 0 | 0 | 0 | 101.2 | 374.2 | 117.633
449 | 303.6983 | 2.1 | 43.2 | 231.8 | 0 | 151.8492 | 0 | 0 | 0 | 87 | 401.6 | 222.3283
450 | 224.6207 | 0.7 | 43 | 240.6 | 37.6 | 112.3103 | 0 | 0 | 0 | 56.2 | 950.9 | 220.4597
451 | 128.3547 | 0 | 42.9 | 188 | 75.1 | 64.1774 | 0 | 0 | 0 | 8.8 | 902.3 | 259.3284
452 | 69.2934 | 0 | 42.9 | 153.4 | 75.1 | 34.6467 | 0 | 0 | 0 | 3.2 | 800.9 | 277.2676
453 | 48.2918 | 0 | 42.9 | 165.5 | 75.1 | 24.1459 | 0 | 0 | 0 | 7.1 | 836.9 | 339.7425
454 | 41.8687 | 0 | 42.9 | 172.6 | 93.9 | 20.9343 | 0 | 0 | 0 | 11.3 | 853.1 | 235.9724
455 | 40.1691 | 0 | 0 | 60.7 | 0 | 20.0845 | 0 | 0 | 0 | 15.1 | 311.7 | 184.3985
456 | 43.2001 | 0 | 0 | 84.8 | 0 | 21.6 | 0 | 0 | 0 | 18.6 | 391.8 | 168.6764
457 | 43.9535 | 0 | 0 | 97.9 | 0 | 21.9768 | 0 | 0 | 0 | 21.8 | 414.3 | 130.1727
458 | 42.7864 | 0 | 0 | 109.4 | 0 | 21.3932 | 0 | 0 | 0 | 25.1 | 434.8 | 98.7534
459 | 44.1993 | 0 | 0 | 119.2 | 0 | 22.0996 | 0 | 0 | 0 | 28.1 | 452.7 | 95.7533
460 | 41.4806 | 0 | 0 | 127.2 | 0 | 20.7403 | 0 | 0 | 0 | 30.4 | 466.9 | 104.1336
461 | 40.818 | 0 | 0 | 134.1 | 0 | 20.409 | 0 | 0 | 0 | 32.3 | 479.5 | 86.222
462 | 42.6986 | 0 | 0 | 141.2 | 0 | 21.3493 | 0 | 0 | 0 | 34.3 | 490.6 | 91.9371
463 | 47.0534 | 0 | 42.9 | 312.1 | 56.3 | 23.5267 | 0 | 0 | 0 | 47.3 | 1085.4 | 92.5306
464 | 64.3154 | 0 | 42.9 | 335.3 | 37.6 | 32.1577 | 0 | 0 | 0 | 49.1 | 1042.5 | 110.296
465 | 74.1164 | 0 | 42.9 | 328.7 | 0 | 37.0582 | 0 | 0 | 0 | 48.2 | 452.5 | 107.7615
466 | 73.3884 | 0 | 42.9 | 336.2 | 0 | 36.6942 | 0 | 0 | 0 | 37.4 | 518.4 | 252.7223
467 | 69.4295 | 0 | 42.9 | 313.1 | 0 | 34.7147 | 0 | 0 | 0 | 27.7 | 505.4 | 192.4072
468 | 62.1608 | 0 | 42.9 | 285.7 | 0 | 31.0804 | 0 | 0 | 0 | 19.2 | 487.1 | 180.426
469 | 59.1868 | 0 | 42.9 | 273 | 75.1 | 29.5934 | 0 | 0 | 0 | 20.2 | 1039.7 | 173.5315
470 | 57.5142 | 0 | 42.9 | 261.4 | 37.6 | 28.7571 | 0 | 0 | 0 | 22.6 | 958.6 | 172.4209
471 | 63.8911 | 0 | 42.9 | 262.8 | 0 | 31.9456 | 0 | 0 | 0 | 22.3 | 379.2 | 143.5721
472 | 68.9856 | 0 | 42.9 | 258.3 | 0 | 34.4928 | 0 | 0 | 0 | 21.2 | 440.4 | 120.4453
473 | 71.5301 | 0 | 42.9 | 259.1 | 0 | 35.7651 | 0 | 0 | 0 | 27.9 | 458.2 | 124.6999
474 | 73.7879 | 0 | 42.9 | 270.4 | 37.6 | 36.8939 | 0 | 0 | 0 | 32.7 | 1039.1 | 176.1011
475 | 68.4061 | 0 | 42.9 | 232.2 | 75.1 | 34.203 | 0 | 0 | 0 | 32.5 | 981.5 | 281.1273
476 | 61.9569 | 0 | 42.9 | 192.4 | 75.1 | 30.9785 | 0 | 0 | 0 | 20.7 | 881.6 | 319.6055
477 | 49.216 | 0 | 42.9 | 205.4 | 75.1 | 24.608 | 0 | 0 | 0 | 24.3 | 923.2 | 293.5098
478 | 42.4981 | 0 | 42.9 | 213.1 | 93.9 | 21.2491 | 0 | 0 | 0 | 25.8 | 946.7 | 334.8551
479 | 41.1899 | 0 | 0 | 107.9 | 0 | 20.595 | 0 | 0 | 0 | 26.9 | 386 | 174.9941
480 | 40.9646 | 0 | 0 | 133.8 | 0 | 20.4823 | 0 | 0 | 0 | 27.8 | 471.3 | 176.127
481 | 43.3544 | 0 | 0 | 144.4 | 0 | 21.6772 | 0 | 0 | 0 | 29 | 495 | 126.6347
482 | 42.8753 | 0 | 0 | 154.7 | 0 | 21.4376 | 0 | 0 | 0 | 30 | 518.3 | 93.0034
483 | 39.861 | 0 | 0 | 164 | 0 | 19.9305 | 0 | 0 | 0 | 30.8 | 540.1 | 81.6099
484 | 41.7503 | 0 | 0 | 171 | 0 | 20.8751 | 0 | 0 | 0 | 31.7 | 558.6 | 80.7798
485 | 42.2096 | 0 | 0 | 177.4 | 0 | 21.1048 | 0 | 0 | 0 | 32.6 | 576.8 | 77.2045
486 | 43.9563 | 0 | 0 | 182.8 | 0 | 21.9782 | 0 | 0 | 0 | 33.3 | 589.6 | 80.663
487 | 57.3347 | 0 | 42.9 | 359.4 | 56.3 | 28.6674 | 0 | 0 | 0 | 46.2 | 1208.8 | 98.7527
488 | 75.5978 | 0 | 42.9 | 363.4 | 37.6 | 37.7989 | 0 | 0 | 0 | 46.7 | 1161.6 | 155.0042
489 | 82.1493 | 0 | 42.9 | 338.4 | 0 | 41.0746 | 0 | 0 | 0 | 46.6 | 537.4 | 195.7651
490 | 74.0039 | 0 | 42.9 | 285 | 0 | 37.002 | 0 | 0 | 0 | 45.4 | 532.9 | 172.0274
491 | 70.3459 | 0 | 42.9 | 218.6 | 0 | 35.1729 | 0 | 0 | 0 | 43.1 | 459.9 | 194.8181
492 | 67.6195 | 0 | 42.9 | 157.4 | 0 | 33.8098 | 0 | 0 | 0 | 40.8 | 387.7 | 109.8163
493 | 65.0809 | 0 | 42.9 | 112.5 | 75.1 | 32.5405 | 0 | 0 | 0 | 39.2 | 826.7 | 173.9781
494 | 64.7843 | 0 | 42.9 | 73.3 | 37.6 | 32.3922 | 0 | 0 | 0 | 38.1 | 693.2 | 303.1934
495 | 69.5745 | 0 | 42.9 | 54.7 | 0 | 34.7873 | 0 | 0 | 0 | 37.8 | 151.9 | 117.4027
496 | 78.221 | 0 | 42.9 | 56.8 | 0 | 39.1105 | 0 | 0 | 0 | 38.3 | 201.3 | 116.7273
497 | 82.0542 | 0 | 42.9 | 78.5 | 0 | 41.0271 | 0 | 0 | 0 | 39.2 | 237.8 | 110.0561
498 | 79.2277 | 0 | 42.9 | 122.2 | 37.6 | 39.6138 | 0 | 0 | 0 | 40.5 | 768.2 | 162.566
499 | 74.4242 | 0 | 42.9 | 130.3 | 75.1 | 37.2121 | 0 | 0 | 0 | 39.6 | 707.8 | 168.8198
500 | 63.0116 | 0 | 42.9 | 91.5 | 75.1 | 31.5058 | 0 | 0 | 0 | 27.8 | 617.9 | 270.8667
501 | 51.2531 | 0 | 42.9 | 108.7 | 75.1 | 25.6266 | 0 | 0 | 0 | 30.5 | 662.2 | 171.5941
502 | 42.7805 | 0 | 42.9 | 119.9 | 93.9 | 21.3902 | 0 | 0 | 0 | 30.6 | 681.4 | 184.8492
503 | 44.0713 | 0 | 0 | 13.3 | 0 | 22.0356 | 0 | 0 | 0 | 31.4 | 187 | 186.9391
504 | 42.8669 | 0 | 0 | 34.5 | 0 | 21.4335 | 0 | 0 | 0 | 32.2 | 265.6 | 175.4775
505 | 41.4791 | 0 | 0 | 51.6 | 0 | 20.7395 | 0 | 0 | 0 | 33.2 | 291.8 | 113.8026
506 | 40.3848 | 0 | 0 | 65.7 | 0 | 20.1924 | 0 | 0 | 0 | 34.2 | 314.4 | 98.3959
507 | 40.3888 | 0 | 0 | 78.4 | 0 | 20.1944 | 0 | 0 | 0 | 35.4 | 336.8 | 97.6768
508 | 44.7048 | 0 | 0 | 88.6 | 0 | 22.3524 | 0 | 0 | 0 | 36.3 | 355.6 | 96.4655
509 | 39.098 | 0 | 0 | 97.6 | 0 | 19.549 | 0 | 0 | 0 | 36.8 | 373 | 114.5356
510 | 43.2584 | 0 | 0 | 105.3 | 0 | 21.6292 | 0 | 0 | 0 | 37.5 | 383.8 | 100.1904
511 | 54.0967 | 0 | 42.9 | 270.5 | 56.3 | 27.0483 | 0 | 0 | 0 | 51.9 | 931.1 | 148.5089
512 | 105.4009 | 0.7 | 43 | 316.1 | 37.6 | 52.7005 | 0 | 0 | 0 | 113.2 | 897.7 | 169.2077
513 | 216.4787 | 2.1 | 43.2 | 309.3 | 0 | 108.2393 | 0 | 0 | 0 | 116.9 | 349.7 | 142.4287
514 | 344.3679 | 3.5 | 43.4 | 308.7 | 0 | 172.184 | 0 | 0 | 0 | 137.4 | 399.7 | 245.9799
515 | 386.7712 | 3.5 | 43.4 | 296.5 | 0 | 193.3856 | 0 | 0 | 0 | 124.1 | 397.4 | 228.9908
516 | 347.6776 | 2.8 | 43.3 | 284.1 | 0 | 173.8388 | 0 | 0 | 0 | 94.4 | 401.6 | 243.3615
517 | 305.4655 | 1.4 | 43.1 | 269.3 | 75.1 | 152.7328 | 0 | 0 | 0 | 60.6 | 934.3 | 336.2403
518 | 277.3307 | 2.1 | 43.2 | 247.1 | 37.6 | 138.6654 | 0 | 0 | 0 | 55.2 | 844.1 | 269.2478
519 | 315.9198 | 3.5 | 43.4 | 222.3 | 0 | 157.9599 | 0 | 0 | 0 | 66.9 | 265.1 | 116.2388
520 | 308.5688 | 2.8 | 43.3 | 189.1 | 0 | 154.2844 | 0 | 0 | 0 | 66 | 292.2 | 166.7792
521 | 239.7511 | 2.1 | 43.2 | 176.8 | 0 | 119.8755 | 0 | 0 | 0 | 58.1 | 298.8 | 222.1251
522 | 137.6 | 0.7 | 43 | 188 | 37.6 | 68.8 | 0 | 0 | 0 | 43 | 807.5 | 239.4763
523 | 87.1136 | 0 | 42.9 | 148 | 75.1 | 43.5568 | 0 | 0 | 0 | 1.6 | 764.2 | 311.6898
524 | 55.5589 | 0 | 42.9 | 121.3 | 75.1 | 27.7794 | 0 | 0 | 0 | 0 | 682.3 | 477.7985
525 | 43.8943 | 0 | 42.9 | 139.6 | 75.1 | 21.9472 | 0 | 0 | 0 | 0.9 | 734.6 | 311.4291
526 | 43.908 | 0 | 42.9 | 153.2 | 93.9 | 21.954 | 0 | 0 | 0 | 2.1 | 765.6 | 287.2438
527 | 40.9761 | 0 | 0 | 48.7 | 0 | 20.488 | 0 | 0 | 0 | 3.2 | 259 | 199.9926
528 | 38.8104 | 0 | 0 | 78.3 | 0 | 19.4052 | 0 | 0 | 0 | 5.3 | 352.5 | 166.5052
529 | 42.2505 | 0 | 0 | 97.3 | 0 | 21.1252 | 0 | 0 | 0 | 9.3 | 390.3 | 139.5575
530 | 41.1224 | 0 | 0 | 115.4 | 0 | 20.5612 | 0 | 0 | 0 | 13.3 | 428.5 | 117.2025
531 | 42.1216 | 0 | 0 | 131.8 | 0 | 21.0608 | 0 | 0 | 0 | 16.3 | 464.4 | 101.5008
532 | 41.7661 | 0 | 0 | 145.3 | 0 | 20.883 | 0 | 0 | 0 | 18.9 | 494.4 | 91.0975
533 | 41.092 | 0 | 0 | 156.5 | 0 | 20.546 | 0 | 0 | 0 | 21.5 | 519.4 | 93.6043
534 | 43.1874 | 0 | 0 | 167 | 0 | 21.5937 | 0 | 0 | 0 | 23.9 | 538.9 | 133.3826
535 | 60.702 | 0 | 42.9 | 342.4 | 56.3 | 30.351 | 0 | 0 | 0 | 37.6 | 1125.8 | 151.0983
536 | 105.0117 | 0.7 | 43 | 400.5 | 37.6 | 52.5058 | 0 | 0 | 0 | 92.6 | 1096.5 | 183.6602
537 | 218.8189 | 2.1 | 43.2 | 395 | 0 | 109.4095 | 0 | 0 | 0 | 106.8 | 503.8 | 312.8561
538 | 314.1238 | 3.5 | 43.4 | 369 | 0 | 157.0619 | 0 | 0 | 0 | 136.8 | 521.6 | 241.1416
539 | 372.5628 | 3.5 | 43.4 | 316.4 | 0 | 186.2814 | 0 | 0 | 0 | 137.4 | 477.6 | 154.198
540 | 335.0244 | 2.8 | 43.3 | 267.5 | 0 | 167.5122 | 0 | 0 | 0 | 115.1 | 438.6 | 193.118
541 | 313.7339 | 1.4 | 43.1 | 224.7 | 75.1 | 156.867 | 0 | 0 | 0 | 81.9 | 919.3 | 183.2754
542 | 283.0243 | 2.1 | 43.2 | 198.5 | 37.6 | 141.5122 | 0 | 0 | 0 | 84.7 | 806 | 168.1796
543 | 249.0655 | 3.5 | 43.4 | 196.1 | 0 | 124.5327 | 0 | 0 | 0 | 111.2 | 261.2 | 154.9798
544 | 276.0718 | 2.8 | 43.3 | 192.7 | 0 | 138.0359 | 0 | 0 | 0 | 110 | 321.6 | 126.3106
545 | 282.0784 | 2.1 | 43.2 | 201.4 | 0 | 141.0392 | 0 | 0 | 0 | 91.1 | 355.7 | 161.2271
546 | 229.0079 | 0.7 | 43 | 222.6 | 37.6 | 114.504 | 0 | 0 | 0 | 56.9 | 893.7 | 170.8824
547 | 133.9739 | 0 | 42.9 | 179.5 | 75.1 | 66.987 | 0 | 0 | 0 | 8.3 | 859.2 | 273.3154
548 | 70.4649 | 0 | 42.9 | 153.6 | 75.1 | 35.2325 | 0 | 0 | 0 | 3.1 | 790.6 | 223.2948
549 | 43.6383 | 0 | 42.9 | 179.5 | 75.1 | 21.8192 | 0 | 0 | 0 | 7.3 | 858 | 256.4043
550 | 42.4253 | 0 | 42.9 | 199.9 | 93.9 | 21.2126 | 0 | 0 | 0 | 12.5 | 911.2 | 190.0528
551 | 42.125 | 0 | 0 | 89.9 | 0 | 21.0625 | 0 | 0 | 0 | 17.3 | 396.8 | 180.5606
552 | 39.5849 | 0 | 0 | 127.8 | 0 | 19.7924 | 0 | 0 | 0 | 21.7 | 509.3 | 149.5742
553 | 41.7391 | 0 | 0 | 151.7 | 0 | 20.8696 | 0 | 0 | 0 | 26.6 | 556 | 97.9142
554 | 41.9173 | 0 | 0 | 173.9 | 0 | 20.9587 | 0 | 0 | 0 | 30.8 | 602.7 | 78.528
555 | 45.1622 | 0 | 0 | 194.2 | 0 | 22.5811 | 0 | 0 | 0 | 34.3 | 647.8 | 80.1877
556 | 41.5798 | 0 | 0 | 210.5 | 0 | 20.7899 | 0 | 0 | 0 | 37.4 | 683.8 | 84.6838
557 | 40.5255 | 0 | 0 | 223.9 | 0 | 20.2627 | 0 | 0 | 0 | 40.4 | 713.5 | 95.034
558 | 42.7377 | 0 | 0 | 237.2 | 0 | 21.3688 | 0 | 0 | 0 | 43.3 | 740.2 | 96.3473
559 | 68.3001 | 0 | 42.9 | 426.4 | 56.3 | 34.1501 | 0 | 0 | 0 | 57.9 | 1357.9 | 142.2926
560 | 121.18 | 0.7 | 43 | 497.4 | 37.6 | 60.59 | 0 | 0 | 0 | 121.4 | 1325.5 | 148.569
561 | 213.2695 | 2.1 | 43.2 | 493.5 | 0 | 106.6347 | 0 | 0 | 0 | 140.6 | 699.5 | 206.5205
562 | 308.8871 | 3.5 | 43.4 | 466 | 0 | 154.4435 | 0 | 0 | 0 | 190.8 | 705.9 | 152.595
563 | 324.6593 | 3.5 | 43.4 | 397.6 | 0 | 162.3297 | 0 | 0 | 0 | 197.5 | 645.8 | 225.5466
564 | 333.2752 | 2.8 | 43.3 | 326.8 | 0 | 166.6376 | 0 | 0 | 0 | 167.5 | 587.5 | 198.9424
565 | 294.5491 | 1.4 | 43.1 | 264.9 | 75.1 | 147.2746 | 0 | 0 | 0 | 119.1 | 1081.4 | 166.2409
566 | 256.1841 | 2.1 | 43.2 | 232.1 | 37.6 | 128.0921 | 0 | 0 | 0 | 129.9 | 937.5 | 212.0035
567 | 250.0529 | 3.5 | 43.4 | 229.8 | 0 | 125.0265 | 0 | 0 | 0 | 173 | 362.2 | 149.8575
568 | 247.2512 | 2.8 | 43.3 | 226.9 | 0 | 123.6256 | 0 | 0 | 0 | 172.6 | 430.9 | 181.7637
569 | 304.4496 | 2.1 | 43.2 | 235 | 0 | 152.2248 | 0 | 0 | 0 | 141.7 | 471.6 | 149.0348
570 | 256.6375 | 0.7 | 43 | 267.4 | 37.6 | 128.3188 | 0 | 0 | 0 | 89.4 | 1039.5 | 205.0667
571 | 152.3827 | 0 | 42.9 | 214.7 | 75.1 | 76.1913 | 0 | 0 | 0 | 33.1 | 1010.7 | 489.416
572 | 92.0882 | 0 | 42.9 | 182.3 | 75.1 | 46.0441 | 0 | 0 | 0 | 28.8 | 926.5 | 296.3389
573 | 60.3757 | 0 | 42.9 | 205.6 | 75.1 | 30.1878 | 0 | 0 | 0 | 35.4 | 981 | 234.5501
574 | 42.9376 | 0 | 42.9 | 223.6 | 93.9 | 21.4688 | 0 | 0 | 0 | 39.6 | 1027.3 | 178.14
575 | 42.0137 | 0 | 0 | 102.6 | 0 | 21.0069 | 0 | 0 | 0 | 43.9 | 482.2 | 159.5704
576 | 41.4314 | 0 | 0 | 138.7 | 0 | 20.7157 | 0 | 0 | 0 | 47 | 585.2 | 132.8386
577 | 42.0754 | 0 | 0 | 158.7 | 0 | 21.0377 | 0 | 0 | 0 | 49.6 | 617.2 | 100.4277
578 | 40.598 | 0 | 0 | 174.8 | 0 | 20.299 | 0 | 0 | 0 | 50.7 | 643.8 | 84.8084
579 | 43.4254 | 0 | 0 | 188.7 | 0 | 21.7127 | 0 | 0 | 0 | 52.5 | 668.5 | 81.4872
580 | 40.9172 | 0 | 0 | 199.5 | 0 | 20.4586 | 0 | 0 | 0 | 53.2 | 687 | 77.0873
581 | 40.2413 | 0 | 0 | 209.1 | 0 | 20.1206 | 0 | 0 | 0 | 53.4 | 704.5 | 78.6455
582 | 40.148 | 0 | 0 | 218.2 | 0 | 20.074 | 0 | 0 | 0 | 54.7 | 719.4 | 88.1222
583 | 48.1592 | 0 | 42.9 | 401.8 | 56.3 | 24.0796 | 0 | 0 | 0 | 70 | 1333.8 | 99.5943
584 | 77.4893 | 0.7 | 43 | 465 | 37.6 | 38.7447 | 0 | 0 | 0 | 137.6 | 1290.7 | 181.3833
585 | 158.0416 | 2.1 | 43.2 | 460.6 | 0 | 79.0208 | 0 | 0 | 0 | 152.3 | 662 | 178.6245
586 | 289.0935 | 3.5 | 43.4 | 449.4 | 0 | 144.5468 | 0 | 0 | 0 | 200.6 | 686.6 | 229.7152
587 | 338.6108 | 3.5 | 43.4 | 405.1 | 0 | 169.3054 | 0 | 0 | 0 | 201.6 | 644.9 | 116.4033
588 | 301.8921 | 2.8 | 43.3 | 354.9 | 0 | 150.946 | 0 | 0 | 0 | 169 | 606.3 | 191.8565
589 | 272.8015 | 1.4 | 43.1 | 308.6 | 75.1 | 136.4008 | 0 | 0 | 0 | 119.3 | 1148.1 | 219.8283
590 | 246.526 | 2.1 | 43.2 | 286.5 | 37.6 | 123.263 | 0 | 0 | 0 | 126.8 | 1027.8 | 241.3156
591 | 264.019 | 3.5 | 43.4 | 287.2 | 0 | 132.0095 | 0 | 0 | 0 | 163 | 428.2 | 174.7733
592 | 275.0184 | 2.8 | 43.3 | 283 | 0 | 137.5092 | 0 | 0 | 0 | 160.1 | 491.6 | 156.1288
593 | 262.5738 | 2.1 | 43.2 | 284.5 | 0 | 131.2869 | 0 | 0 | 0 | 133.3 | 520.9 | 190.5249
594 | 144.6569 | 0.7 | 43 | 300.7 | 37.6 | 72.3285 | 0 | 0 | 0 | 86.1 | 1112.6 | 314.5243
595 | 90.4871 | 0 | 42.9 | 242.7 | 75.1 | 45.2436 | 0 | 0 | 0 | 30.8 | 1075.9 | 321.0475
596 | 52.6534 | 0 | 42.9 | 209.6 | 75.1 | 26.3267 | 0 | 0 | 0 | 25.8 | 974.5 | 204.9423
597 | 44.5916 | 0 | 42.9 | 222.9 | 75.1 | 22.2958 | 0 | 0 | 0 | 31.1 | 1014.2 | 230.1985
598 | 41.2113 | 0 | 42.9 | 231 | 93.9 | 20.6057 | 0 | 0 | 0 | 34.6 | 1040.6 | 293.3499
599 | 41.5027 | 0 | 0 | 118 | 0 | 20.7513 | 0 | 0 | 0 | 37.4 | 466 | 166.1908
600 | 40.9284 | 0 | 0 | 144.5 | 0 | 20.4642 | 0 | 0 | 0 | 40.1 | 556.4 | 146.8107
601 | 43.6238 | 0 | 0 | 157.8 | 0 | 21.8119 | 0 | 0 | 0 | 42.4 | 580.7 | 113.2046
602 | 44.1525 | 0 | 0 | 168.9 | 0 | 22.0762 | 0 | 0 | 0 | 45 | 601 | 98.5173
603 | 41.5488 | 0 | 0 | 179 | 0 | 20.7744 | 0 | 0 | 0 | 48.2 | 620.5 | 95.6324
604 | 42.2939 | 0 | 0 | 188.4 | 0 | 21.1469 | 0 | 0 | 0 | 50.9 | 641.7 | 80.3029
605 | 39.5219 | 0 | 0 | 196.2 | 0 | 19.761 | 0 | 0 | 0 | 51.8 | 661.1 | 80.4217
606 | 43.2581 | 0 | 0 | 203 | 0 | 21.629 | 0 | 0 | 0 | 52.8 | 674.7 | 91.2188
607 | 67.2033 | 0 | 42.9 | 383.7 | 56.3 | 33.6016 | 0 | 0 | 0 | 68.3 | 1303.5 | 105.1029
608 | 113.7078 | 0.7 | 43 | 443.6 | 37.6 | 56.8539 | 0 | 0 | 0 | 136 | 1252.6 | 107.2699
609 | 206.8376 | 2.1 | 43.2 | 427.5 | 0 | 103.4188 | 0 | 0 | 0 | 145.9 | 604.5 | 117.7629
610 | 238.2504 | 3.5 | 43.4 | 367.5 | 0 | 119.1252 | 0 | 0 | 0 | 166.9 | 574 | 105.4598
611 | 244.757 | 3.5 | 43.4 | 265.6 | 0 | 122.3785 | 0 | 0 | 0 | 136.6 | 473.7 | 83.9702
612 | 243.5312 | 2.8 | 43.3 | 171.3 | 0 | 121.7656 | 0 | 0 | 0 | 87.6 | 378.3 | 123.6722
613 | 246.9884 | 1.4 | 43.1 | 95 | 75.1 | 123.4942 | 0 | 0 | 0 | 43.3 | 785.9 | 150.9545
614 | 248.1804 | 2.1 | 43.2 | 46.9 | 37.6 | 124.0902 | 0 | 0 | 0 | 30.4 | 632.9 | 127.6024
615 | 248.2442 | 3.5 | 43.4 | 28 | 0 | 124.1221 | 0 | 0 | 0 | 36.4 | 92.6 | 151.8609
616 | 298.1554 | 2.8 | 43.3 | 26.4 | 0 | 149.0777 | 0 | 0 | 0 | 35 | 131 | 145.5126
617 | 310.5916 | 2.1 | 43.2 | 40.7 | 0 | 155.2958 | 0 | 0 | 0 | 32.9 | 175.7 | 173.9714
618 | 223.2688 | 0.7 | 43 | 90 | 37.6 | 111.6344 | 0 | 0 | 0 | 28.6 | 703 | 212.7904
619 | 129.3133 | 0 | 42.9 | 58.1 | 75.1 | 64.6567 | 0 | 0 | 0 | 0 | 640.3 | 340.5389
620 | 96.0633 | 0 | 42.9 | 30.6 | 75.1 | 48.0316 | 0 | 0 | 0 | 0 | 554.4 | 191.7055
621 | 66.2813 | 0 | 42.9 | 53.3 | 75.1 | 33.1406 | 0 | 0 | 0 | 0 | 598.2 | 192.5744
622 | 45.6999 | 0 | 42.9 | 71 | 93.9 | 22.85 | 0 | 0 | 0 | 0 | 618.1 | 183.477
623 | 44.1568 | 0 | 0 | 0 | 0 | 22.0784 | 0 | 0 | 0 | 0.7 | 143.7 | 171.909
624 | 41.7683 | 0 | 0 | 3.3 | 0 | 20.8841 | 0 | 0 | 0 | 2.4 | 218 | 165.7422
625 | 41.3393 | 0 | 0 | 12.9 | 0 | 20.6697 | 0 | 0 | 0 | 4.2 | 247.5 | 116.8918
626 | 40.8264 | 0 | 0 | 28.3 | 0 | 20.4132 | 0 | 0 | 0 | 6.4 | 276 | 101.7392
627 | 44.8932 | 0 | 0 | 46.9 | 0 | 22.4466 | 0 | 0 | 0 | 10.4 | 302.6 | 98.9903
628 | 43.2568 | 0 | 0 | 62.1 | 0 | 21.6284 | 0 | 0 | 0 | 16.1 | 324.3 | 94.916
629 | 44.2696 | 0 | 0 | 75.4 | 0 | 22.1348 | 0 | 0 | 0 | 21.5 | 344.6 | 88.3644
630 | 41.3412 | 0 | 0 | 87.1 | 0 | 20.6706 | 0 | 0 | 0 | 26.4 | 359.3 | 90.8574
631 | 48.9519 | 0 | 42.9 | 257.5 | 56.3 | 24.476 | 0 | 0 | 0 | 44.6 | 903.6 | 112.7233
632 | 67.1639 | 0 | 42.9 | 274.8 | 37.6 | 33.582 | 0 | 0 | 0 | 47.5 | 862.2 | 221.0606
633 | 64.8885 | 0 | 42.9 | 270.2 | 0 | 32.4442 | 0 | 0 | 0 | 46.5 | 336.8 | 162.7314
634 | 64.409 | 0 | 42.9 | 270.1 | 0 | 32.2045 | 0 | 0 | 0 | 37.6 | 392.7 | 111.2675
635 | 60.5369 | 0 | 42.9 | 257 | 0 | 30.2684 | 0 | 0 | 0 | 27.8 | 389.8 | 147.0711
636 | 58.6879 | 0 | 42.9 | 242.2 | 0 | 29.3439 | 0 | 0 | 0 | 18.3 | 386.3 | 97.7951
637 | 56.0935 | 0 | 42.9 | 233.6 | 75.1 | 28.0467 | 0 | 0 | 0 | 11.3 | 884.1 | 101.74
638 | 54.7305 | 0 | 42.9 | 224.6 | 37.6 | 27.3652 | 0 | 0 | 0 | 6.1 | 823.4 | 163.8333
639 | 55.0295 | 0 | 42.9 | 229.1 | 0 | 27.5148 | 0 | 0 | 0 | 4.2 | 299.4 | 99.4704
640 | 58.1864 | 0 | 42.9 | 226.5 | 0 | 29.0932 | 0 | 0 | 0 | 4.3 | 363.3 | 76.8528
641 | 64.4828 | 0 | 42.9 | 237.1 | 0 | 32.2414 | 0 | 0 | 0 | 7.4 | 394.7 | 106.9132
642 | 68.5028 | 0 | 42.9 | 240.7 | 37.6 | 34.2514 | 0 | 0 | 0 | 17.1 | 911.6 | 177.0845
643 | 66.6349 | 0 | 42.9 | 204.8 | 75.1 | 33.3174 | 0 | 0 | 0 | 20.4 | 860.2 | 217.7444
644 | 52.5684 | 0 | 42.9 | 171.1 | 75.1 | 26.2842 | 0 | 0 | 0 | 10.4 | 774.1 | 257.6
645 | 42.2579 | 0 | 42.9 | 188.3 | 75.1 | 21.129 | 0 | 0 | 0 | 16.9 | 829.3 | 241.806
646 | 40.0017 | 0 | 42.9 | 197 | 93.9 | 20.0008 | 0 | 0 | 0 | 21.9 | 859.3 | 212.7776
647 | 40.523 | 0 | 0 | 93.9 | 0 | 20.2615 | 0 | 0 | 0 | 27 | 329.8 | 153.9597
648 | 42.1814 | 0 | 0 | 122.1 | 0 | 21.0907 | 0 | 0 | 0 | 31.3 | 427.5 | 129.3648
649 | 42.7324 | 0 | 0 | 133.2 | 0 | 21.3662 | 0 | 0 | 0 | 35.4 | 453.3 | 107.1486
650 | 40.58 | 0 | 0 | 143.7 | 0 | 20.29 | 0 | 0 | 0 | 38.9 | 478.2 | 86.8143
651 | 41.1645 | 0 | 0 | 156.8 | 0 | 20.5823 | 0 | 0 | 0 | 42.4 | 510 | 74.1619
652 | 42.4194 | 0 | 0 | 166.5 | 0 | 21.2097 | 0 | 0 | 0 | 45.4 | 533.5 | 75.9148
653 | 43.2847 | 0 | 0 | 174.8 | 0 | 21.6424 | 0 | 0 | 0 | 48.1 | 553.5 | 81.256
654 | 40.8986 | 0 | 0 | 182.2 | 0 | 20.4493 | 0 | 0 | 0 | 51 | 569.4 | 115.0138
655 | 47.6149 | 0 | 42.9 | 358.2 | 56.3 | 23.8075 | 0 | 0 | 0 | 65.7 | 1167.6 | 154.0531
656 | 65.0909 | 0 | 42.9 | 363.2 | 37.6 | 32.5454 | 0 | 0 | 0 | 68 | 1132.3 | 140.3179
657 | 68.7104 | 0 | 42.9 | 346.8 | 0 | 34.3552 | 0 | 0 | 0 | 67.3 | 536.1 | 151.4358
658 | 71.1951 | 0 | 42.9 | 337.7 | 0 | 35.5975 | 0 | 0 | 0 | 59.3 | 594.7 | 153.425
659 | 69.0709 | 0 | 42.9 | 327.9 | 0 | 34.5354 | 0 | 0 | 0 | 50.2 | 597.2 | 253.2272
660 | 71.2834 | 0 | 42.9 | 319.1 | 0 | 35.6417 | 0 | 0 | 0 | 41.2 | 599.9 | 147.1971
661 | 67.9527 | 0 | 42.9 | 317.8 | 75.1 | 33.9763 | 0 | 0 | 0 | 35.4 | 1183.9 | 183.5084
662 | 67.2352 | 0 | 42.9 | 257.4 | 37.6 | 33.6176 | 0 | 0 | 0 | 31.6 | 1021.2 | 94.9167
663 | 63.3987 | 0 | 42.9 | 224.5 | 0 | 31.6993 | 0 | 0 | 0 | 30.2 | 394.4 | 116.5398
664 | 66.0587 | 0 | 42.9 | 215.7 | 0 | 33.0294 | 0 | 0 | 0 | 31.7 | 443.3 | 143.2324
665 | 70.3044 | 0 | 42.9 | 223.1 | 0 | 35.1522 | 0 | 0 | 0 | 34 | 461.1 | 179.1975
666 | 70.0629 | 0 | 42.9 | 250.2 | 37.6 | 35.0315 | 0 | 0 | 0 | 41.2 | 1021.8 | 175.9977
667 | 63.7486 | 0 | 42.9 | 240.7 | 75.1 | 31.8743 | 0 | 0 | 0 | 42.1 | 981.1 | 238.8361
668 | 44.4367 | 0 | 42.9 | 201.9 | 75.1 | 22.2183 | 0 | 0 | 0 | 32.4 | 884.9 | 228.4713
669 | 42.5285 | 0 | 42.9 | 214.9 | 75.1 | 21.2642 | 0 | 0 | 0 | 37.3 | 928.7 | 298.7348
670 | 42.3196 | 0 | 42.9 | 222.4 | 93.9 | 21.1598 | 0 | 0 | 0 | 39.3 | 956 | 276.7862
671 | 40.6132 | 0 | 0 | 115.6 | 0 | 20.3066 | 0 | 0 | 0 | 41.4 | 401.5 | 148.5483
672 | 42.7693 | 0 | 0 | 141.2 | 0 | 21.3847 | 0 | 0 | 0 | 43.4 | 491 | 134.137
673 | 42.4839 | 0 | 0 | 151.1 | 0 | 21.2419 | 0 | 0 | 0 | 45.4 | 513.5 | 100.7868
674 | 41.7924 | 0 | 0 | 160 | 0 | 20.8962 | 0 | 0 | 0 | 47.6 | 533.3 | 90.5019
675 | 41.5578 | 0 | 0 | 168.7 | 0 | 20.7789 | 0 | 0 | 0 | 49.3 | 552.5 | 84.8072
676 | 42.6571 | 0 | 0 | 176.1 | 0 | 21.3286 | 0 | 0 | 0 | 51.1 | 569.9 | 81.4888
677 | 41.1242 | 0 | 0 | 181.5 | 0 | 20.5621 | 0 | 0 | 0 | 52.3 | 585 | 82.789
678 | 41.2358 | 0 | 0 | 186.5 | 0 | 20.6179 | 0 | 0 | 0 | 53 | 596.3 | 96.3495
679 | 63.4675 | 0 | 42.9 | 364.4 | 56.3 | 31.7337 | 0 | 0 | 0 | 68.7 | 1212.7 | 152.2522
680 | 104.9708 | 0.7 | 43 | 422.7 | 37.6 | 52.4854 | 0 | 0 | 0 | 136.7 | 1166.2 | 160.1803
681 | 196.0926 | 2.1 | 43.2 | 415.6 | 0 | 98.0463 | 0 | 0 | 0 | 148.1 | 548.9 | 116.4746
682 | 280.0137 | 3.5 | 43.4 | 406.5 | 0 | 140.0069 | 0 | 0 | 0 | 190.2 | 580.8 | 136.9872
683 | 311.8908 | 3.5 | 43.4 | 365.6 | 0 | 155.9454 | 0 | 0 | 0 | 189.5 | 546 | 260.0858
684 | 233.9385 | 2.8 | 43.3 | 314.4 | 0 | 116.9692 | 0 | 0 | 0 | 159.5 | 506 | 152.2932
685 | 216.4474 | 1.4 | 43.1 | 273.9 | 75.1 | 108.2237 | 0 | 0 | 0 | 110.3 | 1034.4 | 129.7724
686 | 226.9609 | 2.1 | 43.2 | 249.8 | 37.6 | 113.4804 | 0 | 0 | 0 | 94 | 925.1 | 202.1047
687 | 225.9722 | 3.5 | 43.4 | 246.5 | 0 | 112.9861 | 0 | 0 | 0 | 105 | 337.9 | 158.4201
688 | 258.4791 | 2.8 | 43.3 | 241.6 | 0 | 129.2395 | 0 | 0 | 0 | 97.3 | 394.7 | 99.7137
689 | 343.8553 | 2.1 | 43.2 | 242 | 0 | 171.9276 | 0 | 0 | 0 | 79.9 | 417.5 | 104.0137
690 | 269.4677 | 0.7 | 43 | 255.1 | 37.6 | 134.7338 | 0 | 0 | 0 | 55.6 | 992.2 | 112.8426
691 | 184.4959 | 0 | 42.9 | 200.7 | 75.1 | 92.248 | 0 | 0 | 0 | 7.1 | 939 | 181.2435
692 | 105.1998 | 0 | 42.9 | 169.1 | 75.1 | 52.5999 | 0 | 0 | 0 | 3.5 | 837.5 | 231.6927
693 | 58.0894 | 0 | 42.9 | 181.7 | 75.1 | 29.0447 | 0 | 0 | 0 | 5.8 | 874.3 | 195.8349
694 | 41.1013 | 0 | 42.9 | 189 | 93.9 | 20.5507 | 0 | 0 | 0 | 10.1 | 893 | 191.9796
695 | 41.4518 | 0 | 0 | 81.9 | 0 | 20.7259 | 0 | 0 | 0 | 15.6 | 340.4 | 202.4523
696 | 42.2384 | 0 | 0 | 106.3 | 0 | 21.1192 | 0 | 0 | 0 | 20.7 | 423.9 | 170.3121
697 | 40.7111 | 0 | 0 | 118.6 | 0 | 20.3556 | 0 | 0 | 0 | 25.6 | 448.2 | 101.4976
698 | 43.506 | 0 | 0 | 129.5 | 0 | 21.753 | 0 | 0 | 0 | 30.2 | 469.7 | 83.2687
699 | 41.2842 | 0 | 0 | 139.2 | 0 | 20.6421 | 0 | 0 | 0 | 34.1 | 488.8 | 82.4372
700 | 41.6111 | 0 | 0 | 146.9 | 0 | 20.8056 | 0 | 0 | 0 | 37.5 | 505 | 75.2072
701 | 41.5956 | 0 | 0 | 155.2 | 0 | 20.7978 | 0 | 0 | 0 | 40.3 | 525.5 | 76.3791
702 | 39.878 | 0 | 0 | 161.2 | 0 | 19.939 | 0 | 0 | 0 | 42.1 | 536.6 | 88.7166
703 | 51.9185 | 0 | 42.9 | 334.5 | 56.3 | 25.9593 | 0 | 0 | 0 | 56.5 | 1141.4 | 117.1196
704 | 89.6163 | 0.7 | 43 | 388.4 | 37.6 | 44.8081 | 0 | 0 | 0 | 119.1 | 1096.4 | 123.8699
705 | 152.9709 | 2.1 | 43.2 | 383.9 | 0 | 76.4855 | 0 | 0 | 0 | 133.9 | 492.4 | 252.0195
706 | 235.6025 | 3.5 | 43.4 | 391.1 | 0 | 117.8012 | 0 | 0 | 0 | 162.5 | 547.3 | 179.0953
707 | 299.3185 | 3.5 | 43.4 | 377.7 | 0 | 149.6593 | 0 | 0 | 0 | 151.6 | 547.6 | 187.9824
708 | 303.2799 | 2.8 | 43.3 | 359.4 | 0 | 151.64 | 0 | 0 | 0 | 111.6 | 549.3 | 131.7957
709 | 288.5636 | 1.4 | 43.1 | 330.4 | 75.1 | 144.2818 | 0 | 0 | 0 | 63.4 | 1120.6 | 167.226
710 | 270.532 | 2.1 | 43.2 | 275.3 | 37.6 | 135.266 | 0 | 0 | 0 | 59.7 | 960.3 | 122.6056
711 | 231.5161 | 3.5 | 43.4 | 252.4 | 0 | 115.7581 | 0 | 0 | 0 | 78.6 | 341.3 | 113.6782
712 | 239.2912 | 2.8 | 43.3 | 233.6 | 0 | 119.6456 | 0 | 0 | 0 | 73.8 | 381.8 | 133.5764
713 | 241.2198 | 2.1 | 43.2 | 225.8 | 0 | 120.6099 | 0 | 0 | 0 | 60.2 | 393.1 | 127.7519
714 | 199.8002 | 0.7 | 43 | 237.6 | 37.6 | 99.9001 | 0 | 0 | 0 | 44.7 | 947.6 | 285.1157
715 | 138.9668 | 0 | 42.9 | 184.9 | 75.1 | 69.4834 | 0 | 0 | 0 | 1.4 | 890.1 | 325.6785
716 | 89.5989 | 0 | 42.9 | 149.2 | 75.1 | 44.7995 | 0 | 0 | 0 | 0 | 779.5 | 359.249
717 | 58.8035 | 0 | 42.9 | 159 | 75.1 | 29.4017 | 0 | 0 | 0 | 0.3 | 807.4 | 280.7305
718 | 41.3567 | 0 | 42.9 | 163.5 | 93.9 | 20.6783 | 0 | 0 | 0 | 1.9 | 815.1 | 198.1928
719 | 41.9837 | 0 | 0 | 53.3 | 0 | 20.9918 | 0 | 0 | 0 | 3.4 | 270.2 | 182.6343
720 | 42.0397 | 0 | 0 | 72.5 | 0 | 21.0199 | 0 | 0 | 0 | 4.6 | 340.6 | 139.9821
721 | 42.5195 | 0 | 0 | 81 | 0 | 21.2598 | 0 | 0 | 0 | 6.8 | 353.2 | 96.9555
722 | 43.0588 | 0 | 0 | 87.3 | 0 | 21.5294 | 0 | 0 | 0 | 9.9 | 361.8 | 85.5149
723 | 42.3336 | 0 | 0 | 92.5 | 0 | 21.1668 | 0 | 0 | 0 | 12.7 | 368.6 | 87.526
724 | 43.9789 | 0 | 0 | 96.9 | 0 | 21.9895 | 0 | 0 | 0 | 14.9 | 374.2 | 86.8161
725 | 42.0057 | 0 | 0 | 101.5 | 0 | 21.0028 | 0 | 0 | 0 | 17 | 381.3 | 82.5543
726 | 41.3957 | 0 | 0 | 105 | 0 | 20.6979 | 0 | 0 | 0 | 18.9 | 383.4 | 87.6424
727 | 59.3824 | 0 | 42.9 | 266.9 | 56.3 | 29.6912 | 0 | 0 | 0 | 33 | 956.5 | 135.3549
728 | 105.8912 | 0.7 | 43 | 310.6 | 37.6 | 52.9456 | 0 | 0 | 0 | 85.4 | 914 | 110.2969
729 | 178.5612 | 2.1 | 43.2 | 298.8 | 0 | 89.2806 | 0 | 0 | 0 | 97.8 | 337.7 | 125.9974
730 | 239.3184 | 3.5 | 43.4 | 282.5 | 0 | 119.6592 | 0 | 0 | 0 | 123.4 | 368 | 93.2496
731 | 312.4288 | 3.5 | 43.4 | 259.9 | 0 | 156.2144 | 0 | 0 | 0 | 119.5 | 354.8 | 153.5136
732 | 276.312 | 2.8 | 43.3 | 228.3 | 0 | 138.156 | 0 | 0 | 0 | 98.1 | 330.6 | 129.7949
733 | 219.9331 | 1.4 | 43.1 | 199.1 | 75.1 | 109.9665 | 0 | 0 | 0 | 68.1 | 817.9 | 162.8858
734 | 207.6918 | 2.1 | 43.2 | 185.5 | 37.6 | 103.8459 | 0 | 0 | 0 | 67.9 | 742.8 | 215.0292
735 | 220.8508 | 3.5 | 43.4 | 180.7 | 0 | 110.4254 | 0 | 0 | 0 | 87.8 | 202.4 | 135.7329
736 | 198.8144 | 2.8 | 43.3 | 175.9 | 0 | 99.4072 | 0 | 0 | 0 | 85.3 | 249.5 | 105.6984
737 | 234.6448 | 2.1 | 43.2 | 177.4 | 0 | 117.3224 | 0 | 0 | 0 | 71.6 | 268.7 | 138.0385
738 | 158.4417 | 0.7 | 43 | 182.9 | 37.6 | 79.2208 | 0 | 0 | 0 | 46.9 | 791.9 | 161.4772
739 | 115.8211 | 0 | 42.9 | 134.1 | 75.1 | 57.9106 | 0 | 0 | 0 | 2.2 | 723.9 | 219.0695
740 | 84.5205 | 0 | 42.9 | 105.8 | 75.1 | 42.2603 | 0 | 0 | 0 | 0.1 | 628.6 | 262.154
741 | 58.6652 | 0 | 42.9 | 120.1 | 75.1 | 29.3326 | 0 | 0 | 0 | 1.3 | 669.1 | 201.1478
742 | 42.2418 | 0 | 42.9 | 128.5 | 93.9 | 21.1209 | 0 | 0 | 0 | 2.6 | 684.1 | 187.0206
743 | 41.4593 | 0 | 0 | 30.3 | 0 | 20.7296 | 0 | 0 | 0 | 3.6 | 179.9 | 183.6046
744 | 41.8541 | 0 | 0 | 51.6 | 0 | 20.9271 | 0 | 0 | 0 | 5.8 | 253.4 | 150.5045
745 | 41.6403 | 0 | 0 | 65.6 | 0 | 20.8201 | 0 | 0 | 0 | 9.4 | 280.6 | 107.6374
746 | 42.8583 | 0 | 0 | 80.4 | 0 | 21.4291 | 0 | 0 | 0 | 12.4 | 311.9 | 93.2469
747 | 41.683 | 0 | 0 | 94 | 0 | 20.8415 | 0 | 0 | 0 | 15.9 | 341.6 | 93.2462
748 | 42.5356 | 0 | 0 | 105 | 0 | 21.2678 | 0 | 0 | 0 | 19 | 365.4 | 92.2894
749 | 40.5283 | 0 | 0 | 114.4 | 0 | 20.2641 | 0 | 0 | 0 | 21.2 | 386.3 | 90.1446
750 | 40.4415 | 0 | 0 | 122.9 | 0 | 20.2207 | 0 | 0 | 0 | 24.1 | 400.5 | 111.0225
751 | 65.6713 | 0 | 42.9 | 291.2 | 56.3 | 32.8357 | 0 | 0 | 0 | 37.8 | 958.1 | 201.1741
752 | 109.5777 | 0.7 | 43 | 343.4 | 37.6 | 54.7889 | 0 | 0 | 0 | 92 | 937.2 | 144.5854
753 | 211.7735 | 2.1 | 43.2 | 329.9 | 0 | 105.8867 | 0 | 0 | 0 | 104.3 | 366.6 | 240.5924
754 | 390.582 | 3.5 | 43.4 | 287.5 | 0 | 195.291 | 0 | 0 | 0 | 124 | 376.1 | 164.8566
755 | 369.1047 | 3.5 | 43.4 | 230.8 | 0 | 184.5523 | 0 | 0 | 0 | 112 | 333.1 | 194.1678
756 | 350.7883 | 2.8 | 43.3 | 179.9 | 0 | 175.3941 | 0 | 0 | 0 | 85.2 | 291.4 | 176.3924
757 | 327.6625 | 1.4 | 43.1 | 130.7 | 75.1 | 163.8312 | 0 | 0 | 0 | 53.6 | 712.4 | 144.935
758 | 291.7115 | 2.1 | 43.2 | 100.6 | 37.6 | 145.8557 | 0 | 0 | 0 | 52.1 | 593.7 | 133.1867
759 | 279.4466 | 3.5 | 43.4 | 88.5 | 0 | 139.7233 | 0 | 0 | 0 | 69 | 94.3 | 105.8237
760 | 265.117 | 2.8 | 43.3 | 88.4 | 0 | 132.5585 | 0 | 0 | 0 | 68.7 | 136.9 | 120.3032
761 | 301.6008 | 2.1 | 43.2 | 98.2 | 0 | 150.8004 | 0 | 0 | 0 | 59.4 | 168.2 | 247.8119
762 | 247.4437 | 0.7 | 43 | 125.8 | 37.6 | 123.7218 | 0 | 0 | 0 | 42.2 | 667.9 | 124.6672
763 | 156.5911 | 0 | 42.9 | 83.8 | 75.1 | 78.2956 | 0 | 0 | 0 | 0.7 | 595.8 | 192.4486
764 | 91.6419 | 0 | 42.9 | 52.3 | 75.1 | 45.821 | 0 | 0 | 0 | 0 | 515.4 | 227.7738
765 | 58.8118 | 0 | 42.9 | 73.4 | 75.1 | 29.4059 | 0 | 0 | 0 | 0 | 562.1 | 262.8981
766 | 41.4949 | 0 | 42.9 | 88.9 | 93.9 | 20.7475 | 0 | 0 | 0 | 0.8 | 586.7 | 167.6033
767 | 41.931 | 0 | 0 | 0.4 | 0 | 20.9655 | 0 | 0 | 0 | 2.4 | 122.7 | 211.2034
768 | 42.6742 | 0 | 0 | 7.9 | 0 | 21.3371 | 0 | 0 | 0 | 4.2 | 194.3 | 142.0588
769 | 41.3976 | 0 | 0 | 20.3 | 0 | 20.6988 | 0 | 0 | 0 | 7.8 | 220 | 96.8308
770 | 40.9395 | 0 | 0 | 35.4 | 0 | 20.4698 | 0 | 0 | 0 | 11.5 | 241.5 | 91.7019
771 | 39.9918 | 0 | 0 | 49.2 | 0 | 19.9959 | 0 | 0 | 0 | 15.1 | 261.2 | 85.7475
772 | 41.0502 | 0 | 0 | 60.3 | 0 | 20.5251 | 0 | 0 | 0 | 19.4 | 277.7 | 78.6474
773 | 42.2307 | 0 | 0 | 69.7 | 0 | 21.1153 | 0 | 0 | 0 | 23 | 292 | 80.7808
774 | 40.9243 | 0 | 0 | 77.8 | 0 | 20.4622 | 0 | 0 | 0 | 26.1 | 300.7 | 106.431
775 | 57.3986 | 0 | 42.9 | 242.8 | 56.3 | 28.6993 | 0 | 0 | 0 | 41.2 | 825.7 | 132.3748
776 | 90.4704 | 0.7 | 43 | 281.8 | 37.6 | 45.2352 | 0 | 0 | 0 | 96.7 | 782.3 | 109.0881
777 | 158.0868 | 2.1 | 43.2 | 274.5 | 0 | 79.0434 | 0 | 0 | 0 | 110.2 | 275.5 | 183.9911
778 | 272.3937 | 3.5 | 43.4 | 272.8 | 0 | 136.1968 | 0 | 0 | 0 | 131.6 | 326.4 | 157.8591
779 | 314.3612 | 3.5 | 43.4 | 260.8 | 0 | 157.1806 | 0 | 0 | 0 | 121 | 324.3 | 119.6849
780 | 282.3667 | 2.8 | 43.3 | 245.2 | 0 | 141.1833 | 0 | 0 | 0 | 89.5 | 323.2 | 199.2673
781 | 241.0723 | 1.4 | 43.1 | 227.6 | 75.1 | 120.5361 | 0 | 0 | 0 | 53.3 | 800.9 | 195.2915
782 | 216.4635 | 2.1 | 43.2 | 225.3 | 37.6 | 108.2318 | 0 | 0 | 0 | 54.1 | 747.7 | 268.2722
783 | 198.7725 | 3.5 | 43.4 | 225.5 | 0 | 99.3863 | 0 | 0 | 0 | 75.1 | 234.3 | 115.9442
784 | 209.9592 | 2.8 | 43.3 | 217 | 0 | 104.9796 | 0 | 0 | 0 | 77.1 | 289.3 | 148.5214
785 | 273.74 | 2.1 | 43.2 | 209.2 | 0 | 136.87 | 0 | 0 | 0 | 64.4 | 302 | 332.8696
786 | 213.532 | 0.7 | 43 | 210.2 | 37.6 | 106.766 | 0 | 0 | 0 | 44.7 | 803.2 | 219.3052
787 | 127.0918 | 0 | 42.9 | 158.9 | 75.1 | 63.5459 | 0 | 0 | 0 | 1 | 743.8 | 228.9515
788 | 76.8112 | 0 | 42.9 | 130.5 | 75.1 | 38.4056 | 0 | 0 | 0 | 0 | 657.1 | 284.7153
789 | 57.1051 | 0 | 42.9 | 143.6 | 75.1 | 28.5525 | 0 | 0 | 0 | 0.1 | 701.3 | 394.2327
790 | 43.0659 | 0 | 42.9 | 150.4 | 93.9 | 21.533 | 0 | 0 | 0 | 1.4 | 719.9 | 213.2897
791 | 38.978 | 0 | 0 | 45.9 | 0 | 19.489 | 0 | 0 | 0 | 2.9 | 214.6 | 191.577
792 | 41.3359 | 0 | 0 | 69.2 | 0 | 20.668 | 0 | 0 | 0 | 4.7 | 294.8 | 126.0582
793 | 41.1893 | 0 | 0 | 84.1 | 0 | 20.5947 | 0 | 0 | 0 | 9 | 325.7 | 109.8098
794 | 41.7611 | 0 | 0 | 99 | 0 | 20.8806 | 0 | 0 | 0 | 13.8 | 358.3 | 91.5798
795 | 43.5819 | 0 | 0 | 115.2 | 0 | 21.791 | 0 | 0 | 0 | 18.2 | 395.8 | 87.7631
796 | 42.3274 | 0 | 0 | 125.2 | 0 | 21.1637 | 0 | 0 | 0 | 21.8 | 418.6 | 94.2044
797 | 41.472 | 0 | 0 | 132.8 | 0 | 20.736 | 0 | 0 | 0 | 25 | 435.3 | 92.7699
798 | 39.7975 | 0 | 0 | 141.3 | 0 | 19.8987 | 0 | 0 | 0 | 28.1 | 450.2 | 92.7686
799 | 47.7857 | 0 | 42.9 | 312.2 | 56.3 | 23.8929 | 0 | 0 | 0 | 43.5 | 1010.9 | 101.98
800 | 74.0551 | 0 | 42.9 | 338.5 | 37.6 | 37.0275 | 0 | 0 | 0 | 45.1 | 986.5 | 141.792
801 | 70.5976 | 0 | 42.9 | 330.2 | 0 | 35.2988 | 0 | 0 | 0 | 45 | 419.1 | 192.3955
802 | 66.6928 | 0 | 42.9 | 321.6 | 0 | 33.3464 | 0 | 0 | 0 | 41.8 | 464.1 | 205.7641
803 | 61.2311 | 0 | 42.9 | 285.3 | 0 | 30.6155 | 0 | 0 | 0 | 37.1 | 441.6 | 122.5603
804 | 59.7856 | 0 | 42.9 | 252 | 0 | 29.8928 | 0 | 0 | 0 | 33.4 | 421.5 | 187.2568
805 | 57.5452 | 0 | 42.9 | 251.2 | 75.1 | 28.7726 | 0 | 0 | 0 | 29.9 | 948.8 | 182.8094
806 | 54.4308 | 0 | 42.9 | 242.9 | 37.6 | 27.2154 | 0 | 0 | 0 | 27 | 880.9 | 218.4924
807 | 55.0339 | 0 | 42.9 | 244.9 | 0 | 27.5169 | 0 | 0 | 0 | 25.7 | 336.6 | 119.3928
808 | 59.7655 | 0 | 42.9 | 232.7 | 0 | 29.8827 | 0 | 0 | 0 | 26.2 | 390.7 | 136.4125
809 | 71.6835 | 0 | 42.9 | 235.3 | 0 | 35.8418 | 0 | 0 | 0 | 30.1 | 408 | 249.3648
810 | 76.3305 | 0 | 42.9 | 248 | 37.6 | 38.1653 | 0 | 0 | 0 | 34.6 | 936.4 | 165.0709
811 | 69.4487 | 0 | 42.9 | 219.3 | 75.1 | 34.7243 | 0 | 0 | 0 | 35.5 | 904.1 | 261.3088
812 | 51.7859 | 0 | 42.9 | 189.8 | 75.1 | 25.8929 | 0 | 0 | 0 | 26 | 825.8 | 366.2432
813 | 46.3275 | 0 | 42.9 | 208 | 75.1 | 23.1638 | 0 | 0 | 0 | 31.8 | 883.2 | 158.4448
814 | 39.8185 | 0 | 42.9 | 220.4 | 93.9 | 19.9093 | 0 | 0 | 0 | 35.7 | 926 | 234.6394
815 | 42.9085 | 0 | 0 | 118.6 | 0 | 21.4542 | 0 | 0 | 0 | 38.9 | 398.5 | 175.8179
816 | 42.4364 | 0 | 0 | 147.7 | 0 | 21.2182 | 0 | 0 | 0 | 42.6 | 499.4 | 133.2027
817 | 40.3999 | 0 | 0 | 165 | 0 | 20.2 | 0 | 0 | 0 | 47 | 540 | 116.326
818 | 41.9598 | 0 | 0 | 182.5 | 0 | 20.9799 | 0 | 0 | 0 | 51.5 | 582.4 | 87.8868
819 | 43.753 | 0 | 0 | 198.8 | 0 | 21.8765 | 0 | 0 | 0 | 55.7 | 621.3 | 80.4268
820 | 43.5767 | 0 | 0 | 212.5 | 0 | 21.7883 | 0 | 0 | 0 | 59.1 | 653.9 | 76.6139
821 | 43.1908 | 0 | 0 | 223.8 | 0 | 21.5954 | 0 | 0 | 0 | 62.9 | 681.6 | 85.6306
822 | 41.8383 | 0 | 0 | 233.4 | 0 | 20.9191 | 0 | 0 | 0 | 65.4 | 703.5 | 113.8016
823 | 49.2495 | 0 | 42.9 | 421.1 | 56.3 | 24.6247 | 0 | 0 | 0 | 82.4 | 1322 | 151.4588
824 | 66.7954 | 0 | 42.9 | 431.1 | 37.6 | 33.3977 | 0 | 0 | 0 | 86 | 1281.8 | 136.7523
825 | 65.9038 | 0 | 42.9 | 390 | 0 | 32.9519 | 0 | 0 | 0 | 78.5 | 637 | 118.9108
826 | 66.1948 | 0 | 42.9 | 370 | 0 | 33.0974 | 0 | 0 | 0 | 70 | 684.6 | 107.517
827 | 61.1037 | 0 | 42.9 | 344.8 | 0 | 30.5519 | 0 | 0 | 0 | 60.1 | 668 | 143.3366
828 | 60.2945 | 0 | 42.9 | 319 | 0 | 30.1472 | 0 | 0 | 0 | 53.2 | 645.6 | 293.7075
829 | 60.2926 | 0 | 42.9 | 299.9 | 75.1 | 30.1463 | 0 | 0 | 0 | 46.8 | 1192.6 | 168.6329
830 | 57.5507 | 0 | 42.9 | 257.3 | 37.6 | 28.7754 | 0 | 0 | 0 | 41.5 | 1045.3 | 128.5922
831 | 56.6923 | 0 | 42.9 | 232.3 | 0 | 28.3461 | 0 | 0 | 0 | 38.3 | 434 | 159.281
832 | 54.6238 | 0 | 42.9 | 219.3 | 0 | 27.3119 | 0 | 0 | 0 | 37.9 | 481.1 | 162.9253
833 | 64.8637 | 0 | 42.9 | 234.4 | 0 | 32.4318 | 0 | 0 | 0 | 43.8 | 507 | 209.4633
834 | 71.9625 | 0 | 42.9 | 271.8 | 37.6 | 35.9812 | 0 | 0 | 0 | 52.1 | 1063.9 | 312.9474
835 | 67.8445 | 0 | 42.9 | 261.5 | 75.1 | 33.9223 | 0 | 0 | 0 | 52.9 | 1027.9 | 197.3227
836 | 51.5578 | 0 | 42.9 | 221.3 | 75.1 | 25.7789 | 0 | 0 | 0 | 41.3 | 932.8 | 167.0646
837 | 43.4905 | 0 | 42.9 | 235.4 | 75.1 | 21.7452 | 0 | 0 | 0 | 46.9 | 978.5 | 195.5497
838 | 42.773 | 0 | 42.9 | 244.5 | 93.9 | 21.3865 | 0 | 0 | 0 | 51.3 | 1012.5 | 192.1047
839 | 42.4076 | 0 | 0 | 128.6 | 0 | 21.2038 | 0 | 0 | 0 | 54.9 | 457.4 | 165.1202
840 | 42.0469 | 0 | 0 | 156.3 | 0 | 21.0234 | 0 | 0 | 0 | 57.8 | 551.6 | 128.4341
841 | 41.9812 | 0 | 0 | 167.7 | 0 | 20.9906 | 0 | 0 | 0 | 60 | 573.6 | 89.6677
842 | 41.9074 | 0 | 0 | 175.8 | 0 | 20.9537 | 0 | 0 | 0 | 62.1 | 588.6 | 90.9768
843 | 41.4971 | 0 | 0 | 181.8 | 0 | 20.7485 | 0 | 0 | 0 | 66 | 599.4 | 80.5436
844 | 44.6744 | 0 | 0 | 187 | 0 | 22.3372 | 0 | 0 | 0 | 69.6 | 609.1 | 81.4934
845 | 40.774 | 0 | 0 | 192.2 | 0 | 20.387 | 0 | 0 | 0 | 71.1 | 619.5 | 79.1206
846 | 43.0114 | 0 | 0 | 196.8 | 0 | 21.5057 | 0 | 0 | 0 | 72.7 | 626.9 | 88.8375
847 | 62.9589 | 0 | 42.9 | 377.7 | 56.3 | 31.4794 | 0 | 0 | 0 | 91.1 | 1235.9 | 115.3808
848 | 99.8022 | 0.7 | 43 | 433.8 | 37.6 | 49.9011 | 0 | 0 | 0 | 163 | 1187.3 | 138.886
849 | 177.2831 | 2.1 | 43.2 | 427.8 | 0 | 88.6416 | 0 | 0 | 0 | 162.7 | 570.3 | 180.7622
850 | 288.3237 | 3.5 | 43.4 | 442.4 | 0 | 144.1618 | 0 | 0 | 0 | 195.4 | 632.7 | 121.4754
851 | 351.3728 | 3.5 | 43.4 | 426.2 | 0 | 175.6864 | 0 | 0 | 0 | 174.5 | 629.4 | 141.5394
852 | 310.6896 | 2.8 | 43.3 | 395.4 | 0 | 155.3448 | 0 | 0 | 0 | 122.2 | 618.3 | 139.0268
853 | 284.4311 | 1.4 | 43.1 | 342.9 | 75.1 | 142.2155 | 0 | 0 | 0 | 68.7 | 1169.5 | 172.2203
854 | 257.8493 | 2.1 | 43.2 | 302.6 | 37.6 | 128.9247 | 0 | 0 | 0 | 58.7 | 1023.9 | 120.5552
855 | 263.0681 | 3.5 | 43.4 | 279.1 | 0 | 131.5341 | 0 | 0 | 0 | 73 | 391.3 | 244.3268
856 | 231.9525 | 2.8 | 43.3 | 259.7 | 0 | 115.9763 | 0 | 0 | 0 | 68 | 433.4 | 131.7838
857 | 284.1648 | 2.1 | 43.2 | 242.1 | 0 | 142.0824 | 0 | 0 | 0 | 55.7 | 435.9 | 117.7123
858 | 250.5032 | 0.7 | 43 | 251 | 37.6 | 125.2516 | 0 | 0 | 0 | 42.4 | 988.7 | 169.6254
859 | 136.5729 | 0 | 42.9 | 202.4 | 75.1 | 68.2865 | 0 | 0 | 0 | 1.9 | 945.3 | 299.8996
860 | 88.0505 | 0 | 42.9 | 174 | 75.1 | 44.0253 | 0 | 0 | 0 | 0.1 | 854.6 | 339.6253
861 | 50.5995 | 0 | 42.9 | 192.2 | 75.1 | 25.2997 | 0 | 0 | 0 | 1.9 | 903.7 | 307.5818
862 | 42.9534 | 0 | 42.9 | 204.8 | 93.9 | 21.4767 | 0 | 0 | 0 | 3.8 | 936 | 183.244
863 | 39.1104 | 0 | 0 | 97.9 | 0 | 19.5552 | 0 | 0 | 0 | 5.5 | 391.4 | 189.2659
864 | 42.888 | 0 | 0 | 126.7 | 0 | 21.444 | 0 | 0 | 0 | 7.1 | 487.2 | 146.7112
865 | 41.0155 | 0 | 0 | 146 | 0 | 20.5077 | 0 | 0 | 0 | 10.8 | 527.3 | 99.5882
866 | 41.2529 | 0 | 0 | 165.5 | 0 | 20.6264 | 0 | 0 | 0 | 16.8 | 569.7 | 85.2778
867 | 38.1443 | 0 | 0 | 184.2 | 0 | 19.0722 | 0 | 0 | 0 | 23 | 611.1 | 77.924
868 | 40.8159 | 0 | 0 | 199.1 | 0 | 20.4079 | 0 | 0 | 0 | 27.9 | 645.1 | 78.1683
869 | 41.6424 | 0 | 0 | 211.7 | 0 | 20.8212 | 0 | 0 | 0 | 31.5 | 676 | 77.4438
870 | 43.4096 | 0 | 0 | 223.2 | 0 | 21.7048 | 0 | 0 | 0 | 34.3 | 701.3 | 90.2677
871 | 59.8882 | 0 | 42.9 | 411.6 | 56.3 | 29.9441 | 0 | 0 | 0 | 50 | 1333.4 | 119.9079
872 | 97.413 | 0.7 | 43 | 475.2 | 37.6 | 48.7065 | 0 | 0 | 0 | 109.2 | 1286.3 | 142.7567
873 | 183.1933 | 2.1 | 43.2 | 444.4 | 0 | 91.5967 | 0 | 0 | 0 | 127.1 | 624.5 | 109.4456
874 | 314.8806 | 3.5 | 43.4 | 421.4 | 0 | 157.4403 | 0 | 0 | 0 | 172.8 | 643.6 | 103.7764
875 | 350.5515 | 3.5 | 43.4 | 373.6 | 0 | 175.2757 | 0 | 0 | 0 | 179.1 | 607.6 | 200.0231
876 | 334.9165 | 2.8 | 43.3 | 318 | 0 | 167.4583 | 0 | 0 | 0 | 151.5 | 565 | 273.6098
877 | 291.8776 | 1.4 | 43.1 | 253.7 | 75.1 | 145.9388 | 0 | 0 | 0 | 109.1 | 1051.3 | 226.2188
878 | 239.7127 | 2.1 | 43.2 | 227.6 | 37.6 | 119.8563 | 0 | 0 | 0 | 117.5 | 912.8 | 176.8138
879 | 241.1774 | 3.5 | 43.4 | 219.9 | 0 | 120.5887 | 0 | 0 | 0 | 159.4 | 332.7 | 163.9883
880 | 227.9861 | 2.8 | 43.3 | 211.4 | 0 | 113.9931 | 0 | 0 | 0 | 158.3 | 387.8 | 151.4676
881 | 249.6444 | 2.1 | 43.2 | 215.2 | 0 | 124.8222 | 0 | 0 | 0 | 129.8 | 416.8 | 292.7601
882 | 239.3665 | 0.7 | 43 | 240.1 | 37.6 | 119.6832 | 0 | 0 | 0 | 81 | 961.8 | 342.351
883 | 127.3534 | 0 | 42.9 | 188.3 | 75.1 | 63.6767 | 0 | 0 | 0 | 25.6 | 919 | 354.2771
884 | 69.1527 | 0 | 42.9 | 156.8 | 75.1 | 34.5763 | 0 | 0 | 0 | 21.3 | 837.9 | 329.5699
885 | 55.8425 | 0 | 42.9 | 182 | 75.1 | 27.9212 | 0 | 0 | 0 | 29 | 895.4 | 284.0494
886 | 41.8371 | 0 | 42.9 | 200.7 | 93.9 | 20.9185 | 0 | 0 | 0 | 33.2 | 940 | 243.7758
887 | 43.0154 | 0 | 0 | 81.5 | 0 | 21.5077 | 0 | 0 | 0 | 36.6 | 413.5 | 224.5958
888 | 39.4212 | 0 | 0 | 117.6 | 0 | 19.7106 | 0 | 0 | 0 | 40.7 | 515.1 | 235.3267
889 | 39.1792 | 0 | 0 | 138.1 | 0 | 19.5896 | 0 | 0 | 0 | 43.9 | 546.3 | 109.089
890 | 41.6923 | 0 | 0 | 154.5 | 0 | 20.8462 | 0 | 0 | 0 | 46.1 | 572.8 | 89.5442
891 | 43.0383 | 0 | 0 | 169 | 0 | 21.5192 | 0 | 0 | 0 | 48.6 | 598.7 | 87.1748
892 | 42.9677 | 0 | 0 | 180.2 | 0 | 21.4838 | 0 | 0 | 0 | 50.6 | 619.2 | 90.2626
893 | 44.6707 | 0 | 0 | 189.8 | 0 | 22.3353 | 0 | 0 | 0 | 52.2 | 637.3 | 90.2645
894 | 41.6272 | 0 | 0 | 198.9 | 0 | 20.8136 | 0 | 0 | 0 | 54.4 | 651 | 98.8719
895 | 71.0507 | 0 | 42.9 | 378.9 | 56.3 | 35.5253 | 0 | 0 | 0 | 69.3 | 1236.5 | 128.8216
896 | 111.9146 | 0.7 | 43 | 436.2 | 37.6 | 55.9573 | 0 | 0 | 0 | 135.9 | 1199.9 | 111.9941
897 | 197.5644 | 2.1 | 43.2 | 402 | 0 | 98.7822 | 0 | 0 | 0 | 143.5 | 555.4 | 119.4204
898 | 291.1195 | 3.5 | 43.4 | 362.6 | 0 | 145.5598 | 0 | 0 | 0 | 176 | 560.5 | 100.7837
899 | 342.2716 | 3.5 | 43.4 | 297.6 | 0 | 171.1358 | 0 | 0 | 0 | 159.6 | 504.3 | 111.0235
900 | 315.5228 | 2.8 | 43.3 | 224.4 | 0 | 157.7614 | 0 | 0 | 0 | 113.3 | 437.9 | 161.8532
901 | 279.3899 | 1.4 | 43.1 | 156.2 | 75.1 | 139.6949 | 0 | 0 | 0 | 64.8 | 868.4 | 195.5113
902 | 259.8217 | 2.1 | 43.2 | 110.3 | 37.6 | 129.9108 | 0 | 0 | 0 | 58.8 | 714.1 | 141.8305
903 | 260.965 | 3.5 | 43.4 | 92.5 | 0 | 130.4825 | 0 | 0 | 0 | 75.9 | 163.8 | 147.6062
904 | 333.1679 | 2.8 | 43.3 | 83.9 | 0 | 166.584 | 0 | 0 | 0 | 74.4 | 203.2 | 130.6979
905 | 364.5625 | 2.1 | 43.2 | 95.4 | 0 | 182.2812 | 0 | 0 | 0 | 64.8 | 235.7 | 214.5896
906 | 300.6555 | 0.7 | 43 | 132.9 | 37.6 | 150.3278 | 0 | 0 | 0 | 46 | 760.1 | 316.9086
907 | 195.0414 | 0 | 42.9 | 94.9 | 75.1 | 97.5207 | 0 | 0 | 0 | 1.8 | 701.6 | 214.0206
908 | 107.2654 | 0 | 42.9 | 69 | 75.1 | 53.6327 | 0 | 0 | 0 | 0 | 629.9 | 184.4157
909 | 57.6301 | 0 | 42.9 | 97.7 | 75.1 | 28.815 | 0 | 0 | 0 | 1.4 | 688.1 | 182.5791
910 | 43.2931 | 0 | 42.9 | 120.3 | 93.9 | 21.6465 | 0 | 0 | 0 | 3.4 | 728.5 | 241.8278
911 | 40.6764 | 0 | 0 | 14.2 | 0 | 20.3382 | 0 | 0 | 0 | 5.2 | 245.7 | 188.6203
912 | 43.2131 | 0 | 0 | 42.2 | 0 | 21.6066 | 0 | 0 | 0 | 8.6 | 343.3 | 162.8514
913 | 43.3578 | 0 | 0 | 69.8 | 0 | 21.6789 | 0 | 0 | 0 | 15 | 386.5 | 135.764
914 | 39.2148 | 0 | 0 | 95.7 | 0 | 19.6074 | 0 | 0 | 0 | 21.8 | 430.8 | 104.8653
915 | 41.6483 | 0 | 0 | 119.9 | 0 | 20.8242 | 0 | 0 | 0 | 28.9 | 475 | 98.2745
916 | 43.6098 | 0 | 0 | 139.1 | 0 | 21.8049 | 0 | 0 | 0 | 34.7 | 510.4 | 89.9036
917 | 40.8478 | 0 | 0 | 155.4 | 0 | 20.4239 | 0 | 0 | 0 | 39.7 | 542.8 | 79.3603
918 | 39.9004 | 0 | 0 | 169.3 | 0 | 19.9502 | 0 | 0 | 0 | 45 | 567.4 | 107.2743
919 | 53.2351 | 0 | 42.9 | 349 | 56.3 | 26.6175 | 0 | 0 | 0 | 61.3 | 1136.9 | 122.2124
920 | 100.7177 | 0.7 | 43 | 406 | 37.6 | 50.3588 | 0 | 0 | 0 | 122.7 | 1097.5 | 124.1783
921 | 209.0437 | 2.1 | 43.2 | 401.1 | 0 | 104.5218 | 0 | 0 | 0 | 137.5 | 523.9 | 108.727
922 | 324.2825 | 3.5 | 43.4 | 403.6 | 0 | 162.1412 | 0 | 0 | 0 | 178.3 | 574.8 | 126.452
923 | 350.4938 | 3.5 | 43.4 | 377 | 0 | 175.2469 | 0 | 0 | 0 | 174.2 | 558.6 | 218.0293
924 | 315.1233 | 2.8 | 43.3 | 344.5 | 0 | 157.5617 | 0 | 0 | 0 | 134.5 | 544 | 143.9805
925 | 274.0927 | 1.4 | 43.1 | 319.7 | 75.1 | 137.0463 | 0 | 0 | 0 | 87.5 | 1076.1 | 169.4803
926 | 238.3499 | 2.1 | 43.2 | 312 | 37.6 | 119.175 | 0 | 0 | 0 | 89.2 | 995.4 | 323.7738
927 | 211.3997 | 3.5 | 43.4 | 325.5 | 0 | 105.6998 | 0 | 0 | 0 | 119.6 | 438.5 | 140.7527
928 | 233.521 | 2.8 | 43.3 | 319.5 | 0 | 116.7605 | 0 | 0 | 0 | 119.5 | 508 | 104.2536
929 | 278.7731 | 2.1 | 43.2 | 311.3 | 0 | 139.3866 | 0 | 0 | 0 | 99 | 527.8 | 168.811
930 | 248.0651 | 0.7 | 43 | 318.5 | 37.6 | 124.0325 | 0 | 0 | 0 | 63.6 | 1083.6 | 203.0916
931 | 181.6533 | 0 | 42.9 | 255.9 | 75.1 | 90.8267 | 0 | 0 | 0 | 11 | 1059.4 | 198.9204
932 | 108.3926 | 0 | 42.9 | 226.9 | 75.1 | 54.1963 | 0 | 0 | 0 | 5.3 | 976 | 253.9825
933 | 57.9285 | 0 | 42.9 | 245.6 | 75.1 | 28.9643 | 0 | 0 | 0 | 11.9 | 1035.2 | 192.8915
934 | 42.5167 | 0 | 42.9 | 259.3 | 93.9 | 21.2584 | 0 | 0 | 0 | 19.7 | 1084.4 | 301.7769
935 | 42.9233 | 0 | 0 | 150.5 | 0 | 21.4617 | 0 | 0 | 0 | 26.7 | 526.2 | 295.1893
936 | 39.8799 | 0 | 0 | 182.3 | 0 | 19.9399 | 0 | 0 | 0 | 32.5 | 633.6 | 130.0848
937 | 43.7369 | 0 | 0 | 198.7 | 0 | 21.8684 | 0 | 0 | 0 | 36.8 | 669.6 | 101.0242
938 | 41.4382 | 0 | 0 | 212.3 | 0 | 20.7191 | 0 | 0 | 0 | 39.9 | 698.2 | 85.7469
939 | 43.0315 | 0 | 0 | 225.4 | 0 | 21.5157 | 0 | 0 | 0 | 44.4 | 726.1 | 83.968
940 | 42.1498 | 0 | 0 | 236.3 | 0 | 21.0749 | 0 | 0 | 0 | 47.1 | 751 | 79.123
941 | 40.872 | 0 | 0 | 244.7 | 0 | 20.436 | 0 | 0 | 0 | 48.9 | 773.5 | 79.2426
942 | 42.9894 | 0 | 0 | 252.9 | 0 | 21.4947 | 0 | 0 | 0 | 50.8 | 793.2 | 96.7119
943 | 57.0759 | 0 | 42.9 | 441.1 | 56.3 | 28.538 | 0 | 0 | 0 | 65 | 1432.5 | 97.9179
944 | 105.2974 | 0.7 | 43 | 507.7 | 37.6 | 52.6487 | 0 | 0 | 0 | 129.4 | 1378.7 | 104.2511
945 | 190.6553 | 2.1 | 43.2 | 467.5 | 0 | 95.3277 | 0 | 0 | 0 | 151 | 689.1 | 130.0388
946 | 294.3988 | 3.5 | 43.4 | 428.8 | 0 | 147.1994 | 0 | 0 | 0 | 206.5 | 687.5 | 96.8337
947 | 303.0779 | 3.5 | 43.4 | 359.4 | 0 | 151.5389 | 0 | 0 | 0 | 214.5 | 628.2 | 139.2463
948 | 239.955 | 2.8 | 43.3 | 288.7 | 0 | 119.9775 | 0 | 0 | 0 | 181.9 | 566.7 | 136.1784
949 | 217.2842 | 1.4 | 43.1 | 233.1 | 75.1 | 108.6421 | 0 | 0 | 0 | 127.7 | 1051 | 169.5965
950 | 207.2622 | 2.1 | 43.2 | 209 | 37.6 | 103.6311 | 0 | 0 | 0 | 121.2 | 916.1 | 172.3923
951 | 206.1205 | 3.5 | 43.4 | 209.8 | 0 | 103.0602 | 0 | 0 | 0 | 144.7 | 344.8 | 108.1222
952 | 187.0714 | 2.8 | 43.3 | 205.3 | 0 | 93.5357 | 0 | 0 | 0 | 135.1 | 404.4 | 147.6889
953 | 195.2295 | 2.1 | 43.2 | 208.7 | 0 | 97.6147 | 0 | 0 | 0 | 107.8 | 433.5 | 150.1941
954 | 150.1754 | 0.7 | 43 | 237.4 | 37.6 | 75.0877 | 0 | 0 | 0 | 69.5 | 987.9 | 136.3137
955 | 104.5638 | 0 | 42.9 | 187 | 75.1 | 52.2819 | 0 | 0 | 0 | 16.6 | 949.5 | 267.814
956 | 61.5791 | 0 | 42.9 | 154.8 | 75.1 | 30.7896 | 0 | 0 | 0 | 9.8 | 864.8 | 252.0342
957 | 43.0343 | 0 | 42.9 | 179.1 | 75.1 | 21.5171 | 0 | 0 | 0 | 16.3 | 918.4 | 188.0398
958 | 45.1975 | 0 | 42.9 | 197 | 93.9 | 22.5988 | 0 | 0 | 0 | 21.3 | 959.2 | 211.8293
959 | 43.0287 | 0 | 0 | 77.8 | 0 | 21.5144 | 0 | 0 | 0 | 25.6 | 425.8 | 236.9647
960 | 43.1282 | 0 | 0 | 113.3 | 0 | 21.5641 | 0 | 0 | 0 | 29.6 | 525.2 | 172.1369
961 | 41.0592 | 0 | 0 | 135.2 | 0 | 20.5296 | 0 | 0 | 0 | 33.9 | 559.2 | 93.8447
962 | 41.877 | 0 | 0 | 154.2 | 0 | 20.9385 | 0 | 0 | 0 | 37.8 | 591.8 | 85.1604
963 | 42.1454 | 0 | 0 | 171.9 | 0 | 21.0727 | 0 | 0 | 0 | 40.8 | 624.9 | 79.8355
964 | 39.2315 | 0 | 0 | 186 | 0 | 19.6158 | 0 | 0 | 0 | 43.6 | 651.4 | 77.8047
965 | 41.5383 | 0 | 0 | 197.6 | 0 | 20.7691 | 0 | 0 | 0 | 46.8 | 673.2 | 81.2544
966 | 42.1681 | 0 | 0 | 207.5 | 0 | 21.084 | 0 | 0 | 0 | 49.4 | 688.2 | 86.8178
967 | 53.5416 | 0 | 42.9 | 390.4 | 56.3 | 26.7708 | 0 | 0 | 0 | 64.5 | 1294 | 175.8553
968 | 68.377 | 0 | 42.9 | 423 | 37.6 | 34.1885 | 0 | 0 | 0 | 66.2 | 1254.4 | 234.1655
969 | 66.9873 | 0 | 42.9 | 404.3 | 0 | 33.4936 | 0 | 0 | 0 | 62.9 | 621.8 | 190.4148
970 | 65.3844 | 0 | 42.9 | 389.3 | 0 | 32.6922 | 0 | 0 | 0 | 57.9 | 652.1 | 150.7301
971 | 65.2861 | 0 | 42.9 | 346.6 | 0 | 32.6431 | 0 | 0 | 0 | 51.8 | 617.2 | 110.057
972 | 62.5867 | 0 | 42.9 | 306.4 | 0 | 31.2933 | 0 | 0 | 0 | 47.4 | 585.8 | 123.735
973 | 60.019 | 0 | 42.9 | 260.7 | 75.1 | 30.0095 | 0 | 0 | 0 | 48.5 | 1094 | 162.9635
974 | 56.5317 | 0 | 42.9 | 218.3 | 37.6 | 28.2659 | 0 | 0 | 0 | 42.9 | 941.7 | 328.719
975 | 54.171 | 0 | 42.9 | 200.9 | 0 | 27.0855 | 0 | 0 | 0 | 38.3 | 347.2 | 258.9861
976 | 53.571 | 0 | 42.9 | 185.4 | 0 | 26.7855 | 0 | 0 | 0 | 42.9 | 392 | 194.6356
977 | 61.1806 | 0 | 42.9 | 186 | 0 | 30.5903 | 0 | 0 | 0 | 44.4 | 407.5 | 120.1182
978 | 70.1677 | 0 | 42.9 | 214.8 | 37.6 | 35.0838 | 0 | 0 | 0 | 49 | 949.5 | 215.179
979 | 64.6653 | 0 | 42.9 | 192.6 | 75.1 | 32.3327 | 0 | 0 | 0 | 49.9 | 902.4 | 261.1664
980 | 50.4201 | 0 | 42.9 | 156.4 | 75.1 | 25.21 | 0 | 0 | 0 | 39.5 | 814.9 | 234.0205
981 | 45.3984 | 0 | 42.9 | 176.4 | 75.1 | 22.6992 | 0 | 0 | 0 | 44.1 | 864.2 | 257.2901
982 | 41.1856 | 0 | 42.9 | 190.9 | 93.9 | 20.5928 | 0 | 0 | 0 | 46.9 | 898.8 | 196.9479
983 | 41.7001 | 0 | 0 | 74.6 | 0 | 20.85 | 0 | 0 | 0 | 50.7 | 370.1 | 163.7591
984 | 39.3078 | 0 | 0 | 106.2 | 0 | 19.6539 | 0 | 0 | 0 | 53.9 | 464.8 | 141.417
985 | 39.4048 | 0 | 0 | 124.5 | 0 | 19.7024 | 0 | 0 | 0 | 54.9 | 495.3 | 99.1111
986 | 43.9641 | 0 | 0 | 140 | 0 | 21.982 | 0 | 0 | 0 | 56.3 | 523.2 | 78.2858
987 | 44.4695 | 0 | 0 | 154.4 | 0 | 22.2348 | 0 | 0 | 0 | 57.5 | 551.6 | 77.4433
988 | 42.3835 | 0 | 0 | 165.7 | 0 | 21.1917 | 0 | 0 | 0 | 59 | 573.6 | 79.1216
989 | 40.1461 | 0 | 0 | 175.5 | 0 | 20.0731 | 0 | 0 | 0 | 60.9 | 592.9 | 87.6436
990 | 43.59 | 0 | 0 | 184.1 | 0 | 21.795 | 0 | 0 | 0 | 62.7 | 606.1 | 97.5541
991 | 56.5491 | 0 | 42.9 | 361.7 | 56.3 | 28.2745 | 0 | 0 | 0 | 80.4 | 1198.4 | 132.6184
992 | 73.6165 | 0 | 42.9 | 363.9 | 37.6 | 36.8083 | 0 | 0 | 0 | 81.8 | 1161.2 | 177.2867
993 | 74.5351 | 0 | 42.9 | 339 | 0 | 37.2676 | 0 | 0 | 0 | 81.2 | 549.4 | 167.0165
994 | 73.7752 | 0 | 42.9 | 320.8 | 0 | 36.8876 | 0 | 0 | 0 | 80.9 | 593.4 | 242.3814
995 | 71.8177 | 0 | 42.9 | 301.8 | 0 | 35.9089 | 0 | 0 | 0 | 79.3 | 580.9 | 215.3823
996 | 70.1736 | 0 | 42.9 | 275.1 | 0 | 35.0868 | 0 | 0 | 0 | 74 | 555.9 | 203.8163
997 | 64.0678 | 0 | 42.9 | 263.2 | 75.1 | 32.0339 | 0 | 0 | 0 | 68.9 | 1094.5 | 337.9927
998 | 59.2482 | 0 | 42.9 | 233.5 | 37.6 | 29.6241 | 0 | 0 | 0 | 55.8 | 979.6 | 178.2762
999 | 65.1277 | 0 | 42.9 | 228.1 | 0 | 32.5639 | 0 | 0 | 0 | 42.7 | 402.3 | 155.0427
1000 | 70.0521 | 0 | 42.9 | 228.4 | 0 | 35.026 | 0 | 0 | 0 | 37.5 | 461.1 | 204.5144
1001 | 75.4128 | 0 | 42.9 | 237.1 | 0 | 37.7064 | 0 | 0 | 0 | 43.6 | 478.2 | 228.7874
1002 | 76.5592 | 0 | 42.9 | 261.9 | 37.6 | 38.2796 | 0 | 0 | 0 | 49.6 | 1042.8 | 184.0045
1003 | 63.0528 | 0 | 42.9 | 249.5 | 75.1 | 31.5264 | 0 | 0 | 0 | 50.7 | 1001.9 | 225.592
1004 | 46.057 | 0 | 42.9 | 210.9 | 75.1 | 23.0285 | 0 | 0 | 0 | 40 | 908.8 | 204.8377
1005 | 43.2581 | 0 | 42.9 | 225.4 | 75.1 | 21.629 | 0 | 0 | 0 | 44.7 | 956.9 | 230.0691
1006 | 41.6269 | 0 | 42.9 | 234.4 | 93.9 | 20.8135 | 0 | 0 | 0 | 47.2 | 989.1 | 182.6163
1007 | 41.1456 | 0 | 0 | 128.6 | 0 | 20.5728 | 0 | 0 | 0 | 49.3 | 431.5 | 197.6354
1008 | 42.1454 | 0 | 0 | 156.3 | 0 | 21.0727 | 0 | 0 | 0 | 51.6 | 525.2 | 147.1847
1009 | 40.4071 | 0 | 0 | 168.8 | 0 | 20.2035 | 0 | 0 | 0 | 54.3 | 554.8 | 109.2106
1010 | 40.81 | 0 | 0 | 180.5 | 0 | 20.405 | 0 | 0 | 0 | 56.7 | 581.7 | 89.5473
1011 | 39.4054 | 0 | 0 | 191.5 | 0 | 19.7027 | 0 | 0 | 0 | 59.2 | 607.2 | 83.266
1012 | 43.1307 | 0 | 0 | 200.4 | 0 | 21.5653 | 0 | 0 | 0 | 60.3 | 628.8 | 79.0015
1013 | 43.8419 | 0 | 0 | 207.9 | 0 | 21.921 | 0 | 0 | 0 | 61.8 | 649.4 | 78.2867
1014 | 42.5362 | 0 | 0 | 214.7 | 0 | 21.2681 | 0 | 0 | 0 | 63.6 | 666.1 | 89.3078
1015 | 56.157 | 0 | 42.9 | 397.4 | 56.3 | 28.0785 | 0 | 0 | 0 | 82 | 1288.7 | 121.3688
1016 | 106.326 | 0.7 | 43 | 461.4 | 37.6 | 53.163 | 0 | 0 | 0 | 153.6 | 1241 | 131.3421
1017 | 206.7744 | 2.1 | 43.2 | 445.8 | 0 | 103.3872 | 0 | 0 | 0 | 166.7 | 601.9 | 110.6577
1018 | 318.7761 | 3.5 | 43.4 | 435.8 | 0 | 159.388 | 0 | 0 | 0 | 212.1 | 632.4 | 105.5791
1019 | 344.0087 | 3.5 | 43.4 | 396.8 | 0 | 172.0044 | 0 | 0 | 0 | 209.1 | 602.4 | 105.9396
1020 | 311.8666 | 2.8 | 43.3 | 355.4 | 0 | 155.9333 | 0 | 0 | 0 | 171.6 | 576.7 | 171.72
1021 | 309.9724 | 1.4 | 43.1 | 316.6 | 75.1 | 154.9862 | 0 | 0 | 0 | 118.6 | 1126.5 | 217.0058
1022 | 285.196 | 2.1 | 43.2 | 295.1 | 37.6 | 142.598 | 0 | 0 | 0 | 122.5 | 1010.1 | 134.6476
1023 | 238.2532 | 3.5 | 43.4 | 296.3 | 0 | 119.1266 | 0 | 0 | 0 | 155.4 | 415.2 | 192.1115
1024 | 225.2163 | 2.8 | 43.3 | 287.5 | 0 | 112.6082 | 0 | 0 | 0 | 152.6 | 471.6 | 137.4168
1025 | 271.7621 | 2.1 | 43.2 | 282.3 | 0 | 135.881 | 0 | 0 | 0 | 129.8 | 489.4 | 187.6172
1026 | 249.9792 | 0.7 | 43 | 292.6 | 37.6 | 124.9896 | 0 | 0 | 0 | 86.1 | 1058.9 | 202.5831
1027 | 169.0761 | 0 | 42.9 | 234.6 | 75.1 | 84.538 | 0 | 0 | 0 | 30.8 | 1019.8 | 320.8889
1028 | 109.1553 | 0 | 42.9 | 202.6 | 75.1 | 54.5777 | 0 | 0 | 0 | 25.1 | 922.2 | 203.9695
1029 | 65.1801 | 0 | 42.9 | 216 | 75.1 | 32.5901 | 0 | 0 | 0 | 29.9 | 962.1 | 210.5114
1030 | 40.3305 | 0 | 42.9 | 223.2 | 93.9 | 20.1653 | 0 | 0 | 0 | 34.8 | 987.1 | 209.7097
1031 | 41.6418 | 0 | 0 | 111.7 | 0 | 20.8209 | 0 | 0 | 0 | 38.1 | 423.5 | 276.8335
1032 | 42.8967 | 0 | 0 | 137.5 | 0 | 21.4483 | 0 | 0 | 0 | 40.5 | 512.8 | 245.3054
1033 | 38.9086 | 0 | 0 | 149.3 | 0 | 19.4543 | 0 | 0 | 0 | 42.4 | 535.2 | 129.654
1034 | 39.7476 | 0 | 0 | 158.7 | 0 | 19.8738 | 0 | 0 | 0 | 43.8 | 552.6 | 104.9854
1035 | 42.2173 | 0 | 0 | 166.5 | 0 | 21.1087 | 0 | 0 | 0 | 44.8 | 566.4 | 91.3383
1036 | 41.3929 | 0 | 0 | 172.9 | 0 | 20.6965 | 0 | 0 | 0 | 46 | 579 | 89.3096
1037 | 43.8286 | 0 | 0 | 178.9 | 0 | 21.9143 | 0 | 0 | 0 | 47.4 | 593.1 | 92.0567
1038 | 43.9563 | 0 | 0 | 184.2 | 0 | 21.9782 | 0 | 0 | 0 | 48.9 | 602.6 | 114.5346
1039 | 63.5341 | 0 | 42.9 | 361.5 | 56.3 | 31.7671 | 0 | 0 | 0 | 63.9 | 1215.2 | 108.2436
1040 | 114.2371 | 0.7 | 43 | 414.1 | 37.6 | 57.1186 | 0 | 0 | 0 | 129.8 | 1161.3 | 153.7017
1041 | 208.1402 | 2.1 | 43.2 | 377 | 0 | 104.0701 | 0 | 0 | 0 | 138.4 | 503.7 | 135.3669
1042 | 273.3901 | 3.5 | 43.4 | 348.1 | 0 | 136.695 | 0 | 0 | 0 | 171.5 | 516.4 | 151.8136
1043 | 310.7175 | 3.5 | 43.4 | 295 | 0 | 155.3587 | 0 | 0 | 0 | 161.6 | 468.9 | 143.7063
1044 | 293.9209 | 2.8 | 43.3 | 251.3 | 0 | 146.9604 | 0 | 0 | 0 | 128.6 | 430 | 163.5181
1045 | 282.2334 | 1.4 | 43.1 | 208.3 | 75.1 | 141.1167 | 0 | 0 | 0 | 87.9 | 909.5 | 162.9802
1046 | 266.3238 | 2.1 | 43.2 | 190.2 | 37.6 | 133.1619 | 0 | 0 | 0 | 85.8 | 806.3 | 102.5808
1047 | 251.1237 | 3.5 | 43.4 | 173 | 0 | 125.5618 | 0 | 0 | 0 | 104.7 | 235.4 | 96.4683
1048 | 228.7671 | 2.8 | 43.3 | 156.2 | 0 | 114.3836 | 0 | 0 | 0 | 101 | 269 | 120.3101
1049 | 204.1958 | 2.1 | 43.2 | 149.4 | 0 | 102.0979 | 0 | 0 | 0 | 87.6 | 279 | 165.2697
1050 | 179.4588 | 0.7 | 43 | 170.6 | 37.6 | 89.7294 | 0 | 0 | 0 | 58.9 | 798.3 | 253.4076
1051 | 115.2884 | 0 | 42.9 | 133 | 75.1 | 57.6442 | 0 | 0 | 0 | 10.6 | 748.8 | 344.1733
1052 | 73.8502 | 0 | 42.9 | 107.7 | 75.1 | 36.9251 | 0 | 0 | 0 | 5 | 676.3 | 371.1687
1053 | 53.6913 | 0 | 42.9 | 133.2 | 75.1 | 26.8456 | 0 | 0 | 0 | 10.1 | 738.1 | 220.2393
1054 | 42.6484 | 0 | 42.9 | 153.6 | 93.9 | 21.3242 | 0 | 0 | 0 | 14.9 | 781.9 | 260.7942
1055 | 42.6602 | 0 | 0 | 46.4 | 0 | 21.3301 | 0 | 0 | 0 | 19.2 | 286.7 | 230.184
1056 | 42.2933 | 0 | 0 | 82.1 | 0 | 21.1466 | 0 | 0 | 0 | 23.5 | 390.9 | 242.3008
1057 | 39.9639 | 0 | 0 | 108 | 0 | 19.9819 | 0 | 0 | 0 | 28.6 | 438.6 | 130.1346
1058 | 40.4864 | 0 | 0 | 135.4 | 0 | 20.2432 | 0 | 0 | 0 | 34.9 | 494.5 | 89.9074
1059 | 40.669 | 0 | 0 | 162.3 | 0 | 20.3345 | 0 | 0 | 0 | 41.6 | 553.3 | 88.3638
1060 | 42.6915 | 0 | 0 | 183.6 | 0 | 21.3458 | 0 | 0 | 0 | 47.2 | 600.8 | 87.8832
1061 | 41.93 | 0 | 0 | 201.6 | 0 | 20.965 | 0 | 0 | 0 | 51.9 | 641.6 | 97.3117
1062 | 42.2052 | 0 | 0 | 217.4 | 0 | 21.1026 | 0 | 0 | 0 | 56.5 | 673.3 | 108.2454
1063 | 62.5703 | 0 | 42.9 | 406.2 | 56.3 | 31.2851 | 0 | 0 | 0 | 73.5 | 1266 | 103.6574
1064 | 115.8713 | 0.7 | 43 | 472.4 | 37.6 | 57.9357 | 0 | 0 | 0 | 142 | 1239.8 | 112.4808
1065 | 198.2549 | 2.1 | 43.2 | 442.3 | 0 | 99.1275 | 0 | 0 | 0 | 156.1 | 606.7 | 155.6677
1066 | 295.3245 | 3.5 | 43.4 | 425 | 0 | 147.6623 | 0 | 0 | 0 | 200.1 | 638 | 164.6632
1067 | 337.0943 | 3.5 | 43.4 | 382.6 | 0 | 168.5472 | 0 | 0 | 0 | 196.8 | 613.6 | 213.0839
1068 | 317.5915 | 2.8 | 43.3 | 328.3 | 0 | 158.7958 | 0 | 0 | 0 | 163.1 | 580 | 201.3757
1069 | 278.7142 | 1.4 | 43.1 | 277.9 | 75.1 | 139.3571 | 0 | 0 | 0 | 116.9 | 1084 | 165.3019
1070 | 277.994 | 2.1 | 43.2 | 253.7 | 37.6 | 138.997 | 0 | 0 | 0 | 121.1 | 940.2 | 140.2395
1071 | 279.8548 | 3.5 | 43.4 | 255.5 | 0 | 139.9274 | 0 | 0 | 0 | 165.1 | 375 | 200.6404
1072 | 270.836 | 2.8 | 43.3 | 245.7 | 0 | 135.418 | 0 | 0 | 0 | 163.4 | 434.9 | 146.3127
1073 | 263.6951 | 2.1 | 43.2 | 244.2 | 0 | 131.8475 | 0 | 0 | 0 | 129.2 | 470.8 | 174.2169
1074 | 259.2028 | 0.7 | 43 | 273.4 | 37.6 | 129.6014 | 0 | 0 | 0 | 83.9 | 1026.5 | 222.2099
1075 | 156.023 | 0 | 42.9 | 220.1 | 75.1 | 78.0115 | 0 | 0 | 0 | 31.1 | 999.4 | 231.9696
1076 | 77.665 | 0 | 42.9 | 194.7 | 75.1 | 38.8325 | 0 | 0 | 0 | 27 | 938.7 | 194.5687
1077 | 45.4015 | 0 | 42.9 | 227.1 | 75.1 | 22.7007 | 0 | 0 | 0 | 37.5 | 1012.7 | 182.7386
1078 | 42.1166 | 0 | 42.9 | 252.5 | 93.9 | 21.0583 | 0 | 0 | 0 | 45.4 | 1082.6 | 272.5072
1079 | 41.0433 | 0 | 0 | 130.9 | 0 | 20.5217 | 0 | 0 | 0 | 52.4 | 556.7 | 212.1759
1080 | 40.3575 | 0 | 0 | 162.2 | 0 | 20.1787 | 0 | 0 | 0 | 58.5 | 646.3 | 149.6922
1081 | 41.0474 | 0 | 0 | 178.1 | 0 | 20.5237 | 0 | 0 | 0 | 63.2 | 664.5 | 107.7651
1082 | 42.1947 | 0 | 0 | 195.3 | 0 | 21.0974 | 0 | 0 | 0 | 66.5 | 692.4 | 93.0047
1083 | 39.4327 | 0 | 0 | 210.6 | 0 | 19.7163 | 0 | 0 | 0 | 68.9 | 720.2 | 82.2016
1084 | 43.4198 | 0 | 0 | 224.1 | 0 | 21.7099 | 0 | 0 | 0 | 71.2 | 746.9 | 78.8845
1085 | 43.6132 | 0 | 0 | 235.2 | 0 | 21.8066 | 0 | 0 | 0 | 72.9 | 769.3 | 84.4486
1086 | 39.7085 | 0 | 0 | 245.6 | 0 | 19.8543 | 0 | 0 | 0 | 74.7 | 786.3 | 110.0552
1087 | 58.1086 | 0 | 42.9 | 434.4 | 56.3 | 29.0543 | 0 | 0 | 0 | 91.2 | 1382.1 | 141.5353
1088 | 99.0398 | 0.7 | 43 | 496.7 | 37.6 | 49.5199 | 0 | 0 | 0 | 164.3 | 1345.6 | 156.9454
1089 | 185.5295 | 2.1 | 43.2 | 456.3 | 0 | 92.7648 | 0 | 0 | 0 | 179.2 | 675.9 | 146.453
1090 | 314.3891 | 3.5 | 43.4 | 425.6 | 0 | 157.1946 | 0 | 0 | 0 | 229.8 | 685.2 | 128.4707
1091 | 362.0025 | 3.5 | 43.4 | 366.1 | 0 | 181.0012 | 0 | 0 | 0 | 221.9 | 635.3 | 175.9849
1092 | 340.7424 | 2.8 | 43.3 | 296 | 0 | 170.3712 | 0 | 0 | 0 | 172 | 578.6 | 206.9041
1093 | 346.6613 | 1.4 | 43.1 | 229.6 | 75.1 | 173.3307 | 0 | 0 | 0 | 111.7 | 1052.4 | 142.4339
1094 | 364.0616 | 2.1 | 43.2 | 188.1 | 37.6 | 182.0308 | 0 | 0 | 0 | 109.5 | 889.7 | 213.361
1095 | 385.8625 | 3.5 | 43.4 | 180.7 | 0 | 192.9313 | 0 | 0 | 0 | 138.9 | 311.8 | 173.8586
1096 | 378.3438 | 2.8 | 43.3 | 172.2 | 0 | 189.1719 | 0 | 0 | 0 | 136.5 | 362.6 | 310.6893
1097 | 299.5314 | 2.1 | 43.2 | 176.3 | 0 | 149.7657 | 0 | 0 | 0 | 113.5 | 396.6 | 247.2382
1098 | 199.0121 | 0.7 | 43 | 213.3 | 37.6 | 99.506 | 0 | 0 | 0 | 76.3 | 948.4 | 243.2203
1099 | 146.4653 | 0 | 42.9 | 166.4 | 75.1 | 73.2327 | 0 | 0 | 0 | 22.6 | 907.4 | 323.2958
1100 | 85.3815 | 0 | 42.9 | 137.4 | 75.1 | 42.6907 | 0 | 0 | 0 | 15.5 | 830.1 | 411.0214
1101 | 55.336 | 0 | 42.9 | 165.8 | 75.1 | 27.668 | 0 | 0 | 0 | 21.9 | 887.6 | 300.1821
1102 | 42.4467 | 0 | 42.9 | 188.4 | 93.9 | 21.2233 | 0 | 0 | 0 | 25.6 | 935.9 | 229.8849
1103 | 43.7288 | 0 | 0 | 65.3 | 0 | 21.8644 | 0 | 0 | 0 | 28.5 | 415.1 | 184.8178
1104 | 42.1141 | 0 | 0 | 103.1 | 0 | 21.0571 | 0 | 0 | 0 | 30.9 | 518.7 | 122.9654
1105 | 40.9553 | 0 | 0 | 126.5 | 0 | 20.4777 | 0 | 0 | 0 | 33.3 | 551.7 | 116.1133
1106 | 43.3176 | 0 | 0 | 144 | 0 | 21.6588 | 0 | 0 | 0 | 35.5 | 575.2 | 101.1438
1107 | 41.5411 | 0 | 0 | 159 | 0 | 20.7705 | 0 | 0 | 0 | 37.4 | 598.3 | 91.1
1108 | 40.6671 | 0 | 0 | 172.6 | 0 | 20.3336 | 0 | 0 | 0 | 38.8 | 622 | 86.6991
1109 | 43.5667 | 0 | 0 | 184 | 0 | 21.7834 | 0 | 0 | 0 | 39.8 | 642.2 | 110.6596
1110 | 39.6757 | 0 | 0 | 194 | 0 | 19.8378 | 0 | 0 | 0 | 40.5 | 656.6 | 95.7526
1111 | 53.3141 | 0 | 42.9 | 373.6 | 56.3 | 26.6571 | 0 | 0 | 0 | 54.3 | 1235 | 95.277
1112 | 80.9862 | 0.7 | 43 | 427.6 | 37.6 | 40.4931 | 0 | 0 | 0 | 116.2 | 1194.4 | 123.7221
1113 | 150.4014 | 2.1 | 43.2 | 388.3 | 0 | 75.2007 | 0 | 0 | 0 | 127.9 | 547.4 | 156.5113
1114 | 247.0603 | 3.5 | 43.4 | 340.1 | 0 | 123.5302 | 0 | 0 | 0 | 164.5 | 539.9 | 137.1977
1115 | 287.913 | 3.5 | 43.4 | 274.1 | 0 | 143.9565 | 0 | 0 | 0 | 163.6 | 476.5 | 180.3724
1116 | 282.6344 | 2.8 | 43.3 | 206.9 | 0 | 141.3172 | 0 | 0 | 0 | 136.2 | 412.2 | 166.7
1117 | 271.591 | 1.4 | 43.1 | 148.4 | 75.1 | 135.7955 | 0 | 0 | 0 | 95.8 | 844.8 | 154.9206
1118 | 233.0016 | 2.1 | 43.2 | 107.9 | 37.6 | 116.5008 | 0 | 0 | 0 | 99.1 | 698.3 | 147.9318
1119 | 226.4554 | 3.5 | 43.4 | 88.2 | 0 | 113.2277 | 0 | 0 | 0 | 127.2 | 152.9 | 145.9735
1120 | 240.4875 | 2.8 | 43.3 | 80.2 | 0 | 120.2437 | 0 | 0 | 0 | 125.8 | 190.4 | 98.037
1121 | 243.221 | 2.1 | 43.2 | 83.9 | 0 | 121.6105 | 0 | 0 | 0 | 105.8 | 215.9 | 106.5504
1122 | 173.0753 | 0.7 | 43 | 120.5 | 37.6 | 86.5376 | 0 | 0 | 0 | 68.2 | 737.6 | 156.3447
1123 | 92.8996 | 0 | 42.9 | 83.1 | 75.1 | 46.4498 | 0 | 0 | 0 | 17.2 | 672.8 | 220.4748
1124 | 76.584 | 0 | 42.9 | 52.6 | 75.1 | 38.292 | 0 | 0 | 0 | 11.4 | 588.9 | 367.7657
1125 | 61.2841 | 0 | 42.9 | 76 | 75.1 | 30.642 | 0 | 0 | 0 | 16.5 | 634.8 | 291.8564
1126 | 39.7237 | 0 | 42.9 | 93.2 | 93.9 | 19.8618 | 0 | 0 | 0 | 19.1 | 659.3 | 236.1086
1127 | 42.2985 | 0 | 0 | 0.4 | 0 | 21.1493 | 0 | 0 | 0 | 22.2 | 176 | 223.927
1128 | 41.8429 | 0 | 0 | 10.8 | 0 | 20.9215 | 0 | 0 | 0 | 24.9 | 256.5 | 155.1609
1129 | 41.754 | 0 | 0 | 26.6 | 0 | 20.877 | 0 | 0 | 0 | 27.6 | 285.5 | 106.9123
1130 | 43.0848 | 0 | 0 | 46.1 | 0 | 21.5424 | 0 | 0 | 0 | 29.7 | 312.7 | 106.3038
1131 | 41.7707 | 0 | 0 | 63.7 | 0 | 20.8854 | 0 | 0 | 0 | 31.1 | 339.1 | 94.0844
1132 | 39.7978 | 0 | 0 | 77.7 | 0 | 19.8989 | 0 | 0 | 0 | 33.1 | 359.9 | 77.6807
1133 | 41.2944 | 0 | 0 | 90 | 0 | 20.6472 | 0 | 0 | 0 | 34.5 | 379.4 | 85.6295
1134 | 42.5214 | 0 | 0 | 100.5 | 0 | 21.2607 | 0 | 0 | 0 | 35.3 | 393 | 117.1162
1135 | 45.0754 | 0 | 42.9 | 269.8 | 56.3 | 22.5377 | 0 | 0 | 0 | 48 | 937.8 | 112.1172
1136 | 62.8039 | 0 | 42.9 | 287 | 37.6 | 31.402 | 0 | 0 | 0 | 48.5 | 891.4 | 131.6781
1137 | 72.5088 | 0 | 42.9 | 276.5 | 0 | 36.2544 | 0 | 0 | 0 | 48.1 | 354 | 111.8719
1138 | 72.2051 | 0 | 42.9 | 272 | 0 | 36.1026 | 0 | 0 | 0 | 46.6 | 405.4 | 136.9432
1139 | 70.9372 | 0 | 42.9 | 253.9 | 0 | 35.4686 | 0 | 0 | 0 | 45.3 | 396.7 | 88.0075
1140 | 62.2783 | 0 | 42.9 | 232.2 | 0 | 31.1392 | 0 | 0 | 0 | 44.6 | 384.2 | 144.3212
1141 | 65.7085 | 0 | 42.9 | 217 | 75.1 | 32.8543 | 0 | 0 | 0 | 43.9 | 867.8 | 165.2597
1142 | 64.1205 | 0 | 42.9 | 203 | 37.6 | 32.0602 | 0 | 0 | 0 | 43.4 | 794.7 | 118.7011
1143 | 63.8152 | 0 | 42.9 | 204.8 | 0 | 31.9076 | 0 | 0 | 0 | 43.3 | 273.1 | 97.3146
1144 | 70.8024 | 0 | 42.9 | 201.2 | 0 | 35.4012 | 0 | 0 | 0 | 43.7 | 333 | 139.2839
1145 | 72.5832 | 0 | 42.9 | 206.2 | 0 | 36.2916 | 0 | 0 | 0 | 44.5 | 352.9 | 151.6507
1146 | 73.5741 | 0 | 42.9 | 213.2 | 37.6 | 36.787 | 0 | 0 | 0 | 45.7 | 863.4 | 136.449
1147 | 70.6639 | 0 | 42.9 | 185 | 75.1 | 35.3319 | 0 | 0 | 0 | 45.4 | 812.3 | 216.1228
1148 | 54.4277 | 0 | 42.9 | 153.4 | 75.1 | 27.2138 | 0 | 0 | 0 | 35.7 | 727.4 | 278.1447
1149 | 44.1655 | 0 | 42.9 | 168.2 | 75.1 | 22.0828 | 0 | 0 | 0 | 39.5 | 775.4 | 193.7785
1150 | 43.2906 | 0 | 42.9 | 178.6 | 93.9 | 21.6453 | 0 | 0 | 0 | 40.4 | 806 | 308.7711
1151 | 44.689 | 0 | 0 | 74.4 | 0 | 22.3445 | 0 | 0 | 0 | 42.4 | 291.1 | 309.2841
1152 | 43.1998 | 0 | 0 | 100.7 | 0 | 21.5999 | 0 | 0 | 0 | 43.8 | 380.4 | 204.9268
1153 | 42.2347 | 0 | 0 | 115.3 | 0 | 21.1173 | 0 | 0 | 0 | 45.5 | 411.6 | 108.7315
1154 | 42.4042 | 0 | 0 | 128.9 | 0 | 21.2021 | 0 | 0 | 0 | 47.5 | 442.2 | 79.5991
1155 | 41.5755 | 0 | 0 | 144.6 | 0 | 20.7877 | 0 | 0 | 0 | 49.3 | 479.5 | 76.6185
1156 | 40.827 | 0 | 0 | 153.8 | 0 | 20.4135 | 0 | 0 | 0 | 51 | 500.5 | 81.1365
1157 | 42.0903 | 0 | 0 | 160.2 | 0 | 21.0451 | 0 | 0 | 0 | 53 | 514.5 | 77.6869
1158 | 42.7836 | 0 | 0 | 167.6 | 0 | 21.3918 | 0 | 0 | 0 | 55.3 | 526.9 | 120.6119
1159 | 46.1056 | 0 | 42.9 | 341.1 | 56.3 | 23.0528 | 0 | 0 | 0 | 73.1 | 1102.1 | 101.2641
1160 | 51.6783 | 0 | 42.9 | 341.7 | 37.6 | 25.8392 | 0 | 0 | 0 | 75 | 1069.5 | 110.8987
1161 | 52.1671 | 0 | 42.9 | 324.7 | 0 | 26.0835 | 0 | 0 | 0 | 73.1 | 486.2 | 142.4789
1162 | 50.456 | 0 | 42.9 | 319.3 | 0 | 25.228 | 0 | 0 | 0 | 69.2 | 548.8 | 153.6327
1163 | 47.7981 | 0 | 42.9 | 314.5 | 0 | 23.8991 | 0 | 0 | 0 | 66.3 | 558.2 | 124.5519
1164 | 50.1439 | 0 | 42.9 | 310.6 | 0 | 25.072 | 0 | 0 | 0 | 63.2 | 567 | 148.921
1165 | 46.5389 | 0 | 42.9 | 314.6 | 75.1 | 23.2694 | 0 | 0 | 0 | 60.6 | 1147.3 | 187.6225
1166 | 48.5305 | 0 | 42.9 | 263.4 | 37.6 | 24.2652 | 0 | 0 | 0 | 59 | 1004 | 175.3519
1167 | 49.1825 | 0 | 42.9 | 240.1 | 0 | 24.5913 | 0 | 0 | 0 | 58.6 | 398.5 | 132.799
1168 | 49.3062 | 0 | 42.9 | 230.7 | 0 | 24.6531 | 0 | 0 | 0 | 58.8 | 446.1 | 159.2409
1169 | 50.7765 | 0 | 42.9 | 229.9 | 0 | 25.3882 | 0 | 0 | 0 | 60 | 451.8 | 92.2913
1170 | 54.3936 | 0 | 42.9 | 251.7 | 37.6 | 27.1968 | 0 | 0 | 0 | 61.9 | 991.4 | 124.679
1171 | 47.1274 | 0 | 42.9 | 239.5 | 75.1 | 23.5637 | 0 | 0 | 0 | 61.4 | 950 | 168.7442
1172 | 42.8703 | 0 | 42.9 | 198.3 | 75.1 | 21.4352 | 0 | 0 | 0 | 48.1 | 850.3 | 186.9467
1173 | 41.6015 | 0 | 42.9 | 208.6 | 75.1 | 20.8008 | 0 | 0 | 0 | 52.5 | 887.4 | 186.775
1174 | 42.7417 | 0 | 42.9 | 214 | 93.9 | 21.3709 | 0 | 0 | 0 | 54.1 | 908.7 | 186.5774
1175 | 44.2935 | 0 | 0 | 106.5 | 0 | 22.1468 | 0 | 0 | 0 | 55.7 | 359.3 | 183.1718
1176 | 42.5139 | 0 | 0 | 129.9 | 0 | 21.257 | 0 | 0 | 0 | 58 | 441 | 121.4927
1177 | 41.9827 | 0 | 0 | 137.8 | 0 | 20.9914 | 0 | 0 | 0 | 60.2 | 459 | 114.7757
1178 | 41.5718 | 0 | 0 | 144.3 | 0 | 20.7859 | 0 | 0 | 0 | 62.1 | 473.4 | 87.4071
1179 | 41.4983 | 0 | 0 | 149.2 | 0 | 20.7492 | 0 | 0 | 0 | 63.6 | 483.8 | 79.4764
1180 | 41.8817 | 0 | 0 | 153.7 | 0 | 20.9408 | 0 | 0 | 0 | 65.8 | 493.7 | 78.4076
1181 | 43.3476 | 0 | 0 | 157.4 | 0 | 21.6738 | 0 | 0 | 0 | 67.6 | 502.8 | 77.9278
1182 | 44.6809 | 0 | 0 | 160.8 | 0 | 22.3405 | 0 | 0 | 0 | 70.1 | 508.8 | 80.0699
1183 | 64.3886 | 0 | 42.9 | 332 | 56.3 | 32.1943 | 0 | 0 | 0 | 88.9 | 1099.1 | 104.3811
1184 | 108.524 | 0.7 | 43 | 383.8 | 37.6 | 54.262 | 0 | 0 | 0 | 158.9 | 1053.9 | 156.6766
1185 | 187.2198 | 2.1 | 43.2 | 372 | 0 | 93.6099 | 0 | 0 | 0 | 155.4 | 451.2 | 123.8944
1186 | 269.6028 | 3.5 | 43.4 | 370.1 | 0 | 134.8014 | 0 | 0 | 0 | 183.7 | 497.1 | 135.3157
1187 | 302.8637 | 3.5 | 43.4 | 343.4 | 0 | 151.4319 | 0 | 0 | 0 | 163.4 | 481.7 | 127.3082
1188 | 310.653 | 2.8 | 43.3 | 307.1 | 0 | 155.3265 | 0 | 0 | 0 | 121.6 | 459.1 | 147.6765
1189 | 282.9933 | 1.4 | 43.1 | 272.8 | 75.1 | 141.4967 | 0 | 0 | 0 | 78.8 | 983 | 170.044
1190 | 254.9546 | 2.1 | 43.2 | 256 | 37.6 | 127.4773 | 0 | 0 | 0 | 69.9 | 889.8 | 94.6815
1191 | 250.8448 | 3.5 | 43.4 | 257.9 | 0 | 125.4224 | 0 | 0 | 0 | 88.1 | 321.5 | 134.1446
1192 | 245.1651 | 2.8 | 43.3 | 254.2 | 0 | 122.5826 | 0 | 0 | 0 | 86.5 | 380.1 | 141.5022
1193 | 240.4323 | 2.1 | 43.2 | 247.4 | 0 | 120.2161 | 0 | 0 | 0 | 77.1 | 395 | 183.9111
1194 | 206.8962 | 0.7 | 43 | 254.2 | 37.6 | 103.4481 | 0 | 0 | 0 | 53.8 | 953.3 | 147.0645
1195 | 144.8804 | 0 | 42.9 | 194.8 | 75.1 | 72.4402 | 0 | 0 | 0 | 5.8 | 892.1 | 157.5459
1196 | 100.6259 | 0 | 42.9 | 162.6 | 75.1 | 50.313 | 0 | 0 | 0 | 3.1 | 792 | 198.7578
1197 | 66.9885 | 0 | 42.9 | 177.8 | 75.1 | 33.4943 | 0 | 0 | 0 | 5.3 | 836.3 | 221.3321
1198 | 40.5515 | 0 | 42.9 | 186.8 | 93.9 | 20.2757 | 0 | 0 | 0 | 7.9 | 859.9 | 203.6498
1199 | 42.3292 | 0 | 0 | 83.2 | 0 | 21.1646 | 0 | 0 | 0 | 12.2 | 321 | 170.9055
1200 | 43.2906 | 0 | 0 | 109.9 | 0 | 21.6453 | 0 | 0 | 0 | 16 | 410.1 | 146.1768
1201 | 41.8733 | 0 | 0 | 124.7 | 0 | 20.9367 | 0 | 0 | 0 | 19.5 | 442.3 | 105.701
1202 | 43.2503 | 0 | 0 | 139.6 | 0 | 21.6252 | 0 | 0 | 0 | 22.9 | 475.4 | 86.9384
1203 | 43.1645 | 0 | 0 | 154.4 | 0 | 21.5822 | 0 | 0 | 0 | 26.1 | 508.9 | 85.2773
1204 | 40.3268 | 0 | 0 | 165.6 | 0 | 20.1634 | 0 | 0 | 0 | 28.9 | 533.9 | 76.0309
1205 | 41.4252 | 0 | 0 | 175.1 | 0 | 20.7126 | 0 | 0 | 0 | 31.3 | 557 | 78.6498
1206 | 42.5533 | 0 | 0 | 184 | 0 | 21.2766 | 0 | 0 | 0 | 33.6 | 575.7 | 123.6465
1207 | 55.2883 | 0 | 42.9 | 363.7 | 56.3 | 27.6442 | 0 | 0 | 0 | 48.2 | 1183.5 | 118.8923
1208 | 91.9757 | 0.7 | 43 | 415.2 | 37.6 | 45.9879 | 0 | 0 | 0 | 106.6 | 1130.9 | 117.0818
1209 | 167.0541 | 2.1 | 43.2 | 362.5 | 0 | 83.5271 | 0 | 0 | 0 | 115.7 | 465.8 | 104.3794
1210 | 259.3128 | 3.5 | 43.4 | 309.2 | 0 | 129.6564 | 0 | 0 | 0 | 140 | 456.1 | 107.5152
1211 | 316.2192 | 3.5 | 43.4 | 244.4 | 0 | 158.1096 | 0 | 0 | 0 | 130.8 | 398.1 | 237.067
1212 | 316.7783 | 2.8 | 43.3 | 177.4 | 0 | 158.3891 | 0 | 0 | 0 | 100.3 | 336 | 97.073
1213 | 305.5566 | 1.4 | 43.1 | 115.6 | 75.1 | 152.7783 | 0 | 0 | 0 | 62.7 | 745.2 | 147.0626
1214 | 273.1762 | 2.1 | 43.2 | 72.6 | 37.6 | 136.5881 | 0 | 0 | 0 | 59.7 | 600.6 | 131.1545
1215 | 262.0652 | 3.5 | 43.4 | 48.9 | 0 | 131.0326 | 0 | 0 | 0 | 76.8 | 74.7 | 136.9487
1216 | 247.6154 | 2.8 | 43.3 | 38.7 | 0 | 123.8077 | 0 | 0 | 0 | 77.6 | 91.9 | 127.5241
1217 | 232.7608 | 2.1 | 43.2 | 43.8 | 0 | 116.3804 | 0 | 0 | 0 | 67.8 | 115.4 | 210.7892
1218 | 231.4724 | 0.7 | 43 | 83.1 | 37.6 | 115.7362 | 0 | 0 | 0 | 47 | 623.6 | 349.0214
1219 | 145.9159 | 0 | 42.9 | 51.6 | 75.1 | 72.9579 | 0 | 0 | 0 | 2.3 | 554.8 | 238.5394
1220 | 85.1419 | 0 | 42.9 | 27.9 | 75.1 | 42.571 | 0 | 0 | 0 | 0.1 | 483.9 | 187.2408
1221 | 57.5356 | 0 | 42.9 | 52.9 | 75.1 | 28.7678 | 0 | 0 | 0 | 1.3 | 537.7 | 164.084
1222 | 41.4621 | 0 | 42.9 | 73.7 | 93.9 | 20.731 | 0 | 0 | 0 | 2.3 | 568.6 | 170.4145
1223 | 40.3305 | 0 | 0 | 0 | 0 | 20.1653 | 0 | 0 | 0 | 3.2 | 114.5 | 181.3116
1224 | 41.6604 | 0 | 0 | 4.2 | 0 | 20.8302 | 0 | 0 | 0 | 4.3 | 191.9 | 143.3114
1225 | 41.4971 | 0 | 0 | 17.7 | 0 | 20.7485 | 0 | 0 | 0 | 6.4 | 226.3 | 107.03
1226 | 43.1294 | 0 | 0 | 35.6 | 0 | 21.5647 | 0 | 0 | 0 | 9.5 | 256.2 | 90.858
1227 | 43.0984 | 0 | 0 | 53.8 | 0 | 21.5492 | 0 | 0 | 0 | 12.3 | 284.3 | 89.7863
1228 | 41.2138 | 0 | 0 | 69.3 | 0 | 20.6069 | 0 | 0 | 0 | 14.5 | 309.1 | 83.9675
1229 | 42.7365 | 0 | 0 | 81.9 | 0 | 21.3682 | 0 | 0 | 0 | 16.8 | 329.5 | 79.7163
1230 | 42.7485 | 0 | 0 | 92.6 | 0 | 21.3743 | 0 | 0 | 0 | 18.9 | 343 | 82.9146
1231 | 56.7849 | 0 | 42.9 | 262.9 | 56.3 | 28.3925 | 0 | 0 | 0 | 32.3 | 874.5 | 152.1789
1232 | 82.3024 | 0.7 | 43 | 300.4 | 37.6 | 41.1512 | 0 | 0 | 0 | 84 | 820.4 | 130.098
1233 | 148.3664 | 2.1 | 43.2 | 248.7 | 0 | 74.1832 | 0 | 0 | 0 | 90.4 | 253.9 | 111.997
1234 | 285.7953 | 3.5 | 43.4 | 198.2 | 0 | 142.8977 | 0 | 0 | 0 | 105.2 | 242.4 | 120.9139
1235 | 317.695 | 3.5 | 43.4 | 142 | 0 | 158.8475 | 0 | 0 | 0 | 93.9 | 184.3 | 214.4357
1236 | 324.337 | 2.8 | 43.3 | 79.7 | 0 | 162.1685 | 0 | 0 | 0 | 70 | 122.8 | 231.1857
1237 | 305.1218 | 1.4 | 43.1 | 27 | 75.1 | 152.5609 | 0 | 0 | 0 | 42.4 | 494.5 | 105.2205
1238 | 291.4638 | 2.1 | 43.2 | 7.5 | 37.6 | 145.7319 | 0 | 0 | 0 | 37.6 | 360.8 | 151.6586
1239 | 301.3045 | 3.5 | 43.4 | 2.4 | 0 | 150.6522 | 0 | 0 | 0 | 46.2 | 4.7 | 162.0123
1240 | 269.0103 | 2.8 | 43.3 | 0.1 | 0 | 134.5051 | 0 | 0 | 0 | 44.4 | 4.4 | 128.7569
1241 | 235.4683 | 2.1 | 43.2 | 0.5 | 0 | 117.7341 | 0 | 0 | 0 | 39.4 | 3.9 | 114.167
1242 | 218.041 | 0.7 | 43 | 7.1 | 37.6 | 109.0205 | 0 | 0 | 0 | 30.1 | 382.7 | 140.2568
1243 | 107.1452 | 0 | 42.9 | 2.8 | 75.1 | 53.5726 | 0 | 0 | 0 | 0 | 340.1 | 236.3066
1244 | 69.1539 | 0 | 42.9 | 0 | 75.1 | 34.577 | 0 | 0 | 0 | 0 | 290.9 | 221.4679
1245 | 59.6285 | 0 | 42.9 | 0.2 | 75.1 | 29.8142 | 0 | 0 | 0 | 0 | 342.9 | 216.9193
1246 | 42.2226 | 0 | 42.9 | 5.1 | 93.9 | 21.1113 | 0 | 0 | 0 | 0 | 371.1 | 239.7753
1247 | 43.6582 | 0 | 0 | 0 | 0 | 21.8291 | 0 | 0 | 0 | 0 | 4.7 | 166.1371
1248 | 39.0732 | 0 | 0 | 0 | 0 | 19.5366 | 0 | 0 | 0 | 0 | 15.2 | 118.7806
1249 | 39.0577 | 0 | 0 | 0 | 0 | 19.5288 | 0 | 0 | 0 | 0 | 36.1 | 93.6036
1250 | 43.7428 | 0 | 0 | 0 | 0 | 21.8714 | 0 | 0 | 0 | 0 | 75.2 | 86.3436
1251 | 39.892 | 0 | 0 | 0 | 0 | 19.946 | 0 | 0 | 0 | 0.5 | 113.2 | 81.137
1252 | 39.7184 | 0 | 0 | 3.9 | 0 | 19.8592 | 0 | 0 | 0 | 1.4 | 144.6 | 76.8561
1253 | 38.9396 | 0 | 0 | 12 | 0 | 19.4698 | 0 | 0 | 0 | 2.2 | 172.7 | 75.3264
1254 | 41.8411 | 0 | 0 | 26.2 | 0 | 20.9205 | 0 | 0 | 0 | 3.7 | 193.1 | 90.9812
1255 | 60.6128 | 0 | 42.9 | 203.9 | 56.3 | 30.3064 | 0 | 0 | 0 | 20.1 | 705.5 | 134.3998
1256 | 93.9673 | 0.7 | 43 | 232 | 37.6 | 46.9836 | 0 | 0 | 0 | 69.6 | 647.9 | 262.759
1257 | 168.7466 | 2.1 | 43.2 | 209.7 | 0 | 84.3733 | 0 | 0 | 0 | 73.2 | 165.5 | 325.8123
1258 | 250.4285 | 3.5 | 43.4 | 187.4 | 0 | 125.2143 | 0 | 0 | 0 | 82.1 | 184.1 | 183.6976
1259 | 256.1494 | 3.5 | 43.4 | 160.6 | 0 | 128.0747 | 0 | 0 | 0 | 59.5 | 160.5 | 97.5526
1260 | 238.8043 | 2.8 | 43.3 | 133.8 | 0 | 119.4021 | 0 | 0 | 0 | 36.5 | 137.3 | 152.1662
1261 | 229.2212 | 1.4 | 43.1 | 100 | 75.1 | 114.6106 | 0 | 0 | 0 | 25.1 | 534.2 | 160.5599
1262 | 214.0876 | 2.1 | 43.2 | 64.5 | 37.6 | 107.0438 | 0 | 0 | 0 | 21.9 | 409.4 | 202.4801
1263 | 208.4997 | 3.5 | 43.4 | 31.4 | 0 | 104.2499 | 0 | 0 | 0 | 32 | 4.5 | 123.7408
1264 | 198.506 | 2.8 | 43.3 | 6.7 | 0 | 99.253 | 0 | 0 | 0 | 31.2 | 2.2 | 112.8417
1265 | 178.4084 | 2.1 | 43.2 | 3.8 | 0 | 89.2042 | 0 | 0 | 0 | 19.9 | 1 | 176.7938
1266 | 127.4138 | 0.7 | 43 | 11.5 | 37.6 | 63.7069 | 0 | 0 | 0 | 13.7 | 381.5 | 178.6601
1267 | 80.3614 | 0 | 42.9 | 4 | 75.1 | 40.1807 | 0 | 0 | 0 | 0 | 327.1 | 213.4384
1268 | 51.7406 | 0 | 42.9 | 0 | 75.1 | 25.8703 | 0 | 0 | 0 | 0 | 275.6 | 195.3635
1269 | 43.3014 | 0 | 42.9 | 1.2 | 75.1 | 21.6507 | 0 | 0 | 0 | 0 | 330 | 247.19
1270 | 40.7421 | 0 | 42.9 | 12.6 | 93.9 | 20.3711 | 0 | 0 | 0 | 0 | 360.2 | 315.0021
1271 | 42.4724 | 0 | 0 | 0 | 0 | 21.2362 | 0 | 0 | 0 | 0 | 2.1 | 195.45
1272 | 38.4589 | 0 | 0 | 0 | 0 | 19.2295 | 0 | 0 | 0 | 0 | 13.8 | 157.9686
1273 | 41.1236 | 0 | 0 | 0 | 0 | 20.5618 | 0 | 0 | 0 | 0 | 37.5 | 129.7523
1274 | 40.4288 | 0 | 0 | 0 | 0 | 20.2144 | 0 | 0 | 0 | 0.1 | 76.4 | 103.5383
1275 | 44.1066 | 0 | 0 | 3.1 | 0 | 22.0533 | 0 | 0 | 0 | 2.6 | 114.6 | 84.8089
1276 | 41.7363 | 0 | 0 | 9.3 | 0 | 20.8682 | 0 | 0 | 0 | 8.7 | 145.6 | 86.936
1277 | 41.9843 | 0 | 0 | 22 | 0 | 20.9921 | 0 | 0 | 0 | 15.5 | 175.8 | 80.6589
1278 | 43.868 | 0 | 0 | 36.2 | 0 | 21.934 | 0 | 0 | 0 | 21.1 | 194.9 | 93.1231
1279 | 68.8068 | 0 | 42.9 | 210.9 | 56.3 | 34.4034 | 0 | 0 | 0 | 41.3 | 703.3 | 141.7168
1280 | 101.7906 | 0.7 | 43 | 242.4 | 37.6 | 50.8953 | 0 | 0 | 0 | 94.6 | 650.5 | 143.2663
1281 | 186.0387 | 2.1 | 43.2 | 238.3 | 0 | 93.0194 | 0 | 0 | 0 | 96.8 | 194.7 | 145.3988
1282 | 291.1189 | 3.5 | 43.4 | 244.4 | 0 | 145.5594 | 0 | 0 | 0 | 113.2 | 252.9 | 131.2832
1283 | 332.0513 | 3.5 | 43.4 | 239.2 | 0 | 166.0256 | 0 | 0 | 0 | 92.9 | 260.7 | 209.0527
1284 | 279.1274 | 2.8 | 43.3 | 228.9 | 0 | 139.5637 | 0 | 0 | 0 | 55.4 | 267.9 | 191.7431
1285 | 256.7541 | 1.4 | 43.1 | 216.8 | 75.1 | 128.377 | 0 | 0 | 0 | 16 | 741.2 | 192.1352
1286 | 251.632 | 2.1 | 43.2 | 214.9 | 37.6 | 125.816 | 0 | 0 | 0 | 5.3 | 668.9 | 118.7599
1287 | 252.3758 | 3.5 | 43.4 | 224.8 | 0 | 126.1879 | 0 | 0 | 0 | 10 | 201 | 121.5727
1288 | 241.6385 | 2.8 | 43.3 | 221.5 | 0 | 120.8193 | 0 | 0 | 0 | 6.6 | 265.2 | 119.1379
1289 | 225.7373 | 2.1 | 43.2 | 213.8 | 0 | 112.8687 | 0 | 0 | 0 | 4.5 | 283 | 241.1063
1290 | 186.887 | 0.7 | 43 | 212.1 | 37.6 | 93.4435 | 0 | 0 | 0 | 2.2 | 769.9 | 124.5893
1291 | 103.8175 | 0 | 42.9 | 161.9 | 75.1 | 51.9088 | 0 | 0 | 0 | 0 | 706.9 | 239.9211
1292 | 72.3954 | 0 | 42.9 | 144.5 | 75.1 | 36.1977 | 0 | 0 | 0 | 0 | 656.6 | 265.2568
1293 | 48.8683 | 0 | 42.9 | 156.6 | 75.1 | 24.4341 | 0 | 0 | 0 | 0 | 701.6 | 286.8552
1294 | 43.705 | 0 | 42.9 | 162.6 | 93.9 | 21.8525 | 0 | 0 | 0 | 0 | 723.7 | 174.4585
1295 | 42.1848 | 0 | 0 | 57 | 0 | 21.0924 | 0 | 0 | 0 | 0 | 236.5 | 210.0832
1296 | 40.5571 | 0 | 0 | 80.9 | 0 | 20.2785 | 0 | 0 | 0 | 0 | 321.2 | 167.5093
1297 | 39.3378 | 0 | 0 | 91.1 | 0 | 19.6689 | 0 | 0 | 0 | 0 | 340.3 | 104.7444
1298 | 41.8594 | 0 | 0 | 101.8 | 0 | 20.9297 | 0 | 0 | 0 | 0 | 362.5 | 87.4077
1299 | 43.2497 | 0 | 0 | 112.3 | 0 | 21.6248 | 0 | 0 | 0 | 0 | 385.7 | 81.255
1300 | 41.7239 | 0 | 0 | 120.6 | 0 | 20.862 | 0 | 0 | 0 | 0 | 404.3 | 78.6469
1301 | 40.3649 | 0 | 0 | 127.6 | 0 | 20.1825 | 0 | 0 | 0 | 0 | 420.4 | 79.3593
1302 | 44.0236 | 0 | 0 | 133.5 | 0 | 22.0118 | 0 | 0 | 0 | 0 | 429.4 | 79.3598
1303 | 51.378 | 0 | 42.9 | 300 | 56.3 | 25.689 | 0 | 0 | 0 | 8.6 | 974.4 | 104.7419
1304 | 74.9365 | 0 | 42.9 | 322.6 | 37.6 | 37.4682 | 0 | 0 | 0 | 14.5 | 940.2 | 185.4432
1305 | 77.0793 | 0 | 42.9 | 314.2 | 0 | 38.5396 | 0 | 0 | 0 | 13.9 | 388.8 | 149.0137
1306 | 78.8226 | 0 | 42.9 | 313.5 | 0 | 39.4113 | 0 | 0 | 0 | 9.9 | 444.8 | 102.0997
1307 | 72.1651 | 0 | 42.9 | 283.4 | 0 | 36.0826 | 0 | 0 | 0 | 5.1 | 423.7 | 143.2968
1308 | 71.4861 | 0 | 42.9 | 240.7 | 0 | 35.7431 | 0 | 0 | 0 | 2 | 388.5 | 193.8344
1309 | 70.0853 | 0 | 42.9 | 180.1 | 75.1 | 35.0426 | 0 | 0 | 0 | 0.8 | 807.7 | 316.3176
1310 | 64.9709 | 0 | 42.9 | 148.8 | 37.6 | 32.4855 | 0 | 0 | 0 | 0.2 | 694.9 | 212.4549
1311 | 57.6034 | 0 | 42.9 | 141.5 | 0 | 28.8017 | 0 | 0 | 0 | 0 | 178.3 | 316.7236
1312 | 58.3228 | 0 | 42.9 | 131.2 | 0 | 29.1614 | 0 | 0 | 0 | 0 | 216.8 | 169.4093
1313 | 58.2056 | 0 | 42.9 | 128.8 | 0 | 29.1028 | 0 | 0 | 0 | 0.5 | 222.7 | 158.6192
1314 | 78.1984 | 0 | 42.9 | 141.9 | 37.6 | 39.0992 | 0 | 0 | 0 | 1.2 | 712.1 | 232.4982
1315 | 74.621 | 0 | 42.9 | 130.2 | 75.1 | 37.3105 | 0 | 0 | 0 | 2.8 | 659.5 | 383.7486
1316 | 61.5342 | 0 | 42.9 | 98.2 | 75.1 | 30.7671 | 0 | 0 | 0 | 0 | 578.1 | 305.1509
1317 | 47.861 | 0 | 42.9 | 112.9 | 75.1 | 23.9305 | 0 | 0 | 0 | 0.3 | 620.9 | 278.6253
1318 | 42.8369 | 0 | 42.9 | 122.4 | 93.9 | 21.4184 | 0 | 0 | 0 | 2.4 | 640.9 | 208.0798
1319 | 39.4392 | 0 | 0 | 16 | 0 | 19.7196 | 0 | 0 | 0 | 6.6 | 157.6 | 167.2233
1320 | 41.8033 | 0 | 0 | 37.6 | 0 | 20.9016 | 0 | 0 | 0 | 10.8 | 232.9 | 129.5893
1321 | 40.3377 | 0 | 0 | 53.7 | 0 | 20.1688 | 0 | 0 | 0 | 15.6 | 261.1 | 95.0368
1322 | 40.2205 | 0 | 0 | 68.4 | 0 | 20.1103 | 0 | 0 | 0 | 21 | 288.7 | 90.5025
1323 | 43.5519 | 0 | 0 | 81.6 | 0 | 21.7759 | 0 | 0 | 0 | 26.9 | 314.7 | 84.5659
1324 | 44.3223 | 0 | 0 | 92.1 | 0 | 22.1612 | 0 | 0 | 0 | 32.1 | 335.5 | 82.2005
1325 | 41.2426 | 0 | 0 | 100.7 | 0 | 20.6213 | 0 | 0 | 0 | 36.1 | 353.1 | 85.9819
1326 | 43.1536 | 0 | 0 | 107.9 | 0 | 21.5768 | 0 | 0 | 0 | 38.9 | 364.2 | 129.0663
1327 | 46.8076 | 0 | 42.9 | 272.3 | 56.3 | 23.4038 | 0 | 0 | 0 | 51.9 | 905 | 104.7436
1328 | 69.4577 | 0 | 42.9 | 267.7 | 37.6 | 34.7288 | 0 | 0 | 0 | 50 | 868 | 159.1571
1329 | 70.6977 | 0 | 42.9 | 253 | 0 | 35.3488 | 0 | 0 | 0 | 36.8 | 334.6 | 150.1282
1330 | 65.0543 | 0 | 42.9 | 243.3 | 0 | 32.5271 | 0 | 0 | 0 | 23.5 | 385.3 | 138.9116
1331 | 58.2884 | 0 | 42.9 | 231.7 | 0 | 29.1442 | 0 | 0 | 0 | 13.3 | 379.7 | 137.9247
1332 | 58.1222 | 0 | 42.9 | 221.4 | 0 | 29.0611 | 0 | 0 | 0 | 2.5 | 375 | 202.2121
1333 | 57.5188 | 0 | 42.9 | 219.6 | 75.1 | 28.7594 | 0 | 0 | 0 | 0 | 868.1 | 135.8839
1334 | 56.5984 | 0 | 42.9 | 204.8 | 37.6 | 28.2992 | 0 | 0 | 0 | 0 | 804 | 105.8194
1335 | 54.1729 | 0 | 42.9 | 201.9 | 0 | 27.0865 | 0 | 0 | 0 | 0 | 281.1 | 126.1906
1336 | 55.7532 | 0 | 42.9 | 201.7 | 0 | 27.8766 | 0 | 0 | 0 | 0 | 341 | 163.8583
1337 | 55.2455 | 0 | 42.9 | 205.3 | 0 | 27.6228 | 0 | 0 | 0 | 0 | 353.6 | 220.754
1338 | 71.8465 | 0 | 42.9 | 217.1 | 37.6 | 35.9233 | 0 | 0 | 0 | 0 | 862.2 | 313.4872
1339 | 69.7031 | 0 | 42.9 | 210.1 | 75.1 | 34.8516 | 0 | 0 | 0 | 0 | 819 | 194.8002
1340 | 52.4544 | 0 | 42.9 | 170.3 | 75.1 | 26.2272 | 0 | 0 | 0 | 0 | 731.8 | 215.4921
1341 | 45.0572 | 0 | 42.9 | 184.4 | 75.1 | 22.5286 | 0 | 0 | 0 | 0 | 780.6 | 210.1357
1342 | 41.8783 | 0 | 42.9 | 199.9 | 93.9 | 20.9391 | 0 | 0 | 0 | 0 | 827.7 | 202.741
1343 | 41.1977 | 0 | 0 | 97.9 | 0 | 20.5988 | 0 | 0 | 0 | 0 | 307.4 | 179.4866
1344 | 42.261 | 0 | 0 | 121.2 | 0 | 21.1305 | 0 | 0 | 0 | 0.6 | 388.4 | 145.0225
1345 | 41.3681 | 0 | 0 | 131.5 | 0 | 20.6841 | 0 | 0 | 0 | 2 | 414.5 | 98.1546
1346 | 42.7724 | 0 | 0 | 142.9 | 0 | 21.3862 | 0 | 0 | 0 | 3.1 | 443.4 | 85.1593
1347 | 41.4766 | 0 | 0 | 154.1 | 0 | 20.7383 | 0 | 0 | 0 | 5.6 | 472.6 | 84.3247
1348 | 43.8252 | 0 | 0 | 162.7 | 0 | 21.9126 | 0 | 0 | 0 | 9.5 | 494.5 | 80.1887
1349 | 41.5402 | 0 | 0 | 170.9 | 0 | 20.7701 | 0 | 0 | 0 | 13 | 515.8 | 81.8433
1350 | 42.068 | 0 | 0 | 177.3 | 0 | 21.034 | 0 | 0 | 0 | 15.7 | 528.3 | 112.2403
1351 | 55.6568 | 0 | 42.9 | 352 | 56.3 | 27.8284 | 0 | 0 | 0 | 32 | 1105.7 | 103.1805
1352 | 75.4004 | 0.7 | 43 | 407.5 | 37.6 | 37.7002 | 0 | 0 | 0 | 84.3 | 1067.1 | 165.9414
1353 | 123.1012 | 2.1 | 43.2 | 387.6 | 0 | 61.5506 | 0 | 0 | 0 | 97.7 | 460.3 | 139.6421
1354 | 195.3658 | 3.5 | 43.4 | 372.4 | 0 | 97.6829 | 0 | 0 | 0 | 129.2 | 488.8 | 152.8469
1355 | 253.6099 | 3.5 | 43.4 | 330.1 | 0 | 126.8049 | 0 | 0 | 0 | 132.4 | 454.8 | 157.3423
1356 | 260.7239 | 2.8 | 43.3 | 285 | 0 | 130.3619 | 0 | 0 | 0 | 111.8 | 421.6 | 242.35
1357 | 218.5158 | 1.4 | 43.1 | 248.1 | 75.1 | 109.2579 | 0 | 0 | 0 | 79 | 913.5 | 317.5447
1358 | 179.1671 | 2.1 | 43.2 | 223.5 | 37.6 | 89.5836 | 0 | 0 | 0 | 83.2 | 809.3 | 308.0261
1359 | 183.6517 | 3.5 | 43.4 | 217 | 0 | 91.8259 | 0 | 0 | 0 | 112.4 | 259.7 | 170.517
1360 | 156.6506 | 2.8 | 43.3 | 207.2 | 0 | 78.3253 | 0 | 0 | 0 | 113 | 307.6 | 193.248
1361 | 144.2618 | 2.1 | 43.2 | 199.3 | 0 | 72.1309 | 0 | 0 | 0 | 92.4 | 318.4 | 201.2203
1362 | 134.2956 | 0.7 | 43 | 205 | 37.6 | 67.1478 | 0 | 0 | 0 | 56.5 | 824.8 | 195.6099
1363 | 98.8092 | 0 | 42.9 | 167.8 | 75.1 | 49.4046 | 0 | 0 | 0 | 8 | 785.5 | 285.6997
1364 | 63.0692 | 0 | 42.9 | 139.1 | 75.1 | 31.5346 | 0 | 0 | 0 | 2.3 | 705.6 | 170.8711
1365 | 46.4397 | 0 | 42.9 | 156.4 | 75.1 | 23.2199 | 0 | 0 | 0 | 4.4 | 753.6 | 179.5686
1366 | 43.1533 | 0 | 42.9 | 169 | 93.9 | 21.5766 | 0 | 0 | 0 | 8.8 | 784.2 | 179.6805
1367 | 43.4071 | 0 | 0 | 58.2 | 0 | 21.7036 | 0 | 0 | 0 | 14.3 | 275.7 | 172.5417
1368 | 41.772 | 0 | 0 | 87 | 0 | 20.886 | 0 | 0 | 0 | 17.1 | 366.6 | 142.6221
1369 | 42.9605 | 0 | 0 | 103.3 | 0 | 21.4803 | 0 | 0 | 0 | 18.3 | 395.9 | 104.8611
1370 | 44.0536 | 0 | 0 | 117 | 0 | 22.0268 | 0 | 0 | 0 | 19.6 | 421.1 | 90.144
1371 | 42.1733 | 0 | 0 | 129.1 | 0 | 21.0867 | 0 | 0 | 0 | 21.8 | 445.4 | 88.0033
1372 | 41.4689 | 0 | 0 | 139.3 | 0 | 20.7344 | 0 | 0 | 0 | 23.5 | 467 | 78.7654
1373 | 44.8452 | 0 | 0 | 147.3 | 0 | 22.4226 | 0 | 0 | 0 | 25.4 | 484.3 | 80.304
1374 | 40.1548 | 0 | 0 | 154.2 | 0 | 20.0774 | 0 | 0 | 0 | 26.7 | 494.7 | 110.6606
1375 | 60.9624 | 0 | 42.9 | 325.8 | 56.3 | 30.4812 | 0 | 0 | 0 | 38.8 | 1053.3 | 132.4954
1376 | 94.9841 | 0.7 | 43 | 371 | 37.6 | 47.4921 | 0 | 0 | 0 | 92.3 | 1010 | 143.0533
1377 | 134.8684 | 2.1 | 43.2 | 316.8 | 0 | 67.4342 | 0 | 0 | 0 | 103.2 | 377.4 | 123.1558
1378 | 180.5887 | 3.5 | 43.4 | 251.9 | 0 | 90.2944 | 0 | 0 | 0 | 129.4 | 353.8 | 131.0198
1379 | 225.2972 | 3.5 | 43.4 | 182 | 0 | 112.6486 | 0 | 0 | 0 | 127.5 | 283.6 | 135.1211
1380 | 222.7317 | 2.8 | 43.3 | 112.4 | 0 | 111.3658 | 0 | 0 | 0 | 107.7 | 212.7 | 154.4049
1381 | 224.6944 | 1.4 | 43.1 | 50.1 | 75.1 | 112.3472 | 0 | 0 | 0 | 73.2 | 586.3 | 209.1428
1382 | 215.645 | 2.1 | 43.2 | 16.1 | 37.6 | 107.8225 | 0 | 0 | 0 | 52.2 | 439.8 | 157.1061
1383 | 222.8479 | 3.5 | 43.4 | 7.6 | 0 | 111.424 | 0 | 0 | 0 | 49.5 | 10.2 | 221.6149
1384 | 216.2165 | 2.8 | 43.3 | 5.2 | 0 | 108.1083 | 0 | 0 | 0 | 36.2 | 10.6 | 148.1611
1385 | 215.0314 | 2.1 | 43.2 | 5.5 | 0 | 107.5157 | 0 | 0 | 0 | 24 | 9.8 | 193.261
1386 | 212.1045 | 0.7 | 43 | 12.6 | 37.6 | 106.0522 | 0 | 0 | 0 | 14.2 | 442.2 | 183.9331
1387 | 156.3866 | 0 | 42.9 | 9.2 | 75.1 | 78.1933 | 0 | 0 | 0 | 0 | 396.1 | 421.7714
1388 | 93.3645 | 0 | 42.9 | 2 | 75.1 | 46.6822 | 0 | 0 | 0 | 0 | 347.4 | 273.4483
1389 | 62.693 | 0 | 42.9 | 8.6 | 75.1 | 31.3465 | 0 | 0 | 0 | 0 | 404.8 | 297.9407
1390 | 41.9657 | 0 | 42.9 | 21.8 | 93.9 | 20.9828 | 0 | 0 | 0 | 0 | 439.4 | 206.4407
1391 | 40.9842 | 0 | 0 | 0 | 0 | 20.4921 | 0 | 0 | 0 | 0 | 21.8 | 195.6484
1392 | 42.4736 | 0 | 0 | 0 | 0 | 21.2368 | 0 | 0 | 0 | 0 | 76.4 | 247.138
1393 | 40.571 | 0 | 0 | 0 | 0 | 20.2855 | 0 | 0 | 0 | 0 | 121.8 | 92.768
1394 | 42.0091 | 0 | 0 | 3 | 0 | 21.0045 | 0 | 0 | 0 | 0.1 | 167.3 | 91.9397
1395 | 42.3807 | 0 | 0 | 19.6 | 0 | 21.1903 | 0 | 0 | 0 | 1.6 | 212.7 | 80.4233
1396 | 39.9558 | 0 | 0 | 40.6 | 0 | 19.9779 | 0 | 0 | 0 | 3.6 | 249.5 | 81.7263
1397 | 44.2148 | 0 | 0 | 59.8 | 0 | 22.1074 | 0 | 0 | 0 | 7.1 | 282.4 | 86.8184
1398 | 41.2284 | 0 | 0 | 75.4 | 0 | 20.6142 | 0 | 0 | 0 | 11.3 | 304.6 | 128.5676
1399 | 58.532 | 0 | 42.9 | 254.6 | 56.3 | 29.266 | 0 | 0 | 0 | 30.7 | 828.7 | 106.0607
1400 | 83.0843 | 0.7 | 43 | 289.2 | 37.6 | 41.5422 | 0 | 0 | 0 | 82.1 | 766.8 | 124.1224
1401 | 160.6641 | 2.1 | 43.2 | 242 | 0 | 80.3321 | 0 | 0 | 0 | 79.6 | 224 | 136.8487
1402 | 243.534 | 3.5 | 43.4 | 196.6 | 0 | 121.767 | 0 | 0 | 0 | 87.1 | 213.2 | 290.2205
1403 | 257.9801 | 3.5 | 43.4 | 142.3 | 0 | 128.9901 | 0 | 0 | 0 | 63.5 | 155 | 137.151
1404 | 243.5672 | 2.8 | 43.3 | 81.8 | 0 | 121.7836 | 0 | 0 | 0 | 33.7 | 97.4 | 168.5489
1405 | 222.5925 | 1.4 | 43.1 | 28 | 75.1 | 111.2963 | 0 | 0 | 0 | 9.3 | 472.6 | 236.2267
1406 | 214.1998 | 2.1 | 43.2 | 6.3 | 37.6 | 107.0999 | 0 | 0 | 0 | 5.5 | 337.9 | 187.0106
1407 | 212.7082 | 3.5 | 43.4 | 0.9 | 0 | 106.3541 | 0 | 0 | 0 | 6.3 | 0.1 | 205.6062
1408 | 193.0672 | 2.8 | 43.3 | 0 | 0 | 96.5336 | 0 | 0 | 0 | 3.3 | 0 | 139.6272
1409 | 169.7244 | 2.1 | 43.2 | 0.4 | 0 | 84.8622 | 0 | 0 | 0 | 0.5 | 0.1 | 206.852
1410 | 144.3551 | 0.7 | 43 | 7 | 37.6 | 72.1775 | 0 | 0 | 0 | 0 | 368 | 215.393
1411 | 89.126 | 0 | 42.9 | 2.5 | 75.1 | 44.563 | 0 | 0 | 0 | 0 | 335.4 | 318.8441
1412 | 63.7377 | 0 | 42.9 | 0 | 75.1 | 31.8689 | 0 | 0 | 0 | 0 | 299.1 | 387.5651
1413 | 43.3901 | 0 | 42.9 | 1.8 | 75.1 | 21.695 | 0 | 0 | 0 | 0 | 363.5 | 243.1153
1414 | 42.3243 | 0 | 42.9 | 17.5 | 93.9 | 21.1621 | 0 | 0 | 0 | 0 | 408.4 | 231.6546
1415 | 41.185 | 0 | 0 | 0 | 0 | 20.5925 | 0 | 0 | 0 | 0 | 9.4 | 225.1043
1416 | 44.4962 | 0 | 0 | 0 | 0 | 22.2481 | 0 | 0 | 0 | 0 | 47.9 | 135.5896
1417 | 43.9985 | 0 | 0 | 0 | 0 | 21.9992 | 0 | 0 | 0 | 0 | 96.7 | 97.5548
1418 | 42.9023 | 0 | 0 | 3.9 | 0 | 21.4511 | 0 | 0 | 0 | 0 | 143.8 | 86.3464
1419 | 40.946 | 0 | 0 | 15.9 | 0 | 20.473 | 0 | 0 | 0 | 0 | 190.9 | 80.4283
1420 | 41.8863 | 0 | 0 | 37 | 0 | 20.9432 | 0 | 0 | 0 | 0 | 230.5 | 83.029
1421 | 40.7139 | 0 | 0 | 56.5 | 0 | 20.3569 | 0 | 0 | 0 | 0 | 265 | 80.6625
1422 | 42.5548 | 0 | 0 | 72.6 | 0 | 21.2774 | 0 | 0 | 0 | 0 | 289.1 | 115.8395
1423 | 55.2508 | 0 | 42.9 | 254.8 | 56.3 | 27.6254 | 0 | 0 | 0 | 6.1 | 811.7 | 136.1085
1424 | 87.484 | 0.7 | 43 | 288.8 | 37.6 | 43.742 | 0 | 0 | 0 | 64.7 | 749.1 | 231.2333
1425 | 178.3703 | 2.1 | 43.2 | 250.2 | 0 | 89.1852 | 0 | 0 | 0 | 63.8 | 226.6 | 298.8139
1426 | 320.074 | 3.5 | 43.4 | 216.4 | 0 | 160.037 | 0 | 0 | 0 | 76.3 | 231.2 | 259.4319
1427 | 306.88 | 3.5 | 43.4 | 173.1 | 0 | 153.44 | 0 | 0 | 0 | 63.5 | 190.4 | 106.1827
1428 | 283.4213 | 2.8 | 43.3 | 122.9 | 0 | 141.7107 | 0 | 0 | 0 | 33.3 | 149.9 | 211.4317
1429 | 255.7815 | 1.4 | 43.1 | 73.1 | 75.1 | 127.8908 | 0 | 0 | 0 | 7.9 | 554.8 | 165.1382
1430 | 228.822 | 2.1 | 43.2 | 41.1 | 37.6 | 114.411 | 0 | 0 | 0 | 20 | 421.9 | 171.7907
1431 | 236.8688 | 3.5 | 43.4 | 29.2 | 0 | 118.4344 | 0 | 0 | 0 | 49.8 | 8 | 151.4223
1432 | 223.3215 | 2.8 | 43.3 | 23.8 | 0 | 111.6607 | 0 | 0 | 0 | 55.8 | 10.2 | 152.1256
1433 | 243.6326 | 2.1 | 43.2 | 23.8 | 0 | 121.8163 | 0 | 0 | 0 | 44.9 | 15.7 | 233.9412
1434 | 216.1737 | 0.7 | 43 | 44.6 | 37.6 | 108.0869 | 0 | 0 | 0 | 24.4 | 482.9 | 397.9028
1435 | 133.6101 | 0 | 42.9 | 23 | 75.1 | 66.805 | 0 | 0 | 0 | 0 | 433.2 | 231.8133
1436 | 71.9281 | 0 | 42.9 | 6.6 | 75.1 | 35.964 | 0 | 0 | 0 | 0 | 383.5 | 445.3233
1437 | 56.5655 | 0 | 42.9 | 23.5 | 75.1 | 28.2828 | 0 | 0 | 0 | 0 | 438.4 | 313.8673
1438 | 43.0712 | 0 | 42.9 | 45.1 | 93.9 | 21.5356 | 0 | 0 | 0 | 0 | 473.7 | 227.1567
1439 | 44.7509 | 0 | 0 | 0 | 0 | 22.3755 | 0 | 0 | 0 | 0 | 34.6 | 182.4855
1440 | 41.2141 | 0 | 0 | 0 | 0 | 20.6071 | 0 | 0 | 0 | 0 | 93.4 | 152.544
1441 | 41.6155 | 0 | 0 | 1.8 | 0 | 20.8077 | 0 | 0 | 0 | 0 | 131 | 96.954
1442 | 41.9065 | 0 | 0 | 8.7 | 0 | 20.9532 | 0 | 0 | 0 | 0 | 163.9 | 83.2649
1443 | 43.383 | 0 | 0 | 17.6 | 0 | 21.6915 | 0 | 0 | 0 | 0 | 194.4 | 79.3578
1444 | 40.6178 | 0 | 0 | 33.7 | 0 | 20.3089 | 0 | 0 | 0 | 0.1 | 220.7 | 82.5564
1445 | 41.8213 | 0 | 0 | 47.9 | 0 | 20.9106 | 0 | 0 | 0 | 1.7 | 243.8 | 89.0695
1446 | 41.9421 | 0 | 0 | 60.3 | 0 | 20.9711 | 0 | 0 | 0 | 5.2 | 260.4 | 97.6702
1447 | 59.1614 | 0 | 42.9 | 234.3 | 56.3 | 29.5807 | 0 | 0 | 0 | 25.6 | 774 | 111.8768
1448 | 101.8033 | 0.7 | 43 | 266.9 | 37.6 | 50.9017 | 0 | 0 | 0 | 80.5 | 717.5 | 181.1909
1449 | 153.2012 | 2.1 | 43.2 | 257.8 | 0 | 76.6006 | 0 | 0 | 0 | 88.9 | 238.3 | 184.784
1450 | 232.979 | 3.5 | 43.4 | 251.2 | 0 | 116.4895 | 0 | 0 | 0 | 112.3 | 283.2 | 112.7214
1451 | 279.7264 | 3.5 | 43.4 | 234.4 | 0 | 139.8632 | 0 | 0 | 0 | 102.7 | 276.1 | 120.7427
1452 | 261.2064 | 2.8 | 43.3 | 209.9 | 0 | 130.6032 | 0 | 0 | 0 | 74.6 | 264.1 | 119.146
1453 | 252.2952 | 1.4 | 43.1 | 186.5 | 75.1 | 126.1476 | 0 | 0 | 0 | 43.1 | 714.6 | 166.2518
1454 | 228.3432 | 2.1 | 43.2 | 185.8 | 37.6 | 114.1716 | 0 | 0 | 0 | 40.6 | 640.7 | 246.7302
1455 | 216.541 | 3.5 | 43.4 | 184.3 | 0 | 108.2705 | 0 | 0 | 0 | 55.3 | 158.2 | 194.7654
1456 | 286.1369 | 2.8 | 43.3 | 175.1 | 0 | 143.0684 | 0 | 0 | 0 | 52.8 | 206.1 | 154.3195
1457 | 283.6848 | 2.1 | 43.2 | 168.2 | 0 | 141.8424 | 0 | 0 | 0 | 42.2 | 219.9 | 132.9474
1458 | 193.5636 | 0.7 | 43 | 173.1 | 37.6 | 96.7818 | 0 | 0 | 0 | 25.1 | 704.7 | 153.5011
1459 | 98.3679 | 0 | 42.9 | 131.3 | 75.1 | 49.1839 | 0 | 0 | 0 | 0 | 642.3 | 298.117
1460 | 61.3324 | 0 | 42.9 | 101.7 | 75.1 | 30.6662 | 0 | 0 | 0 | 0 | 566.9 | 175.7404
1461 | 42.9252 | 0 | 42.9 | 117.7 | 75.1 | 21.4626 | 0 | 0 | 0 | 0 | 617.6 | 281.2968
1462 | 40.0442 | 0 | 42.9 | 129.2 | 93.9 | 20.0221 | 0 | 0 | 0 | 0 | 647.6 | 331.0683
1463 | 42.42 | 0 | 0 | 19.4 | 0 | 21.21 | 0 | 0 | 0 | 0 | 171 | 138.623
1464 | 42.2648 | 0 | 0 | 44.4 | 0 | 21.1324 | 0 | 0 | 0 | 0 | 254.9 | 124.4506
1465 | 40.58 | 0 | 0 | 63.7 | 0 | 20.29 | 0 | 0 | 0 | 0 | 291.9 | 94.325
1466 | 42.4172 | 0 | 0 | 80.1 | 0 | 21.2086 | 0 | 0 | 0 | 0.4 | 324.2 | 95.2763
1467 | 40.4718 | 0 | 0 | 93.4 | 0 | 20.2359 | 0 | 0 | 0 | 2.7 | 351 | 94.2016
1468 | 42.5617 | 0 | 0 | 106 | 0 | 21.2808 | 0 | 0 | 0 | 6.9 | 377.5 | 87.5265
1469 | 41.9533 | 0 | 0 | 116.4 | 0 | 20.9766 | 0 | 0 | 0 | 11.2 | 399.9 | 82.2032
1470 | 43.2032 | 0 | 0 | 124.3 | 0 | 21.6016 | 0 | 0 | 0 | 15.8 | 412.3 | 109.206
1471 | 50.2793 | 0 | 42.9 | 291 | 56.3 | 25.1397 | 0 | 0 | 0 | 35.3 | 953.6 | 104.2544
1472 | 65.4978 | 0 | 42.9 | 312.7 | 37.6 | 32.7489 | 0 | 0 | 0 | 37.6 | 912.5 | 172.9894
1473 | 61.4641 | 0 | 42.9 | 297.3 | 0 | 30.7321 | 0 | 0 | 0 | 37.8 | 366.7 | 160.6557
1474 | 61.603 | 0 | 42.9 | 287.6 | 0 | 30.8015 | 0 | 0 | 0 | 38.3 | 413.5 | 134.9107
1475 | 60.6776 | 0 | 42.9 | 265.7 | 0 | 30.3388 | 0 | 0 | 0 | 34.9 | 402.5 | 133.3582
1476 | 55.8583 | 0 | 42.9 | 245.5 | 0 | 27.9291 | 0 | 0 | 0 | 31.1 | 394.8 | 166.8768
1477 | 57.4872 | 0 | 42.9 | 232.5 | 75.1 | 28.7436 | 0 | 0 | 0 | 25.5 | 882.6 | 155.5997
1478 | 53.6897 | 0 | 42.9 | 218.9 | 37.6 | 26.8449 | 0 | 0 | 0 | 20.8 | 808.2 | 149.9316
1479 | 53.3479 | 0 | 42.9 | 220.6 | 0 | 26.6739 | 0 | 0 | 0 | 20.6 | 287.3 | 125.0731
1480 | 52.7187 | 0 | 42.9 | 218.8 | 0 | 26.3594 | 0 | 0 | 0 | 22 | 352.9 | 123.0142
1481 | 60.6816 | 0 | 42.9 | 227.2 | 0 | 30.3408 | 0 | 0 | 0 | 20 | 380.4 | 141.0251
1482 | 69.8073 | 0 | 42.9 | 229.5 | 37.6 | 34.9036 | 0 | 0 | 0 | 25 | 881.8 | 171.8722
1483 | 66.4198 | 0 | 42.9 | 197.4 | 75.1 | 33.2099 | 0 | 0 | 0 | 27.2 | 823.5 | 227.042
1484 | 57.5018 | 0 | 42.9 | 166.3 | 75.1 | 28.7509 | 0 | 0 | 0 | 16.7 | 742.6 | 234.9259
1485 | 46.9254 | 0 | 42.9 | 181.7 | 75.1 | 23.4627 | 0 | 0 | 0 | 22.1 | 794.4 | 299.4635
1486 | 43.995 | 0 | 42.9 | 192.6 | 93.9 | 21.9975 | 0 | 0 | 0 | 25.7 | 829.6 | 261.6381
1487 | 42.7867 | 0 | 0 | 85 | 0 | 21.3933 | 0 | 0 | 0 | 29.2 | 314.6 | 153.9493
1488 | 43.4951 | 0 | 0 | 112.7 | 0 | 21.7476 | 0 | 0 | 0 | 32.1 | 408.9 | 123.1303
1489 | 42.3946 | 0 | 0 | 127.2 | 0 | 21.1973 | 0 | 0 | 0 | 34.9 | 439.8 | 88.8387
1490 | 42.6745 | 0 | 0 | 138.9 | 0 | 21.3372 | 0 | 0 | 0 | 37.1 | 465.4 | 79.7148
1491 | 42.4888 | 0 | 0 | 149.6 | 0 | 21.2444 | 0 | 0 | 0 | 38.3 | 490.1 | 78.165
1492 | 41.7571 | 0 | 0 | 158.2 | 0 | 20.8785 | 0 | 0 | 0 | 39.6 | 510 | 75.4421
1493 | 39.4751 | 0 | 0 | 166.1 | 0 | 19.7376 | 0 | 0 | 0 | 43.2 | 527.9 | 77.9297
1494 | 43.3219 | 0 | 0 | 173.2 | 0 | 21.6609 | 0 | 0 | 0 | 44.2 | 539.6 | 90.8599
1495 | 45.8744 | 0 | 42.9 | 346.4 | 56.3 | 22.9372 | 0 | 0 | 0 | 56.5 | 1111.1 | 115.508
1496 | 63.9221 | 0 | 42.9 | 342.4 | 37.6 | 31.9611 | 0 | 0 | 0 | 57.8 | 1071.5 | 127.8114
1497 | 62.7928 | 0 | 42.9 | 315.9 | 0 | 31.3964 | 0 | 0 | 0 | 55.6 | 475.5 | 109.5729
1498 | 63.761 | 0 | 42.9 | 294.4 | 0 | 31.8805 | 0 | 0 | 0 | 53.1 | 515.9 | 132.7563
1499 | 59.0356 | 0 | 42.9 | 271.2 | 0 | 29.5178 | 0 | 0 | 0 | 50.5 | 498.4 | 236.4528
1500 | 57.2117 | 0 | 42.9 | 240.7 | 0 | 28.6058 | 0 | 0 | 0 | 45 | 469.6 | 235.2458
1501 | 56.7573 | 0 | 42.9 | 238.7 | 75.1 | 28.3787 | 0 | 0 | 0 | 40.8 | 994 | 175.0008
1502 | 53.3572 | 0 | 42.9 | 227.7 | 37.6 | 26.6786 | 0 | 0 | 0 | 40.4 | 918.2 | 205.9029
1503 | 53.9278 | 0 | 42.9 | 227.4 | 0 | 26.9639 | 0 | 0 | 0 | 39.8 | 369.6 | 134.265
1504 | 53.9938 | 0 | 42.9 | 235.6 | 0 | 26.9969 | 0 | 0 | 0 | 39.4 | 444.2 | 137.8062
1505 | 59.6523 | 0 | 42.9 | 236.4 | 0 | 29.8262 | 0 | 0 | 0 | 40.5 | 452.3 | 130.0567
1506 | 69.6758 | 0 | 42.9 | 251.1 | 37.6 | 34.8379 | 0 | 0 | 0 | 42.2 | 977.7 | 259.7227
1507 | 64.802 | 0 | 42.9 | 241 | 75.1 | 32.401 | 0 | 0 | 0 | 42.5 | 947.3 | 413.5398
1508 | 52.5083 | 0 | 42.9 | 204.6 | 75.1 | 26.2542 | 0 | 0 | 0 | 32.7 | 860.8 | 329.9942
1509 | 45.7774 | 0 | 42.9 | 219 | 75.1 | 22.8887 | 0 | 0 | 0 | 37.5 | 910.6 | 218.1418
1510 | 42.7172 | 0 | 42.9 | 228.6 | 93.9 | 21.3586 | 0 | 0 | 0 | 40.1 | 946.2 | 181.1646
1511 | 42.2322 | 0 | 0 | 125.3 | 0 | 21.1161 | 0 | 0 | 0 | 42.9 | 405.4 | 173.5947
1512 | 41.1249 | 0 | 0 | 154 | 0 | 20.5624 | 0 | 0 | 0 | 45.3 | 502.7 | 122.6195
1513 | 41.215 | 0 | 0 | 167 | 0 | 20.6075 | 0 | 0 | 0 | 47.1 | 534.5 | 109.0871
1514 | 42.3481 | 0 | 0 | 179.6 | 0 | 21.1741 | 0 | 0 | 0 | 49.3 | 564.9 | 85.2812
1515 | 41.5637 | 0 | 0 | 191.1 | 0 | 20.7819 | 0 | 0 | 0 | 51.9 | 592.7 | 86.4646
1516 | 42.7653 | 0 | 0 | 200.7 | 0 | 21.3826 | 0 | 0 | 0 | 54.5 | 616.3 | 87.7607
1517 | 43.6123 | 0 | 0 | 208.6 | 0 | 21.8061 | 0 | 0 | 0 | 56.3 | 637.5 | 83.3832
1518 | 43.9938 | 0 | 0 | 215.7 | 0 | 21.9969 | 0 | 0 | 0 | 57.7 | 654.4 | 108.6027
1519 | 64.6635 | 0 | 42.9 | 398.6 | 56.3 | 32.3317 | 0 | 0 | 0 | 75.3 | 1269.2 | 107.3948
1520 | 94.3466 | 0.7 | 43 | 452.9 | 37.6 | 47.1733 | 0 | 0 | 0 | 141.3 | 1209 | 177.5629
1521 | 166.6376 | 2.1 | 43.2 | 401.8 | 0 | 83.3188 | 0 | 0 | 0 | 141.1 | 532.2 | 117.9562
1522 | 301.3866 | 3.5 | 43.4 | 355.3 | 0 | 150.6933 | 0 | 0 | 0 | 171.8 | 527.7 | 144.1278
1523 | 294.3123 | 3.5 | 43.4 | 294.3 | 0 | 147.1562 | 0 | 0 | 0 | 159.3 | 475.1 | 301.3534
1524 | 267.1498 | 2.8 | 43.3 | 233.5 | 0 | 133.5749 | 0 | 0 | 0 | 121.6 | 424 | 165.9041
1525 | 248.7354 | 1.4 | 43.1 | 178.9 | 75.1 | 124.3677 | 0 | 0 | 0 | 78.5 | 866.4 | 116.5065
1526 | 234.0761 | 2.1 | 43.2 | 143.1 | 37.6 | 117.038 | 0 | 0 | 0 | 74.1 | 727.5 | 200.6541
1527 | 230.6477 | 3.5 | 43.4 | 129.1 | 0 | 115.3239 | 0 | 0 | 0 | 95 | 176.7 | 202.5407
1528 | 229.5853 | 2.8 | 43.3 | 115.1 | 0 | 114.7927 | 0 | 0 | 0 | 92 | 203 | 172.2442
1529 | 196.6812 | 2.1 | 43.2 | 106.5 | 0 | 98.3406 | 0 | 0 | 0 | 76.2 | 218.5 | 117.5191
1530 | 193.8094 | 0.7 | 43 | 122.4 | 37.6 | 96.9047 | 0 | 0 | 0 | 50.6 | 709.7 | 172.4382
1531 | 136.8206 | 0 | 42.9 | 95.1 | 75.1 | 68.4103 | 0 | 0 | 0 | 3.8 | 668.2 | 212.56
1532 | 81.8229 | 0 | 42.9 | 74.9 | 75.1 | 40.9115 | 0 | 0 | 0 | 1.8 | 608.1 | 266.2809
1533 | 57.0223 | 0 | 42.9 | 103.1 | 75.1 | 28.5112 | 0 | 0 | 0 | 4.4 | 663.9 | 405.9197
1534 | 41.5894 | 0 | 42.9 | 125.4 | 93.9 | 20.7947 | 0 | 0 | 0 | 7.9 | 704.3 | 190.6206
1535 | 42.4163 | 0 | 0 | 15 | 0 | 21.2082 | 0 | 0 | 0 | 14.9 | 225.3 | 178.812
1536 | 40.4672 | 0 | 0 | 43.6 | 0 | 20.2336 | 0 | 0 | 0 | 22.1 | 320.1 | 248.5623
1537 | 42.7634 | 0 | 0 | 69.5 | 0 | 21.3817 | 0 | 0 | 0 | 26.9 | 359.5 | 115.0168
1538 | 41.128 | 0 | 0 | 91.9 | 0 | 20.564 | 0 | 0 | 0 | 30.4 | 396 | 89.1874
1539 | 41.8064 | 0 | 0 | 111.6 | 0 | 20.9032 | 0 | 0 | 0 | 34 | 430 | 88.5988
1540 | 43.0783 | 0 | 0 | 128.2 | 0 | 21.5391 | 0 | 0 | 0 | 37 | 460.1 | 75.7918
1541 | 42.116 | 0 | 0 | 141.7 | 0 | 21.058 | 0 | 0 | 0 | 39.7 | 485.9 | 75.5582
1542 | 41.4803 | 0 | 0 | 153.3 | 0 | 20.7402 | 0 | 0 | 0 | 41.9 | 505.1 | 100.6658
1543 | 61.8974 | 0 | 42.9 | 328.7 | 56.3 | 30.9487 | 0 | 0 | 0 | 57.1 | 1059.3 | 116.2673
1544 | 111.0443 | 0.7 | 43 | 371.6 | 37.6 | 55.5222 | 0 | 0 | 0 | 114 | 995.6 | 190.0805
1545 | 212.0886 | 2.1 | 43.2 | 319.4 | 0 | 106.0443 | 0 | 0 | 0 | 114.1 | 385.6 | 285.8574
1546 | 310.1283 | 3.5 | 43.4 | 267.8 | 0 | 155.0641 | 0 | 0 | 0 | 129.9 | 375.8 | 91.9378
1547 | 362.0065 | 3.5 | 43.4 | 209.7 | 0 | 181.0033 | 0 | 0 | 0 | 114.5 | 319.5 | 143.4397
1548 | 349.1376 | 2.8 | 43.3 | 149.6 | 0 | 174.5688 | 0 | 0 | 0 | 78.7 | 266.1 | 267.492
1549 | 293.7411 | 1.4 | 43.1 | 91.8 | 75.1 | 146.8706 | 0 | 0 | 0 | 41.6 | 673 | 268.4637
1550 | 219.8287 | 2.1 | 43.2 | 52.7 | 37.6 | 109.9143 | 0 | 0 | 0 | 34.5 | 528.2 | 181.4539
1551 | 214.392 | 3.5 | 43.4 | 37.6 | 0 | 107.196 | 0 | 0 | 0 | 45.7 | 38.9 | 119.5704
1552 | 208.7003 | 2.8 | 43.3 | 29.7 | 0 | 104.3501 | 0 | 0 | 0 | 41.8 | 45.1 | 84.5642
1553 | 228.2734 | 2.1 | 43.2 | 28.4 | 0 | 114.1367 | 0 | 0 | 0 | 30.1 | 63.9 | 110.9044
1554 | 228.7203 | 0.7 | 43 | 50.5 | 37.6 | 114.3602 | 0 | 0 | 0 | 14.2 | 547.3 | 141.4953
1555 | 139.8039 | 0 | 42.9 | 33.1 | 75.1 | 69.9019 | 0 | 0 | 0 | 0 | 503.3 | 161.3599
1556 | 81.5279 | 0 | 42.9 | 19.1 | 75.1 | 40.764 | 0 | 0 | 0 | 0 | 459.4 | 225.964
1557 | 56.6284 | 0 | 42.9 | 46.9 | 75.1 | 28.3142 | 0 | 0 | 0 | 0 | 524.4 | 284.262
1558 | 42.3038 | 0 | 42.9 | 74.9 | 93.9 | 21.1519 | 0 | 0 | 0 | 0 | 571 | 213.8714
1559 | 40.0699 | 0 | 0 | 0 | 0 | 20.0349 | 0 | 0 | 0 | 0 | 118 | 144.1928
1560 | 43.1837 | 0 | 0 | 5.8 | 0 | 21.5918 | 0 | 0 | 0 | 0 | 205.1 | 127.891
1561 | 41.5767 | 0 | 0 | 26.8 | 0 | 20.7884 | 0 | 0 | 0 | 0.1 | 255.3 | 106.3081
1562 | 41.3765 | 0 | 0 | 54.9 | 0 | 20.6883 | 0 | 0 | 0 | 1.5 | 305.2 | 88.1258
1563 | 40.5255 | 0 | 0 | 80.7 | 0 | 20.2627 | 0 | 0 | 0 | 3.1 | 352.7 | 78.5299
1564 | 43.9861 | 0 | 0 | 101.8 | 0 | 21.993 | 0 | 0 | 0 | 4.2 | 391.9 | 79.3583
1565 | 42.155 | 0 | 0 | 118.9 | 0 | 21.0775 | 0 | 0 | 0 | 6.6 | 423.8 | 78.8849
1566 | 43.3969 | 0 | 0 | 133.8 | 0 | 21.6984 | 0 | 0 | 0 | 10.1 | 448.6 | 81.3719
1567 | 61.9172 | 0 | 42.9 | 313.9 | 56.3 | 30.9586 | 0 | 0 | 0 | 28.8 | 994.1 | 108.6036
1568 | 103.8966 | 0.7 | 43 | 356 | 37.6 | 51.9483 | 0 | 0 | 0 | 82.1 | 925.4 | 98.0355
1569 | 205.7334 | 2.1 | 43.2 | 306.4 | 0 | 102.8667 | 0 | 0 | 0 | 93.8 | 345 | 95.5137
1570 | 317.5103 | 3.5 | 43.4 | 260.1 | 0 | 158.7552 | 0 | 0 | 0 | 126.3 | 337.9 | 100.3098
1571 | 366.1155 | 3.5 | 43.4 | 205.4 | 0 | 183.0577 | 0 | 0 | 0 | 131 | 285.4 | 199.6428
1572 | 357.8951 | 2.8 | 43.3 | 145.4 | 0 | 178.9475 | 0 | 0 | 0 | 110.5 | 235.7 | 297.6065
1573 | 315.6582 | 1.4 | 43.1 | 86.9 | 75.1 | 157.8291 | 0 | 0 | 0 | 77.5 | 647.1 | 215.7335
1574 | 266.6846 | 2.1 | 43.2 | 48.9 | 37.6 | 133.3423 | 0 | 0 | 0 | 81.7 | 497.7 | 171.8525
1575 | 265.7666 | 3.5 | 43.4 | 35.6 | 0 | 132.8833 | 0 | 0 | 0 | 111.5 | 21.8 | 119.7947
1576 | 232.5116 | 2.8 | 43.3 | 25.8 | 0 | 116.2558 | 0 | 0 | 0 | 110.3 | 25 | 120.0489
1577 | 197.3283 | 2.1 | 43.2 | 22.1 | 0 | 98.6641 | 0 | 0 | 0 | 90.4 | 42.1 | 168.615
1578 | 211.4958 | 0.7 | 43 | 41.5 | 37.6 | 105.7479 | 0 | 0 | 0 | 56.1 | 525.8 | 136.8125
1579 | 174.9138 | 0 | 42.9 | 25.9 | 75.1 | 87.4569 | 0 | 0 | 0 | 7.2 | 483.9 | 232.7684
1580 | 99.4111 | 0 | 42.9 | 14.6 | 75.1 | 49.7055 | 0 | 0 | 0 | 2.3 | 447.6 | 310.0865
1581 | 55.5251 | 0 | 42.9 | 43.9 | 75.1 | 27.7625 | 0 | 0 | 0 | 5.4 | 521.4 | 260.6133
1582 | 42.7557 | 0 | 42.9 | 75.6 | 93.9 | 21.3778 | 0 | 0 | 0 | 11.1 | 576.6 | 253.8147
1583 | 42.9348 | 0 | 0 | 0 | 0 | 21.4674 | 0 | 0 | 0 | 15.8 | 124.3 | 306.8194
1584 | 41.6145 | 0 | 0 | 9 | 0 | 20.8073 | 0 | 0 | 0 | 21.6 | 217.2 | 169.5133
1585 | 43.5311 | 0 | 0 | 33.2 | 0 | 21.7655 | 0 | 0 | 0 | 26.3 | 273.4 | 104.9812
1586 | 40.8106 | 0 | 0 | 63.1 | 0 | 20.4053 | 0 | 0 | 0 | 30.6 | 326.5 | 88.7178
1587 | 40.7765 | 0 | 0 | 89.9 | 0 | 20.3883 | 0 | 0 | 0 | 35.6 | 376.7 | 84.088
1588 | 40.8633 | 0 | 0 | 111.8 | 0 | 20.4316 | 0 | 0 | 0 | 39.4 | 417.5 | 76.7338
1589 | 44.5901 | 0 | 0 | 130.3 | 0 | 22.295 | 0 | 0 | 0 | 42.5 | 453.2 | 77.9282
1590 | 42.0484 | 0 | 0 | 146.4 | 0 | 21.0242 | 0 | 0 | 0 | 44.5 | 481.1 | 91.4558
1591 | 62.0722 | 0 | 42.9 | 329.5 | 56.3 | 31.0361 | 0 | 0 | 0 | 58.3 | 1027 | 97.4321
1592 | 103.6706 | 0.7 | 43 | 383.6 | 37.6 | 51.8353 | 0 | 0 | 0 | 119.1 | 973.9 | 114.41
1593 | 183.1679 | 2.1 | 43.2 | 386.8 | 0 | 91.584 | 0 | 0 | 0 | 136.4 | 457.9 | 178.5358
1594 | 287.5746 | 3.5 | 43.4 | 405.1 | 0 | 143.7873 | 0 | 0 | 0 | 174.9 | 534.3 | 227.3722
1595 | 316.6856 | 3.5 | 43.4 | 402.5 | 0 | 158.3428 | 0 | 0 | 0 | 171.8 | 546.7 | 192.4369
1596 | 305.5619 | 2.8 | 43.3 | 388.1 | 0 | 152.7809 | 0 | 0 | 0 | 137.9 | 556.8 | 203.6917
1597 | 281.921 | 1.4 | 43.1 | 363.6 | 75.1 | 140.9605 | 0 | 0 | 0 | 91.3 | 1101.5 | 174.9406
1598 | 271.2482 | 2.1 | 43.2 | 314.6 | 37.6 | 135.6241 | 0 | 0 | 0 | 92.8 | 945.9 | 152.7549
1599 | 215.8083 | 3.5 | 43.4 | 302.6 | 0 | 107.9042 | 0 | 0 | 0 | 125.8 | 370.9 | 138.2806
1600 | 184.1243 | 2.8 | 43.3 | 282.6 | 0 | 92.0622 | 0 | 0 | 0 | 132.8 | 417.7 | 196.6026
1601 | 145.6016 | 2.1 | 43.2 | 259.3 | 0 | 72.8008 | 0 | 0 | 0 | 109.7 | 424.2 | 256.3469
1602 | 157.5634 | 0.7 | 43 | 256.5 | 37.6 | 78.7817 | 0 | 0 | 0 | 69.9 | 930.5 | 216.7158
1603 | 106.1602 | 0 | 42.9 | 206.6 | 75.1 | 53.0801 | 0 | 0 | 0 | 18.1 | 890.7 | 184.6746
1604 | 74.5419 | 0 | 42.9 | 177.5 | 75.1 | 37.271 | 0 | 0 | 0 | 11.4 | 817 | 346.0277
1605 | 57.8021 | 0 | 42.9 | 198 | 75.1 | 28.901 | 0 | 0 | 0 | 20.5 | 872.7 | 367.3386
1606 | 42.7687 | 0 | 42.9 | 212.2 | 93.9 | 21.3843 | 0 | 0 | 0 | 26.7 | 915.8 | 263.3116
1607 | 41.4323 | 0 | 0 | 94 | 0 | 20.7161 | 0 | 0 | 0 | 32.6 | 394.1 | 204.8924
1608 | 41.3536 | 0 | 0 | 125 | 0 | 20.6768 | 0 | 0 | 0 | 38 | 492.4 | 142.8029
1609 | 40.3968 | 0 | 0 | 143.1 | 0 | 20.1984 | 0 | 0 | 0 | 42 | 526.4 | 131.1329
1610 | 42.2703 | 0 | 0 | 158.7 | 0 | 21.1352 | 0 | 0 | 0 | 45 | 557.4 | 76.3796
1611 | 40.8165 | 0 | 0 | 171.7 | 0 | 20.4082 | 0 | 0 | 0 | 47.5 | 584.7 | 75.9134
1612 | 42.0063 | 0 | 0 | 183.4 | 0 | 21.0031 | 0 | 0 | 0 | 49.2 | 609.8 | 80.0694
1613 | 43.6123 | 0 | 0 | 193.4 | 0 | 21.8061 | 0 | 0 | 0 | 50.8 | 631.5 | 82.79
1614 | 44.7181 | 0 | 0 | 201.8 | 0 | 22.359 | 0 | 0 | 0 | 51.8 | 645.1 | 106.0642
1615 | 59.0526 | 0 | 42.9 | 381 | 56.3 | 29.5263 | 0 | 0 | 0 | 64.3 | 1224 | 112.3576
1616 | 90.6548 | 0.7 | 43 | 432 | 37.6 | 45.3274 | 0 | 0 | 0 | 126.7 | 1181.6 | 111.6297
1617 | 176.7556 | 2.1 | 43.2 | 402.7 | 0 | 88.3778 | 0 | 0 | 0 | 138.5 | 545.9 | 107.3965
1618 | 282.1507 | 3.5 | 43.4 | 385 | 0 | 141.0753 | 0 | 0 | 0 | 164.3 | 570.6 | 95.754
1619 | 327.1058 | 3.5 | 43.4 | 343.2 | 0 | 163.5529 | 0 | 0 | 0 | 150.7 | 535.9 | 93.2455
1620 | 313.7187 | 2.8 | 43.3 | 295.9 | 0 | 156.8594 | 0 | 0 | 0 | 116.1 | 501.1 | 170.2707
1621 | 282.91 | 1.4 | 43.1 | 261.3 | 75.1 | 141.455 | 0 | 0 | 0 | 79.8 | 1001.6 | 243.5412
1622 | 254.7706 | 2.1 | 43.2 | 244.8 | 37.6 | 127.3853 | 0 | 0 | 0 | 86.4 | 898.5 | 155.9363
1623 | 260.0541 | 3.5 | 43.4 | 247.7 | 0 | 130.0271 | 0 | 0 | 0 | 115.3 | 340.1 | 195.1664
1624 | 257.8685 | 2.8 | 43.3 | 240.6 | 0 | 128.9343 | 0 | 0 | 0 | 110.4 | 397 | 253.6691
1625 | 194.8346 | 2.1 | 43.2 | 234.5 | 0 | 97.4173 | 0 | 0 | 0 | 92.2 | 414.3 | 121.2484
1626 | 193.475 | 0.7 | 43 | 243.6 | 37.6 | 96.7375 | 0 | 0 | 0 | 59.5 | 942.2 | 138.8391
1627 | 95.7868 | 0 | 42.9 | 197.9 | 75.1 | 47.8934 | 0 | 0 | 0 | 10 | 911.2 | 136.2756
1628 | 51.9969 | 0 | 42.9 | 167.1 | 75.1 | 25.9985 | 0 | 0 | 0 | 4 | 828.1 | 210.6474
1629 | 40.7365 | 0 | 42.9 | 184.3 | 75.1 | 20.3683 | 0 | 0 | 0 | 10.7 | 873.7 | 207.9277
1630 | 40.2884 | 0 | 42.9 | 196.1 | 93.9 | 20.1442 | 0 | 0 | 0 | 17.7 | 905.8 | 159.3011
1631 | 39.3626 | 0 | 0 | 78 | 0 | 19.6813 | 0 | 0 | 0 | 23.2 | 371.1 | 178.8202
1632 | 42.0611 | 0 | 0 | 106.1 | 0 | 21.0306 | 0 | 0 | 0 | 28.2 | 460.5 | 143.3735
1633 | 41.5355 | 0 | 0 | 122.1 | 0 | 20.7678 | 0 | 0 | 0 | 32.9 | 486.7 | 101.4961
1634 | 42.0311 | 0 | 0 | 136.1 | 0 | 21.0155 | 0 | 0 | 0 | 37.1 | 511 | 81.4898
1635 | 43.1855 | 0 | 0 | 148 | 0 | 21.5928 | 0 | 0 | 0 | 41.7 | 533.8 | 75.6766
1636 | 40.1653 | 0 | 0 | 157.8 | 0 | 20.0827 | 0 | 0 | 0 | 44.7 | 552.6 | 76.0287
1637 | 42.6875 | 0 | 0 | 166.4 | 0 | 21.3437 | 0 | 0 | 0 | 47 | 569 | 78.1645
1638 | 40.4133 | 0 | 0 | 173.5 | 0 | 20.2066 | 0 | 0 | 0 | 50.1 | 578.1 | 122.6439
1639 | 43.0476 | 0 | 42.9 | 348.1 | 56.3 | 21.5238 | 0 | 0 | 0 | 65.7 | 1164.1 | 87.7649
1640 | 60.7151 | 0 | 42.9 | 368.5 | 37.6 | 30.3575 | 0 | 0 | 0 | 62.7 | 1115.7 | 114.8973
1641 | 70.4426 | 0 | 42.9 | 333.1 | 0 | 35.2213 | 0 | 0 | 0 | 50.5 | 479.8 | 186.6021
1642 | 68.7052 | 0 | 42.9 | 307.2 | 0 | 34.3526 | 0 | 0 | 0 | 41.7 | 501.2 | 147.8237
1643 | 64.1701 | 0 | 42.9 | 265.2 | 0 | 32.085 | 0 | 0 | 0 | 34.6 | 464.9 | 163.067
1644 | 64.1605 | 0 | 42.9 | 224.1 | 0 | 32.0802 | 0 | 0 | 0 | 24.9 | 427.9 | 147.9595
1645 | 61.5174 | 0 | 42.9 | 196.7 | 75.1 | 30.7587 | 0 | 0 | 0 | 15.1 | 899.3 | 170.9488
1646 | 61.0281 | 0 | 42.9 | 178.1 | 37.6 | 30.514 | 0 | 0 | 0 | 9.7 | 802.5 | 271.0085
1647 | 58.5338 | 0 | 42.9 | 173.2 | 0 | 29.2669 | 0 | 0 | 0 | 5.6 | 260.9 | 228.3231
1648 | 59.6567 | 0 | 42.9 | 167.4 | 0 | 29.8283 | 0 | 0 | 0 | 3.3 | 311.5 | 150.5735
1649 | 61.5407 | 0 | 42.9 | 172.1 | 0 | 30.7703 | 0 | 0 | 0 | 2.4 | 327.6 | 150.5767
1650 | 68.239 | 0 | 42.9 | 188.4 | 37.6 | 34.1195 | 0 | 0 | 0 | 3.2 | 841.7 | 229.1107
1651 | 68.9612 | 0 | 42.9 | 170.9 | 75.1 | 34.4806 | 0 | 0 | 0 | 10.4 | 798.4 | 460.0754
1652 | 47.5796 | 0 | 42.9 | 137.4 | 75.1 | 23.7898 | 0 | 0 | 0 | 4.3 | 715.2 | 309.9667
1653 | 43.9755 | 0 | 42.9 | 152.7 | 75.1 | 21.9878 | 0 | 0 | 0 | 8.5 | 758.4 | 365.7324
1654 | 40.2196 | 0 | 42.9 | 162.6 | 93.9 | 20.1098 | 0 | 0 | 0 | 13.4 | 782.7 | 215.6472
1655 | 42.8886 | 0 | 0 | 48.8 | 0 | 21.4443 | 0 | 0 | 0 | 18.3 | 270.6 | 294.317
1656 | 40.9092 | 0 | 0 | 74.8 | 0 | 20.4546 | 0 | 0 | 0 | 23 | 354.9 | 123.6045
1657 | 42.2613 | 0 | 0 | 90.8 | 0 | 21.1307 | 0 | 0 | 0 | 27.1 | 381.8 | 95.1569
1658 | 43.7806 | 0 | 0 | 104.2 | 0 | 21.8903 | 0 | 0 | 0 | 30.9 | 405.4 | 91.4584
1659 | 42.231 | 0 | 0 | 115.7 | 0 | 21.1155 | 0 | 0 | 0 | 34.5 | 426.6 | 79.1196
1660 | 43.9783 | 0 | 0 | 125.1 | 0 | 21.9892 | 0 | 0 | 0 | 37.5 | 445.1 | 77.0878
1661 | 41.9762 | 0 | 0 | 133 | 0 | 20.9881 | 0 | 0 | 0 | 40 | 461.2 | 76.9719
1662 | 43.4068 | 0 | 0 | 140.3 | 0 | 21.7034 | 0 | 0 | 0 | 42.1 | 471.4 | 96.8315
1663 | 52.4987 | 0 | 42.9 | 309.7 | 56.3 | 26.2494 | 0 | 0 | 0 | 55.8 | 1028.6 | 118.2722
1664 | 67.2247 | 0 | 42.9 | 297.8 | 37.6 | 33.6123 | 0 | 0 | 0 | 46.9 | 978.7 | 106.0564
1665 | 69.7171 | 0 | 42.9 | 249.8 | 0 | 34.8585 | 0 | 0 | 0 | 35.5 | 370 | 211.1041
1666 | 69.3786 | 0 | 42.9 | 216 | 0 | 34.6893 | 0 | 0 | 0 | 25.9 | 387.3 | 138.1516
1667 | 67.1571 | 0 | 42.9 | 189.4 | 0 | 33.5786 | 0 | 0 | 0 | 15.5 | 360.2 | 179.9855
1668 | 61.4899 | 0 | 42.9 | 162.2 | 0 | 30.7449 | 0 | 0 | 0 | 4.9 | 329.3 | 256.9996
1669 | 58.3423 | 0 | 42.9 | 145.7 | 75.1 | 29.1711 | 0 | 0 | 0 | 0.3 | 773.5 | 186.6292
1670 | 57.2638 | 0 | 42.9 | 124.7 | 37.6 | 28.6319 | 0 | 0 | 0 | 0 | 675.3 | 124.9278
1671 | 57.2098 | 0 | 42.9 | 114.2 | 0 | 28.6049 | 0 | 0 | 0 | 0 | 166.3 | 170.1044
1672 | 55.8852 | 0 | 42.9 | 110.6 | 0 | 27.9426 | 0 | 0 | 0 | 0 | 208.5 | 265.5573
1673 | 68.6655 | 0 | 42.9 | 115.8 | 0 | 34.3327 | 0 | 0 | 0 | 0 | 221.6 | 207.9934
1674 | 75.7097 | 0 | 42.9 | 133.4 | 37.6 | 37.8549 | 0 | 0 | 0 | 0 | 706.8 | 140.2672
1675 | 66.3755 | 0 | 42.9 | 140.1 | 75.1 | 33.1877 | 0 | 0 | 0 | 0.1 | 650.4 | 224.7874
1676 | 48.6355 | 0 | 42.9 | 110.3 | 75.1 | 24.3178 | 0 | 0 | 0 | 0 | 581.2 | 190.7673
1677 | 44.8786 | 0 | 42.9 | 130.6 | 75.1 | 22.4393 | 0 | 0 | 0 | 0 | 639.4 | 336.6135
1678 | 43.5029 | 0 | 42.9 | 145.9 | 93.9 | 21.7514 | 0 | 0 | 0 | 0.3 | 677.8 | 229.3447
1679 | 42.3754 | 0 | 0 | 38.8 | 0 | 21.1877 | 0 | 0 | 0 | 2.2 | 204.1 | 335.0034
1680 | 42.0072 | 0 | 0 | 68.6 | 0 | 21.0036 | 0 | 0 | 0 | 4.2 | 297.6 | 194.5342
1681 | 42.4179 | 0 | 0 | 90.4 | 0 | 21.2089 | 0 | 0 | 0 | 8 | 340.8 | 142.5327
1682 | 42.1746 | 0 | 0 | 110.9 | 0 | 21.0873 | 0 | 0 | 0 | 14.3 | 384.2 | 88.3578
1683 | 42.4668 | 0 | 0 | 131 | 0 | 21.2334 | 0 | 0 | 0 | 20.7 | 428.8 | 76.8556
1684 | 40.3789 | 0 | 0 | 147.3 | 0 | 20.1894 | 0 | 0 | 0 | 26.3 | 466 | 77.2073
1685 | 40.9383 | 0 | 0 | 159.8 | 0 | 20.4691 | 0 | 0 | 0 | 30.7 | 495.7 | 77.9249
1686 | 41.652 | 0 | 0 | 170.3 | 0 | 20.826 | 0 | 0 | 0 | 34.6 | 517.5 | 78.2824
1687 | 56.3343 | 0 | 42.9 | 342.2 | 56.3 | 28.1672 | 0 | 0 | 0 | 49.7 | 1070.8 | 85.9847
1688 | 89.8066 | 0.7 | 43 | 367 | 37.6 | 44.9033 | 0 | 0 | 0 | 94.8 | 975.9 | 100.309
1689 | 146.0222 | 2.1 | 43.2 | 311.8 | 0 | 73.0111 | 0 | 0 | 0 | 98.4 | 367.2 | 127.1721
1690 | 245.2407 | 3.5 | 43.4 | 266.7 | 0 | 122.6204 | 0 | 0 | 0 | 119.9 | 363.8 | 81.4929
1691 | 288.3956 | 3.5 | 43.4 | 211.5 | 0 | 144.1978 | 0 | 0 | 0 | 106.8 | 309.3 | 108.0043
1692 | 307.9474 | 2.8 | 43.3 | 150.6 | 0 | 153.9737 | 0 | 0 | 0 | 70.7 | 252.6 | 142.0156
1693 | 302.2367 | 1.4 | 43.1 | 91.6 | 75.1 | 151.1184 | 0 | 0 | 0 | 31.6 | 654.2 | 297.8249
1694 | 288.6376 | 2.1 | 43.2 | 52 | 37.6 | 144.3188 | 0 | 0 | 0 | 24.7 | 503.6 | 176.843
1695 | 271.9836 | 3.5 | 43.4 | 35.3 | 0 | 135.9918 | 0 | 0 | 0 | 38.9 | 24.1 | 160.9465
1696 | 236.7544 | 2.8 | 43.3 | 23.9 | 0 | 118.3772 | 0 | 0 | 0 | 33.9 | 23.1 | 214.7456
1697 | 168.75 | 2.1 | 43.2 | 18.6 | 0 | 84.375 | 0 | 0 | 0 | 19.8 | 27.5 | 77.684
1698 | 114.3781 | 0.7 | 43 | 29.9 | 37.6 | 57.1891 | 0 | 0 | 0 | 5.9 | 492.5 | 116.7159
1699 | 82.7406 | 0 | 42.9 | 20.6 | 75.1 | 41.3703 | 0 | 0 | 0 | 0 | 449.8 | 203.234
1700 | 47.1095 | 0 | 42.9 | 9.9 | 75.1 | 23.5547 | 0 | 0 | 0 | 0 | 406.5 | 192.3289
1701 | 43.5361 | 0 | 42.9 | 29.6 | 75.1 | 21.768 | 0 | 0 | 0 | 0 | 468.2 | 251.3517
1702 | 39.1445 | 0 | 42.9 | 56.2 | 93.9 | 19.5722 | 0 | 0 | 0 | 0 | 511.6 | 193.2089
1703 | 41.0846 | 0 | 0 | 0 | 0 | 20.5423 | 0 | 0 | 0 | 0 | 66.2 | 173.791
1704 | 40.3367 | 0 | 0 | 0.3 | 0 | 20.1684 | 0 | 0 | 0 | 0 | 140.1 | 132.8752
1705 | 42.8369 | 0 | 0 | 9.4 | 0 | 21.4184 | 0 | 0 | 0 | 0 | 185.5 | 109.9371
1706 | 39.3905 | 0 | 0 | 27.2 | 0 | 19.6953 | 0 | 0 | 0 | 0.2 | 225.2 | 90.3826
1707 | 41.8817 | 0 | 0 | 50.2 | 0 | 20.9408 | 0 | 0 | 0 | 2.1 | 265 | 86.4628
1708 | 43.5085 | 0 | 0 | 69.3 | 0 | 21.7542 | 0 | 0 | 0 | 4 | 298.2 | 81.0202
1709 | 42.2285 | 0 | 0 | 85.9 | 0 | 21.1142 | 0 | 0 | 0 | 7.1 | 328.4 | 83.2671
1710 | 43.4716 | 0 | 0 | 99.7 | 0 | 21.7358 | 0 | 0 | 0 | 12.1 | 349.5 | 89.903
1711 | 71.1932 | 0 | 42.9 | 275.2 | 56.3 | 35.5966 | 0 | 0 | 0 | 32 | 874.6 | 141.1851
1712 | 109.6205 | 0.7 | 43 | 306 | 37.6 | 54.8103 | 0 | 0 | 0 | 78.2 | 798.2 | 165.1935
1713 | 162.726 | 2.1 | 43.2 | 276.9 | 0 | 81.363 | 0 | 0 | 0 | 78.7 | 275.7 | 106.3055
1714 | 210.3903 | 3.5 | 43.4 | 250.2 | 0 | 105.1951 | 0 | 0 | 0 | 99.8 | 293.4 | 148.292
1715 | 228.8586 | 3.5 | 43.4 | 217.8 | 0 | 114.4293 | 0 | 0 | 0 | 88.8 | 262.8 | 376.3517
1716 | 220.7882 | 2.8 | 43.3 | 188.8 | 0 | 110.3941 | 0 | 0 | 0 | 57.1 | 238.8 | 236.7988
1717 | 196.537 | 1.4 | 43.1 | 153.3 | 75.1 | 98.2685 | 0 | 0 | 0 | 20.2 | 666.9 | 138.89
1718 | 180.3802 | 2.1 | 43.2 | 125.4 | 37.6 | 90.1901 | 0 | 0 | 0 | 12.7 | 539.7 | 180.5307
1719 | 183.4707 | 3.5 | 43.4 | 115.2 | 0 | 91.7354 | 0 | 0 | 0 | 23.7 | 72.2 | 159.8977
1720 | 182.0665 | 2.8 | 43.3 | 106.2 | 0 | 91.0332 | 0 | 0 | 0 | 15.5 | 100.2 | 149.3549
1721 | 174.037 | 2.1 | 43.2 | 102.8 | 0 | 87.0185 | 0 | 0 | 0 | 4.2 | 116.7 | 302.0678
1722 | 138.3754 | 0.7 | 43 | 116.4 | 37.6 | 69.1877 | 0 | 0 | 0 | 0.2 | 593.5 | 233.3202
1723 | 80.1962 | 0 | 42.9 | 81.5 | 75.1 | 40.0981 | 0 | 0 | 0 | 0 | 536.2 | 199.0093
1724 | 47.1153 | 0 | 42.9 | 51.1 | 75.1 | 23.5577 | 0 | 0 | 0 | 0 | 469.2 | 232.3983
1725 | 44.5297 | 0 | 42.9 | 70.1 | 75.1 | 22.2648 | 0 | 0 | 0 | 0 | 515.6 | 394.6461
1726 | 40.9687 | 0 | 42.9 | 83.8 | 93.9 | 20.4843 | 0 | 0 | 0 | 0 | 539.9 | 417.2094
1727 | 39.7999 | 0 | 0 | 0 | 0 | 19.9 | 0 | 0 | 0 | 0 | 89.7 | 192.1517
1728 | 42.2465 | 0 | 0 | 3 | 0 | 21.1232 | 0 | 0 | 0 | 0 | 152.3 | 148.2998
1729 | 43.3163 | 0 | 0 | 11.7 | 0 | 21.6582 | 0 | 0 | 0 | 0 | 183.6 | 114.2885
1730 | 41.8702 | 0 | 0 | 27.4 | 0 | 20.9351 | 0 | 0 | 0 | 0 | 211.3 | 95.9895
1731 | 41.8894 | 0 | 0 | 39.6 | 0 | 20.9447 | 0 | 0 | 0 | 0 | 227.6 | 96.8329
1732 | 39.0217 | 0 | 0 | 52.7 | 0 | 19.5109 | 0 | 0 | 0 | 0 | 250.1 | 77.205
1733 | 41.7528 | 0 | 0 | 73.8 | 0 | 20.8764 | 0 | 0 | 0 | 0 | 295.7 | 82.2037
1734 | 42.5973 | 0 | 0 | 81.3 | 0 | 21.2986 | 0 | 0 | 0 | 1.1 | 304.2 | 88.6
1735 | 52.0645 | 0 | 42.9 | 236.9 | 56.3 | 26.0323 | 0 | 0 | 0 | 16.3 | 797.8 | 106.3064
1736 | 83.9611 | 0.7 | 43 | 263.6 | 37.6 | 41.9806 | 0 | 0 | 0 | 67.8 | 730.6 | 106.1844
1737 | 173.8253 | 2.1 | 43.2 | 252.5 | 0 | 86.9127 | 0 | 0 | 0 | 69.4 | 236.9 | 145.5356
1738 | 255.8001 | 3.5 | 43.4 | 253.1 | 0 | 127.9001 | 0 | 0 | 0 | 88.4 | 291 | 121.7893
1739 | 275.4058 | 3.5 | 43.4 | 243.4 | 0 | 137.7029 | 0 | 0 | 0 | 76.4 | 292.5 | 168.6499
1740 | 271.0815 | 2.8 | 43.3 | 228.2 | 0 | 135.5407 | 0 | 0 | 0 | 44.6 | 291.5 | 175.6241
1741 | 251.3385 | 1.4 | 43.1 | 212.2 | 75.1 | 125.6692 | 0 | 0 | 0 | 8.6 | 762 | 193.5198
1742 | 216.8701 | 2.1 | 43.2 | 206.6 | 37.6 | 108.4351 | 0 | 0 | 0 | 3.3 | 695.5 | 116.2605
1743 | 223.9224 | 3.5 | 43.4 | 211.6 | 0 | 111.9612 | 0 | 0 | 0 | 6.8 | 207 | 123.329
1744 | 216.761 | 2.8 | 43.3 | 206 | 0 | 108.3805 | 0 | 0 | 0 | 4.2 | 264.5 | 152.2864
1745 | 188.6861 | 2.1 | 43.2 | 195.9 | 0 | 94.343 | 0 | 0 | 0 | 2.1 | 273.9 | 163.7844
1746 | 160.5603 | 0.7 | 43 | 195.1 | 37.6 | 80.2802 | 0 | 0 | 0 | 0 | 762.3 | 481.0461
1747 | 109.239 | 0 | 42.9 | 147.5 | 75.1 | 54.6195 | 0 | 0 | 0 | 0 | 701 | 491.0961
1748 | 66.1409 | 0 | 42.9 | 119 | 75.1 | 33.0704 | 0 | 0 | 0 | 0 | 616 | 317.7182
1749 | 57.1469 | 0 | 42.9 | 129.1 | 75.1 | 28.5735 | 0 | 0 | 0 | 0 | 653.5 | 197.5689
1750 | 40.7207 | 0 | 42.9 | 134.4 | 93.9 | 20.3604 | 0 | 0 | 0 | 0 | 668.2 | 246.9185
1751 | 42.0962 | 0 | 0 | 28 | 0 | 21.0481 | 0 | 0 | 0 | 0 | 170.6 | 176.7437
1752 | 43.4223 | 0 | 0 | 46.8 | 0 | 21.7112 | 0 | 0 | 0 | 0 | 240.4 | 134.3348
1753 | 41.8876 | 0 | 0 | 58.9 | 0 | 20.9438 | 0 | 0 | 0 | 0 | 263.5 | 87.8862
1754 | 43.8361 | 0 | 0 | 70.5 | 0 | 21.918 | 0 | 0 | 0 | 0 | 286.7 | 84.208
1755 | 42.5561 | 0 | 0 | 76.5 | 0 | 21.278 | 0 | 0 | 0 | 0 | 296.9 | 82.9082
1756 | 43.5624 | 0 | 0 | 81.1 | 0 | 21.7812 | 0 | 0 | 0 | 0 | 304.7 | 83.7331
1757 | 42.1293 | 0 | 0 | 86.2 | 0 | 21.0647 | 0 | 0 | 0 | 0 | 314.9 | 79.5961
1758 | 41.1221 | 0 | 0 | 91.6 | 0 | 20.561 | 0 | 0 | 0 | 0 | 321.8 | 94.9174
1759 | 60.5706 | 0 | 42.9 | 252 | 56.3 | 30.2853 | 0 | 0 | 0 | 1.6 | 854.8 | 116.7572
1760 | 91.1253 | 0.7 | 43 | 288 | 37.6 | 45.5626 | 0 | 0 | 0 | 58.8 | 811.2 | 133.4977
1761 | 150.1922 | 2.1 | 43.2 | 269.5 | 0 | 75.0961 | 0 | 0 | 0 | 58.7 | 271.3 | 135.4127
1762 | 254.7783 | 3.5 | 43.4 | 260.1 | 0 | 127.3892 | 0 | 0 | 0 | 78.7 | 312.5 | 149.8363
1763 | 273.1927 | 3.5 | 43.4 | 240.3 | 0 | 136.5963 | 0 | 0 | 0 | 73.4 | 302.1 | 228.7106
1764 | 239.1563 | 2.8 | 43.3 | 213.7 | 0 | 119.5782 | 0 | 0 | 0 | 52.4 | 286.3 | 145.0101
1765 | 222.3148 | 1.4 | 43.1 | 190.8 | 75.1 | 111.1574 | 0 | 0 | 0 | 25.2 | 742.9 | 102.2209
1766 | 220.1249 | 2.1 | 43.2 | 178.5 | 37.6 | 110.0625 | 0 | 0 | 0 | 24.8 | 677.4 | 152.4554
1767 | 240.8175 | 3.5 | 43.4 | 174.9 | 0 | 120.4088 | 0 | 0 | 0 | 39.7 | 172.8 | 157.0674
1768 | 287.8275 | 2.8 | 43.3 | 167.5 | 0 | 143.9138 | 0 | 0 | 0 | 37.7 | 219.5 | 109.9343
1769 | 289.4915 | 2.1 | 43.2 | 160.9 | 0 | 144.7457 | 0 | 0 | 0 | 28.8 | 227.7 | 128.3474
1770 | 249.1439 | 0.7 | 43 | 161.9 | 37.6 | 124.572 | 0 | 0 | 0 | 15 | 708.8 | 136.967
1771 | 175.8479 | 0 | 42.9 | 120.8 | 75.1 | 87.9239 | 0 | 0 | 0 | 0 | 641.6 | 296.2859
1772 | 102.3603 | 0 | 42.9 | 91.7 | 75.1 | 51.1801 | 0 | 0 | 0 | 0 | 552.8 | 286.0785
1773 | 61.5097 | 0 | 42.9 | 103.5 | 75.1 | 30.7548 | 0 | 0 | 0 | 0 | 591.7 | 188.5856
1774 | 43.8237 | 0 | 42.9 | 111.4 | 93.9 | 21.9118 | 0 | 0 | 0 | 0 | 607.3 | 167.4707
1775 | 41.8355 | 0 | 0 | 11.3 | 0 | 20.9178 | 0 | 0 | 0 | 0 | 131.9 | 166.0954
1776 | 42.7132 | 0 | 0 | 35.2 | 0 | 21.3566 | 0 | 0 | 0 | 0 | 215 | 187.5719
1777 | 40.7068 | 0 | 0 | 45.4 | 0 | 20.3534 | 0 | 0 | 0 | 0 | 230.3 | 138.91
1778 | 39.9983 | 0 | 0 | 61 | 0 | 19.9991 | 0 | 0 | 0 | 0 | 261.7 | 102.4587
1779 | 40.9907 | 0 | 0 | 69 | 0 | 20.4953 | 0 | 0 | 0 | 0 | 275.2 | 107.2752
1780 | 42.2276 | 0 | 0 | 72.6 | 0 | 21.1138 | 0 | 0 | 0 | 0.3 | 278.6 | 86.1062
1781 | 41.057 | 0 | 0 | 78.4 | 0 | 20.5285 | 0 | 0 | 0 | 3.4 | 289.3 | 79.4779
1782 | 44.1079 | 0 | 0 | 84 | 0 | 22.0539 | 0 | 0 | 0 | 8.4 | 296.5 | 111.6345
1783 | 62.9105 | 0 | 42.9 | 243.2 | 56.3 | 31.4553 | 0 | 0 | 0 | 27.4 | 826.9 | 107.5143
1784 | 110.1195 | 0.7 | 43 | 280.2 | 37.6 | 55.0597 | 0 | 0 | 0 | 70.4 | 783 | 111.7527
1785 | 183.6151 | 2.1 | 43.2 | 263.8 | 0 | 91.8076 | 0 | 0 | 0 | 67.6 | 255.3 | 150.0325
1786 | 278.3963 | 3.5 | 43.4 | 256 | 0 | 139.1981 | 0 | 0 | 0 | 81.8 | 298.7 | 156.0115
1787 | 336.6502 | 3.5 | 43.4 | 239.5 | 0 | 168.3251 | 0 | 0 | 0 | 68.2 | 292.2 | 91.5779
1788 | 291.4195 | 2.8 | 43.3 | 218.6 | 0 | 145.7098 | 0 | 0 | 0 | 37.8 | 283.2 | 115.7935
1789 | 252.0597 | 1.4 | 43.1 | 198.8 | 75.1 | 126.0298 | 0 | 0 | 0 | 4.4 | 745.9 | 121.8577
1790 | 241.5858 | 2.1 | 43.2 | 184 | 37.6 | 120.7929 | 0 | 0 | 0 | 0.4 | 674.8 | 319.5032
1791 | 241.2545 | 3.5 | 43.4 | 180.5 | 0 | 120.6273 | 0 | 0 | 0 | 1.1 | 172.9 | 219.8421
1792 | 224.2708 | 2.8 | 43.3 | 170.3 | 0 | 112.1354 | 0 | 0 | 0 | 0 | 217 | 269.7167
1793 | 183.8209 | 2.1 | 43.2 | 160.7 | 0 | 91.9105 | 0 | 0 | 0 | 0 | 222.2 | 161.9707
1794 | 181.3608 | 0.7 | 43 | 163.6 | 37.6 | 90.6804 | 0 | 0 | 0 | 0 | 705.6 | 300.0123
1795 | 117.2883 | 0 | 42.9 | 121.9 | 75.1 | 58.6442 | 0 | 0 | 0 | 0 | 636.2 | 215.8097
1796 | 69.3517 | 0 | 42.9 | 94.8 | 75.1 | 34.6758 | 0 | 0 | 0 | 0 | 554.2 | 249.6598
1797 | 53.6603 | 0 | 42.9 | 105.4 | 75.1 | 26.8301 | 0 | 0 | 0 | 0 | 590.3 | 252.6552
1798 | 42.888 | 0 | 42.9 | 105.7 | 93.9 | 21.444 | 0 | 0 | 0 | 0 | 586.8 | 248.0307
1799 | 41.6759 | 0 | 0 | 4.1 | 0 | 20.8379 | 0 | 0 | 0 | 0 | 104 | 258.7494
1800 | 45.2103 | 0 | 0 | 15.5 | 0 | 22.6051 | 0 | 0 | 0 | 0 | 160.9 | 220.4078
1801 | 42.637 | 0 | 0 | 24.5 | 0 | 21.3185 | 0 | 0 | 0 | 0 | 173.6 | 119.5242
1802 | 42.3069 | 0 | 0 | 30.6 | 0 | 21.1535 | 0 | 0 | 0 | 0 | 181 | 111.6326
1803 | 41.4934 | 0 | 0 | 36.2 | 0 | 20.7467 | 0 | 0 | 0 | 0 | 188.7 | 119.9726
1804 | 43.3808 | 0 | 0 | 41.3 | 0 | 21.6904 | 0 | 0 | 0 | 0 | 196.2 | 175.0821
1805 | 42.3701 | 0 | 0 | 45.6 | 0 | 21.1851 | 0 | 0 | 0 | 0 | 202.7 | 88.5964
1806 | 42.4237 | 0 | 0 | 49.1 | 0 | 21.2119 | 0 | 0 | 0 | 0 | 204 | 97.9157
1807 | 47.7005 | 0 | 42.9 | 202.7 | 56.3 | 23.8502 | 0 | 0 | 0 | 0 | 723.8 | 116.9562
1808 | 70.9459 | 0 | 42.9 | 195.2 | 37.6 | 35.473 | 0 | 0 | 0 | 0 | 662.4 | 121.2368
1809 | 69.2246 | 0 | 42.9 | 162.4 | 0 | 34.6123 | 0 | 0 | 0 | 0 | 139.1 | 165.9988
1810 | 67.5138 | 0 | 42.9 | 131.1 | 0 | 33.7569 | 0 | 0 | 0 | 0 | 150.2 | 146.5087
1811 | 65.8347 | 0 | 42.9 | 99 | 0 | 32.9173 | 0 | 0 | 0 | 0 | 120.9 | 172.8065
1812 | 57.7909 | 0 | 42.9 | 69.2 | 0 | 28.8955 | 0 | 0 | 0 | 0 | 89.6 | 344.4398
1813 | 53.6609 | 0 | 42.9 | 44.5 | 75.1 | 26.8305 | 0 | 0 | 0 | 0 | 466.2 | 212.0276
1814 | 55.1055 | 0 | 42.9 | 25.2 | 37.6 | 27.5527 | 0 | 0 | 0 | 0 | 375 | 130.0943
1815 | 54.4193 | 0 | 42.9 | 11.2 | 0 | 27.2096 | 0 | 0 | 0 | 0 | 3.4 | 153.7451
1816 | 57.053 | 0 | 42.9 | 6.9 | 0 | 28.5265 | 0 | 0 | 0 | 0 | 4.4 | 262.9468
1817 | 68.7743 | 0 | 42.9 | 9.2 | 0 | 34.3871 | 0 | 0 | 0 | 0 | 4.1 | 161.7726
1818 | 77.9192 | 0 | 42.9 | 21.2 | 37.6 | 38.9596 | 0 | 0 | 0 | 0 | 386.7 | 154.7166
1819 | 75.8839 | 0 | 42.9 | 16.4 | 75.1 | 37.942 | 0 | 0 | 0 | 0 | 310.5 | 204.4578
1820 | 64.2352 | 0 | 42.9 | 0.8 | 75.1 | 32.1176 | 0 | 0 | 0 | 0 | 248 | 157.098
1821 | 48.9377 | 0 | 42.9 | 9.4 | 75.1 | 24.4688 | 0 | 0 | 0 | 0 | 301 | 236.822
1822 | 43.2109 | 0 | 42.9 | 23.3 | 93.9 | 21.6055 | 0 | 0 | 0 | 0 | 327.1 | 285.2549
1823 | 39.7581 | 0 | 0 | 0 | 0 | 19.879 | 0 | 0 | 0 | 0 | 1 | 163.7292
1824 | 41.5993 | 0 | 0 | 0 | 0 | 20.7997 | 0 | 0 | 0 | 0 | 8.5 | 128.1489
1825 | 42.456 | 0 | 0 | 0 | 0 | 21.228 | 0 | 0 | 0 | 0 | 26.5 | 97.5489
1826 | 41.5653 | 0 | 0 | 0.8 | 0 | 20.7826 | 0 | 0 | 0 | 0 | 70.4 | 79.5971
1827 | 42.3506 | 0 | 0 | 9.3 | 0 | 21.1753 | 0 | 0 | 0 | 0 | 115.9 | 80.0704
1828 | 41.7745 | 0 | 0 | 25.4 | 0 | 20.8872 | 0 | 0 | 0 | 0 | 149.2 | 77.9254
1829 | 42.8177 | 0 | 0 | 41 | 0 | 21.4088 | 0 | 0 | 0 | 0 | 178.9 | 80.6604
1830 | 40.6978 | 0 | 0 | 54 | 0 | 20.3489 | 0 | 0 | 0 | 0 | 198.8 | 86.8155
1831 | 44.8926 | 0 | 42.9 | 219.1 | 56.3 | 22.4463 | 0 | 0 | 0 | 0 | 697.9 | 106.7902
1832 | 65.8433 | 0 | 42.9 | 182.9 | 37.6 | 32.9217 | 0 | 0 | 0 | 0 | 614.1 | 221.9471
1833 | 67.7859 | 0 | 42.9 | 153.7 | 0 | 33.893 | 0 | 0 | 0 | 0 | 131 | 161.6587
1834 | 64.5764 | 0 | 42.9 | 127.8 | 0 | 32.2882 | 0 | 0 | 0 | 0 | 146.3 | 237.3655
1835 | 60.2951 | 0 | 42.9 | 104.1 | 0 | 30.1476 | 0 | 0 | 0 | 0 | 116.8 | 208.0542
1836 | 59.1785 | 0 | 42.9 | 81.4 | 0 | 29.5892 | 0 | 0 | 0 | 0 | 90.1 | 208.6987
1837 | 57.9614 | 0 | 42.9 | 62.5 | 75.1 | 28.9807 | 0 | 0 | 0 | 0 | 485.4 | 285.7297
1838 | 56.3024 | 0 | 42.9 | 41.2 | 37.6 | 28.1512 | 0 | 0 | 0 | 0 | 378.4 | 248.6509
1839 | 54.7354 | 0 | 42.9 | 30.5 | 0 | 27.3677 | 0 | 0 | 0 | 0 | 4.3 | 240.2382
1840 | 53.7294 | 0 | 42.9 | 28.5 | 0 | 26.8647 | 0 | 0 | 0 | 0 | 6.7 | 160.1542
1841 | 57.729 | 0 | 42.9 | 32.4 | 0 | 28.8645 | 0 | 0 | 0 | 0 | 8.6 | 213.7224
1842 | 65.8585 | 0 | 42.9 | 49.2 | 37.6 | 32.9293 | 0 | 0 | 0 | 0 | 440.9 | 191.913
1843 | 65.6664 | 0 | 42.9 | 62.2 | 75.1 | 32.8332 | 0 | 0 | 0 | 0 | 371.5 | 237.6744
1844 | 51.8581 | 0 | 42.9 | 31.6 | 75.1 | 25.929 | 0 | 0 | 0 | 0 | 320.9 | 288.6459
1845 | 43.2615 | 0 | 42.9 | 54.2 | 75.1 | 21.6307 | 0 | 0 | 0 | 0 | 384.6 | 516.2202
1846 | 42.6122 | 0 | 42.9 | 73.5 | 93.9 | 21.3061 | 0 | 0 | 0 | 0 | 427.7 | 353.6961
1847 | 41.4692 | 0 | 0 | 0 | 0 | 20.7346 | 0 | 0 | 0 | 0 | 23.6 | 276.744
1848 | 39.7789 | 0 | 0 | 3.8 | 0 | 19.8894 | 0 | 0 | 0 | 0 | 85.2 | 232.1876
1849 | 42.95 | 0 | 0 | 16.6 | 0 | 21.475 | 0 | 0 | 0 | 0 | 130.3 | 100.0748
1850 | 41.3412 | 0 | 0 | 36.3 | 0 | 20.6706 | 0 | 0 | 0 | 0 | 169.2 | 82.9076
1851 | 42.1451 | 0 | 0 | 54.2 | 0 | 21.0726 | 0 | 0 | 0 | 0 | 205.1 | 80.1867
1852 | 42.1411 | 0 | 0 | 69.2 | 0 | 21.0705 | 0 | 0 | 0 | 0 | 235.4 | 78.6493
1853 | 42.9754 | 0 | 0 | 82.2 | 0 | 21.4877 | 0 | 0 | 0 | 0 | 262.2 | 80.7813
1854 | 44.4934 | 0 | 0 | 93.4 | 0 | 22.2467 | 0 | 0 | 0 | 0 | 282 | 98.3944
1855 | 60.0992 | 0 | 42.9 | 259.5 | 56.3 | 30.0496 | 0 | 0 | 0 | 0.8 | 791.6 | 102.8236
1856 | 94.8211 | 0.7 | 43 | 271 | 37.6 | 47.4105 | 0 | 0 | 0 | 55.2 | 691.6 | 128.8097
1857 | 162.8506 | 2.1 | 43.2 | 221.7 | 0 | 81.4253 | 0 | 0 | 0 | 49 | 165.7 | 103.4209
1858 | 251.045 | 3.5 | 43.4 | 181.6 | 0 | 125.5225 | 0 | 0 | 0 | 60.7 | 161.8 | 263.7626
1859 | 277.4036 | 3.5 | 43.4 | 135.9 | 0 | 138.7018 | 0 | 0 | 0 | 49 | 113.4 | 285.6507
1860 | 260.1973 | 2.8 | 43.3 | 87.3 | 0 | 130.0986 | 0 | 0 | 0 | 26.5 | 67 | 186.5874
1861 | 214.0092 | 1.4 | 43.1 | 39.2 | 75.1 | 107.0046 | 0 | 0 | 0 | 2.1 | 440.9 | 251.6036
1862 | 182.7343 | 2.1 | 43.2 | 10.7 | 37.6 | 91.3672 | 0 | 0 | 0 | 0.1 | 312.9 | 273.4764
1863 | 184.2846 | 3.5 | 43.4 | 4 | 0 | 92.1423 | 0 | 0 | 0 | 1.7 | 0 | 156.151
1864 | 195.0197 | 2.8 | 43.3 | 0.7 | 0 | 97.5098 | 0 | 0 | 0 | 0.9 | 0 | 165.778
1865 | 219.0343 | 2.1 | 43.2 | 0 | 0 | 109.5172 | 0 | 0 | 0 | 0 | 0 | 317.0711
1866 | 209.0362 | 0.7 | 43 | 3.2 | 37.6 | 104.5181 | 0 | 0 | 0 | 0 | 305.9 | 236.6064
1867 | 140.7783 | 0 | 42.9 | 0 | 75.1 | 70.3891 | 0 | 0 | 0 | 0 | 270.7 | 284.5739
1868 | 84.4663 | 0 | 42.9 | 0 | 75.1 | 42.2331 | 0 | 0 | 0 | 0 | 237.1 | 289.945
1869 | 61.6176 | 0 | 42.9 | 0 | 75.1 | 30.8088 | 0 | 0 | 0 | 0 | 308.2 | 262.3753
1870 | 42.4994 | 0 | 42.9 | 10.3 | 93.9 | 21.2497 | 0 | 0 | 0 | 0 | 355.6 | 283.5021
1871 | 42.7005 | 0 | 0 | 0 | 0 | 21.3503 | 0 | 0 | 0 | 0 | 0.3 | 553.8265
1872 | 42.7643 | 0 | 0 | 0 | 0 | 21.3822 | 0 | 0 | 0 | 0 | 12.5 | 165.4043
1873 | 41.811 | 0 | 0 | 0 | 0 | 20.9055 | 0 | 0 | 0 | 0 | 59.9 | 129.1987
1874 | 43.0789 | 0 | 0 | 5.3 | 0 | 21.5395 | 0 | 0 | 0 | 0 | 120.5 | 102.2217
1875 | 42.1814 | 0 | 0 | 19.9 | 0 | 21.0907 | 0 | 0 | 0 | 0 | 178.8 | 86.3395
1876 | 41.7236 | 0 | 0 | 44.9 | 0 | 20.8618 | 0 | 0 | 0 | 0 | 227.4 | 76.6152
1877 | 42.6918 | 0 | 0 | 66.1 | 0 | 21.3459 | 0 | 0 | 0 | 0 | 267.6 | 76.6157
1878 | 41.9895 | 0 | 0 | 84.4 | 0 | 20.9948 | 0 | 0 | 0 | 0 | 298.6 | 80.3035
1879 | 53.1244 | 0 | 42.9 | 263.1 | 56.3 | 26.5622 | 0 | 0 | 0 | 5 | 806.9 | 154.9752
1880 | 90.3976 | 0.7 | 43 | 265.6 | 37.6 | 45.1988 | 0 | 0 | 0 | 65.8 | 684.2 | 149.3651
1881 | 158.7618 | 2.1 | 43.2 | 215.8 | 0 | 79.3809 | 0 | 0 | 0 | 73.6 | 157.8 | 134.6835
1882 | 244.6603 | 3.5 | 43.4 | 175.9 | 0 | 122.3301 | 0 | 0 | 0 | 101.1 | 143.9 | 263.6432
1883 | 268.6511 | 3.5 | 43.4 | 118.9 | 0 | 134.3255 | 0 | 0 | 0 | 97.3 | 90.4 | 168.8653
1884 | 237.5627 | 2.8 | 43.3 | 56.3 | 0 | 118.7814 | 0 | 0 | 0 | 70.8 | 41 | 140.6979
1885 | 232.6176 | 1.4 | 43.1 | 10.2 | 75.1 | 116.3088 | 0 | 0 | 0 | 30.8 | 420.8 | 248.001
1886 | 223.8189 | 2.1 | 43.2 | 0.6 | 37.6 | 111.9095 | 0 | 0 | 0 | 18.8 | 285.9 | 125.0219
1887 | 221.664 | 3.5 | 43.4 | 0 | 0 | 110.832 | 0 | 0 | 0 | 24.7 | 0 | 94.6767
1888 | 211.7143 | 2.8 | 43.3 | 0 | 0 | 105.8571 | 0 | 0 | 0 | 14.8 | 0 | 165.0889
1889 | 188.3399 | 2.1 | 43.2 | 0 | 0 | 94.17 | 0 | 0 | 0 | 1.8 | 0 | 129.7877
1890 | 187.9841 | 0.7 | 43 | 0 | 37.6 | 93.9921 | 0 | 0 | 0 | 0 | 300.5 | 216.8949
1891 | 168.269 | 0 | 42.9 | 0 | 75.1 | 84.1345 | 0 | 0 | 0 | 0 | 286.8 | 356.4968
1892 | 105.3086 | 0 | 42.9 | 0 | 75.1 | 52.6543 | 0 | 0 | 0 | 0 | 266.4 | 262.2389
1893 | 62.8715 | 0 | 42.9 | 0 | 75.1 | 31.4357 | 0 | 0 | 0 | 0 | 339.1 | 207.4604
1894 | 41.5411 | 0 | 42.9 | 4.7 | 93.9 | 20.7705 | 0 | 0 | 0 | 0 | 389.3 | 188.5019
1895 | 43.7242 | 0 | 0 | 0 | 0 | 21.8621 | 0 | 0 | 0 | 0 | 0.1 | 211.7169
1896 | 41.1661 | 0 | 0 | 0 | 0 | 20.583 | 0 | 0 | 0 | 0 | 15.1 | 114.0435
1897 | 41.008 | 0 | 0 | 0 | 0 | 20.504 | 0 | 0 | 0 | 0 | 65.2 | 116.2479
1898 | 43.6064 | 0 | 0 | 4.9 | 0 | 21.8032 | 0 | 0 | 0 | 0 | 124 | 115.2612
1899 | 40.7582 | 0 | 0 | 15.5 | 0 | 20.3791 | 0 | 0 | 0 | 0 | 180.9 | 79.5976
1900 | 41.9849 | 0 | 0 | 35.7 | 0 | 20.9924 | 0 | 0 | 0 | 0 | 228.4 | 78.5265
1901 | 41.891 | 0 | 0 | 58.1 | 0 | 20.9455 | 0 | 0 | 0 | 0 | 268.9 | 78.5284
1902 | 43.4068 | 0 | 0 | 77.7 | 0 | 21.7034 | 0 | 0 | 0 | 0 | 301.4 | 97.5519
1903 | 54.7432 | 0 | 42.9 | 265 | 56.3 | 27.3716 | 0 | 0 | 0 | 0 | 813.6 | 97.192
1904 | 89.0661 | 0.7 | 43 | 263.5 | 37.6 | 44.5331 | 0 | 0 | 0 | 57.1 | 680.6 | 116.4298
1905 | 144.669 | 2.1 | 43.2 | 206.4 | 0 | 72.3345 | 0 | 0 | 0 | 55.7 | 142.2 | 156.7223
1906 | 211.6045 | 3.5 | 43.4 | 159.3 | 0 | 105.8023 | 0 | 0 | 0 | 73.4 | 119.2 | 109.9381
1907 | 226.3755 | 3.5 | 43.4 | 95.2 | 0 | 113.1877 | 0 | 0 | 0 | 69.3 | 61.9 | 133.7203
1908 | 221.8267 | 2.8 | 43.3 | 30.5 | 0 | 110.9134 | 0 | 0 | 0 | 48.8 | 17.7 | 107.7642
1909 | 224.9985 | 1.4 | 43.1 | 1 | 75.1 | 112.4992 | 0 | 0 | 0 | 22.7 | 383.2 | 157.3388
1910 | 204.7202 | 2.1 | 43.2 | 0 | 37.6 | 102.3601 | 0 | 0 | 0 | 21.7 | 244.4 | 293.3882
1911 | 202.3875 | 3.5 | 43.4 | 0 | 0 | 101.1937 | 0 | 0 | 0 | 39 | 0 | 304.6369
1912 | 180.1722 | 2.8 | 43.3 | 0 | 0 | 90.0861 | 0 | 0 | 0 | 38 | 0 | 242.0612
1913 | 136.0296 | 2.1 | 43.2 | 0 | 0 | 68.0148 | 0 | 0 | 0 | 28.5 | 0 | 140.3283
1914 | 94.1312 | 0.7 | 43 | 0 | 37.6 | 47.0656 | 0 | 0 | 0 | 13.5 | 222.5 | 220.5883
1915 | 70.0192 | 0 | 42.9 | 0 | 75.1 | 35.0096 | 0 | 0 | 0 | 0 | 224.2 | 220.3079
1916 | 47.8514 | 0 | 42.9 | 0 | 75.1 | 23.9257 | 0 | 0 | 0 | 0 | 197.4 | 314.6331
1917 | 40.0098 | 0 | 42.9 | 0 | 75.1 | 20.0049 | 0 | 0 | 0 | 0 | 266.1 | 242.2157
1918 | 41.2299 | 0 | 42.9 | 0 | 93.9 | 20.615 | 0 | 0 | 0 | 0 | 305.1 | 279.843
1919 | 39.0921 | 0 | 0 | 0 | 0 | 19.546 | 0 | 0 | 0 | 0 | 0 | 181.2136
1920 | 39.5021 | 0 | 0 | 0 | 0 | 19.7511 | 0 | 0 | 0 | 0 | 0 | 129.1247
1921 | 41.7961 | 0 | 0 | 0 | 0 | 20.8981 | 0 | 0 | 0 | 0 | 0.3 | 115.904
1922 | 44.203 | 0 | 0 | 0 | 0 | 22.1015 | 0 | 0 | 0 | 0 | 9.5 | 89.4275
1923 | 43.1186 | 0 | 0 | 0 | 0 | 21.5593 | 0 | 0 | 0 | 0 | 39.2 | 83.5019
1924 | 39.0642 | 0 | 0 | 0.8 | 0 | 19.5321 | 0 | 0 | 0 | 0 | 85.9 | 78.4071
1925 | 41.7239 | 0 | 0 | 7.7 | 0 | 20.862 | 0 | 0 | 0 | 0 | 127.2 | 77.5625
1926 | 41.4741 | 0 | 0 | 14.3 | 0 | 20.7371 | 0 | 0 | 0 | 0 | 158.9 | 86.1039
1927 | 60.1154 | 0 | 42.9 | 199.9 | 56.3 | 30.0577 | 0 | 0 | 0 | 0 | 667.6 | 111.6268
1928 | 96.0465 | 0.7 | 43 | 197.9 | 37.6 | 48.0233 | 0 | 0 | 0 | 49.2 | 537 | 138.4175
1929 | 196.4856 | 2.1 | 43.2 | 143.2 | 0 | 98.2428 | 0 | 0 | 0 | 44.8 | 43.8 | 188.0237
1930 | 320.784 | 3.5 | 43.4 | 92.6 | 0 | 160.392 | 0 | 0 | 0 | 61.2 | 17.6 | 239.4486
1931 | 363.5468 | 3.5 | 43.4 | 35 | 0 | 181.7734 | 0 | 0 | 0 | 59.3 | 3.8 | 150.9281
1932 | 348.029 | 2.8 | 43.3 | 0.2 | 0 | 174.0145 | 0 | 0 | 0 | 47 | 0 | 197.2258
1933 | 318.8501 | 1.4 | 43.1 | 0 | 75.1 | 159.4251 | 0 | 0 | 0 | 28.7 | 251.1 | 205.968
1934 | 292.0914 | 2.1 | 43.2 | 0 | 37.6 | 146.0457 | 0 | 0 | 0 | 29.1 | 156.1 | 172.0798
1935 | 288.082 | 3.5 | 43.4 | 0 | 0 | 144.041 | 0 | 0 | 0 | 42.9 | 0 | 142.1605
1936 | 265.6935 | 2.8 | 43.3 | 0 | 0 | 132.8467 | 0 | 0 | 0 | 42.1 | 0 | 111.7518
1937 | 226.955 | 2.1 | 43.2 | 0 | 0 | 113.4775 | 0 | 0 | 0 | 35.9 | 0 | 149.1436
1938 | 206.1208 | 0.7 | 43 | 0 | 37.6 | 103.0604 | 0 | 0 | 0 | 24.8 | 97.2 | 181.6643
1939 | 132.1382 | 0 | 42.9 | 0 | 75.1 | 66.0691 | 0 | 0 | 0 | 0 | 97.4 | 243.9736
1940 | 72.5566 | 0 | 42.9 | 0 | 75.1 | 36.2783 | 0 | 0 | 0 | 0 | 69.6 | 511.1919
1941 | 57.2827 | 0 | 42.9 | 0 | 75.1 | 28.6413 | 0 | 0 | 0 | 0 | 144.8 | 241.7607
1942 | 42.2629 | 0 | 42.9 | 0 | 93.9 | 21.1314 | 0 | 0 | 0 | 0 | 186.1 | 307.9444
1943 | 41.587 | 0 | 0 | 0 | 0 | 20.7935 | 0 | 0 | 0 | 0 | 0 | 182.3032
1944 | 43.311 | 0 | 0 | 0 | 0 | 21.6555 | 0 | 0 | 0 | 0 | 0 | 133.5851
1945 | 41.4927 | 0 | 0 | 0 | 0 | 20.7464 | 0 | 0 | 0 | 0 | 0 | 102.2185
1946 | 40.2425 | 0 | 0 | 0 | 0 | 20.1213 | 0 | 0 | 0 | 0 | 0 | 85.9836
1947 | 41.4366 | 0 | 0 | 0 | 0 | 20.7183 | 0 | 0 | 0 | 0 | 1.3 | 87.5242
1948 | 39.4082 | 0 | 0 | 0 | 0 | 19.7041 | 0 | 0 | 0 | 0 | 10.6 | 80.1882
1949 | 39.9701 | 0 | 0 | 0 | 0 | 19.985 | 0 | 0 | 0 | 1.1 | 36.7 | 79.835
1950 | 41.1016 | 0 | 0 | 1.1 | 0 | 20.5508 | 0 | 0 | 0 | 6.4 | 77.4 | 86.9337
1951 | 59.9613 | 0 | 42.9 | 159.5 | 56.3 | 29.9807 | 0 | 0 | 0 | 24.5 | 601.5 | 95.1589
1952 | 97.1672 | 0.7 | 43 | 181.3 | 37.6 | 48.5836 | 0 | 0 | 0 | 65.4 | 490.9 | 106.7919
1953 | 141.8419 | 2.1 | 43.2 | 132.3 | 0 | 70.921 | 0 | 0 | 0 | 57.1 | 22.3 | 97.9149
1954 | 257.6129 | 3.5 | 43.4 | 92.2 | 0 | 128.8064 | 0 | 0 | 0 | 68.3 | 11.1 | 85.8667
1955 | 305.1838 | 3.5 | 43.4 | 50.2 | 0 | 152.5919 | 0 | 0 | 0 | 55.3 | 3 | 82.7922
1956 | 295.0568 | 2.8 | 43.3 | 8.5 | 0 | 147.5284 | 0 | 0 | 0 | 31.1 | 0 | 177.8497
1957 | 228.0797 | 1.4 | 43.1 | 0 | 75.1 | 114.0399 | 0 | 0 | 0 | 2.9 | 311.5 | 199.6881
1958 | 198.0609 | 2.1 | 43.2 | 0 | 37.6 | 99.0305 | 0 | 0 | 0 | 0.2 | 218.8 | 137.6808
1959 | 186.3065 | 3.5 | 43.4 | 0 | 0 | 93.1533 | 0 | 0 | 0 | 0.9 | 0 | 109.9353
1960 | 176.4088 | 2.8 | 43.3 | 0 | 0 | 88.2044 | 0 | 0 | 0 | 0 | 0 | 163.8881
1961 | 144.6963 | 2.1 | 43.2 | 0 | 0 | 72.3482 | 0 | 0 | 0 | 0 | 0 | 141.5568
1962 | 141.1762 | 0.7 | 43 | 0 | 37.6 | 70.5881 | 0 | 0 | 0 | 0 | 248.1 | 250.2105
1963 | 100.89 | 0 | 42.9 | 0 | 75.1 | 50.445 | 0 | 0 | 0 | 0 | 231.6 | 313.2386
1964 | 62.097 | 0 | 42.9 | 0 | 75.1 | 31.0485 | 0 | 0 | 0 | 0 | 204.6 | 239.8774
1965 | 48.1554 | 0 | 42.9 | 0 | 75.1 | 24.0777 | 0 | 0 | 0 | 0 | 278.2 | 254.442
1966 | 43.383 | 0 | 42.9 | 0.2 | 93.9 | 21.6915 | 0 | 0 | 0 | 0 | 323 | 195.7181
1967 | 40.011 | 0 | 0 | 0 | 0 | 20.0055 | 0 | 0 | 0 | 0 | 0 | 222.1602
1968 | 42.4668 | 0 | 0 | 0 | 0 | 21.2334 | 0 | 0 | 0 | 0 | 0.1 | 200.4572
1969 | 41.7813 | 0 | 0 | 0 | 0 | 20.8906 | 0 | 0 | 0 | 0 | 6.5 | 93.4845
1970 | 39.9276 | 0 | 0 | 0 | 0 | 19.9638 | 0 | 0 | 0 | 0 | 32.3 | 76.7361
1971 | 40.4935 | 0 | 0 | 2 | 0 | 20.2468 | 0 | 0 | 0 | 0 | 84.3 | 83.1467
1972 | 41.41 | 0 | 0 | 9.7 | 0 | 20.705 | 0 | 0 | 0 | 0 | 130.7 | 79.7173
1973 | 40.832 | 0 | 0 | 16.3 | 0 | 20.416 | 0 | 0 | 0 | 0 | 169.8 | 78.4056
1974 | 40.7006 | 0 | 0 | 25.7 | 0 | 20.3503 | 0 | 0 | 0 | 0 | 198.6 | 99.8315
1975 | 42.2003 | 0 | 42.9 | 213 | 56.3 | 21.1001 | 0 | 0 | 0 | 0 | 703.7 | 105.8212
1976 | 57.1795 | 0 | 42.9 | 196.1 | 37.6 | 28.5897 | 0 | 0 | 0 | 0 | 588.6 | 114.5285
1977 | 60.4225 | 0 | 42.9 | 148.2 | 0 | 30.2112 | 0 | 0 | 0 | 0 | 91 | 91.5792
1978 | 59.5513 | 0 | 42.9 | 98.3 | 0 | 29.7756 | 0 | 0 | 0 | 0 | 68.9 | 89.785
1979 | 56.0008 | 0 | 42.9 | 40.1 | 0 | 28.0004 | 0 | 0 | 0 | 0 | 20.6 | 140.8489
1980 | 51.4691 | 0 | 42.9 | 1.2 | 0 | 25.7346 | 0 | 0 | 0 | 0 | 3.4 | 198.8813
1981 | 52.8523 | 0 | 42.9 | 0 | 75.1 | 26.4262 | 0 | 0 | 0 | 0 | 329.1 | 159.1146
1982 | 52.8883 | 0 | 42.9 | 0 | 37.6 | 26.4441 | 0 | 0 | 0 | 0 | 201.2 | 249.5058
1983 | 52.1156 | 0 | 42.9 | 0 | 0 | 26.0578 | 0 | 0 | 0 | 0 | 0 | 393.0259
1984 | 51.462 | 0 | 42.9 | 0 | 0 | 25.731 | 0 | 0 | 0 | 0 | 0 | 133.3934
1985 | 55.6881 | 0 | 42.9 | 0 | 0 | 27.8441 | 0 | 0 | 0 | 0 | 0 | 118.8843
1986 | 56.9569 | 0 | 42.9 | 0 | 37.6 | 28.4785 | 0 | 0 | 0 | 0 | 171.5 | 116.7675
1987 | 66.0879 | 0 | 42.9 | 0 | 75.1 | 33.0439 | 0 | 0 | 0 | 0 | 161.8 | 156.4364
1988 | 45.3866 | 0 | 42.9 | 0 | 75.1 | 22.6933 | 0 | 0 | 0 | 0 | 132.8 | 213.7689
1989 | 41.8594 | 0 | 42.9 | 0 | 75.1 | 20.9297 | 0 | 0 | 0 | 0 | 202.1 | 207.674
1990 | 42.3298 | 0 | 42.9 | 0 | 93.9 | 21.1649 | 0 | 0 | 0 | 0 | 237.4 | 243.1487
1991 | 42.2496 | 0 | 0 | 0 | 0 | 21.1248 | 0 | 0 | 0 | 0 | 0 | 180.7503
1992 | 42.275 | 0 | 0 | 0 | 0 | 21.1375 | 0 | 0 | 0 | 0 | 0 | 131.1506
1993 | 42.5694 | 0 | 0 | 0 | 0 | 21.2847 | 0 | 0 | 0 | 0 | 0 | 115.9408
1994 | 38.9774 | 0 | 0 | 0 | 0 | 19.4887 | 0 | 0 | 0 | 0 | 0 | 88.124
1995 | 43.6768 | 0 | 0 | 0 | 0 | 21.8384 | 0 | 0 | 0 | 0 | 3.3 | 89.4257
1996 | 44.3326 | 0 | 0 | 0 | 0 | 22.1663 | 0 | 0 | 0 | 0 | 15.1 | 85.279
1997 | 41.2321 | 0 | 0 | 0 | 0 | 20.616 | 0 | 0 | 0 | 0 | 45.9 | 87.7637
1998 | 44.6654 | 0 | 0 | 1.9 | 0 | 22.3327 | 0 | 0 | 0 | 0.1 | 80.1 | 105.8229
1999 | 61.3017 | 0 | 42.9 | 155 | 56.3 | 30.6509 | 0 | 0 | 0 | 17.2 | 589.4 | 120.3309
2000 | 71.4034 | 0 | 42.9 | 131.1 | 37.6 | 35.7017 | 0 | 0 | 0 | 16.2 | 487 | 90.2651
2001 | 68.9079 | 0 | 42.9 | 96 | 0 | 34.4539 | 0 | 0 | 0 | 12.5 | 39.5 | 87.7613
2002 | 65.6713 | 0 | 42.9 | 60.2 | 0 | 32.8357 | 0 | 0 | 0 | 9 | 29.7 | 113.6792
2003 | 62.7382 | 0 | 42.9 | 28.6 | 0 | 31.3691 | 0 | 0 | 0 | 5.9 | 10.3 | 91.5818
2004 | 61.0693 | 0 | 42.9 | 6.5 | 0 | 30.5346 | 0 | 0 | 0 | 1.8 | 3.2 | 134.8447
2005 | 61.4235 | 0 | 42.9 | 0 | 75.1 | 30.7118 | 0 | 0 | 0 | 0 | 347.2 | 86.3407
2006 | 54.0288 | 0 | 42.9 | 0 | 37.6 | 27.0144 | 0 | 0 | 0 | 0 | 242.5 | 111.0254
2007 | 53.7743 | 0 | 42.9 | 0 | 0 | 26.8872 | 0 | 0 | 0 | 0 | 0 | 144.4656
2008 | 52.1228 | 0 | 42.9 | 0 | 0 | 26.0614 | 0 | 0 | 0 | 0 | 0 | 100.7821
2009 | 53.9367 | 0 | 42.9 | 0 | 0 | 26.9684 | 0 | 0 | 0 | 0 | 0 | 128.3968
2010 | 56.7846 | 0 | 42.9 | 0 | 37.6 | 28.3923 | 0 | 0 | 0 | 1.4 | 278.6 | 180.9031
2011 | 58.6786 | 0 | 42.9 | 1 | 75.1 | 29.3393 | 0 | 0 | 0 | 3.2 | 241.8 | 251.7878
2012 | 51.1109 | 0 | 42.9 | 0 | 75.1 | 25.5554 | 0 | 0 | 0 | 0 | 207.8 | 241.6292
2013 | 42.0212 | 0 | 42.9 | 1.7 | 75.1 | 21.0106 | 0 | 0 | 0 | 0 | 280.3 | 221.3645
2014 | 38.2556 | 0 | 42.9 | 9.8 | 93.9 | 19.1278 | 0 | 0 | 0 | 0.1 | 322.6 | 204.9816
2015 | 41.8684 | 0 | 0 | 0 | 0 | 20.9342 | 0 | 0 | 0 | 3 | 0 | 121.0401
2016 | 40.8682 | 0 | 0 | 0 | 0 | 20.4341 | 0 | 0 | 0 | 6.5 | 1 | 101.2617
2017 | 40.037 | 0 | 0 | 0 | 0 | 20.0185 | 0 | 0 | 0 | 10.4 | 14.3 | 93.844
2018 | 40.647 | 0 | 0 | 2.4 | 0 | 20.3235 | 0 | 0 | 0 | 14.2 | 59.9 | 79.1186
2019 | 41.6381 | 0 | 0 | 10.7 | 0 | 20.819 | 0 | 0 | 0 | 17.7 | 112.9 | 87.2906
2020 | 44.0694 | 0 | 0 | 18.6 | 0 | 22.0347 | 0 | 0 | 0 | 20.6 | 156.1 | 89.7844
2021 | 40.5521 | 0 | 0 | 31.4 | 0 | 20.2761 | 0 | 0 | 0 | 23.8 | 194.4 | 82.0825
2022 | 61.9073 | 0 | 0 | 46.5 | 0 | 30.9537 | 0 | 0 | 0 | 26.5 | 223.5 | 122.1822
2023 | 100.5262 | 0 | 42.9 | 230.8 | 56.3 | 50.2631 | 0 | 0 | 0 | 38.9 | 725.6 | 91.2182
2024 | 167.7849 | 0.7 | 43 | 237.8 | 37.6 | 83.8925 | 0 | 0 | 0 | 85.7 | 621.4 | 89.6658
2025 | 222.9217 | 2.1 | 43.2 | 195.4 | 0 | 111.4608 | 0 | 0 | 0 | 88.5 | 123.6 | 101.6212
2026 | 254.2583 | 3.5 | 43.4 | 162.4 | 0 | 127.1291 | 0 | 0 | 0 | 102.2 | 119.2 | 173.0438
2027 | 248.8802 | 3.5 | 43.4 | 119.1 | 0 | 124.4401 | 0 | 0 | 0 | 89.2 | 75.5 | 160.3729
2028 | 233.1352 | 2.8 | 43.3 | 74.9 | 0 | 116.5676 | 0 | 0 | 0 | 66.1 | 39.9 | 127.943
2029 | 232.1713 | 1.4 | 43.1 | 32.7 | 75.1 | 116.0857 | 0 | 0 | 0 | 38.2 | 422.2 | 232.2196
2030 | 223.6791 | 2.1 | 43.2 | 5.6 | 37.6 | 111.8396 | 0 | 0 | 0 | 34.5 | 299.7 | 114.1639
2031 | 202.5164 | 3.5 | 43.4 | 0 | 0 | 101.2582 | 0 | 0 | 0 | 46.5 | 0 | 164.0696
2032 | 180.5199 | 2.8 | 43.3 | 0 | 0 | 90.26 | 0 | 0 | 0 | 45.4 | 0 | 219.8072
2033 | 127.3555 | 2.1 | 43.2 | 0 | 0 | 63.6778 | 0 | 0 | 0 | 35.8 | 0 | 93.9645
2034 | 111.7918 | 0.7 | 43 | 1.6 | 37.6 | 55.8959 | 0 | 0 | 0 | 23.8 | 320 | 149.0864
2035 | 81.6128 | 0 | 42.9 | 0.1 | 75.1 | 40.8064 | 0 | 0 | 0 | 0 | 287.4 | 309.7967
2036 | 58.0153 | 0 | 42.9 | 0 | 75.1 | 29.0077 | 0 | 0 | 0 | 0 | 253.2 | 227.3154
2037 | 41.3836 | 0 | 42.9 | 0.8 | 75.1 | 20.6918 | 0 | 0 | 0 | 0 | 315.3 | 197.8361
2038 | 43.7939 | 0 | 42.9 | 8.6 | 93.9 | 21.897 | 0 | 0 | 0 | 0 | 354.5 | 224.8203
2039 | 42.8409 | 0 | 0 | 0 | 0 | 21.4204 | 0 | 0 | 0 | 0 | 0 | 194.5628
2040 | 42.6782 | 0 | 0 | 0 | 0 | 21.3391 | 0 | 0 | 0 | 0 | 3.5 | 155.1819
2041 | 43.0895 | 0 | 0 | 0 | 0 | 21.5447 | 0 | 0 | 0 | 0 | 26.5 | 102.8252
2042 | 40.1517 | 0 | 0 | 0.5 | 0 | 20.0758 | 0 | 0 | 0 | 0 | 70.7 | 95.5116
2043 | 40.81 | 0 | 0 | 6.4 | 0 | 20.405 | 0 | 0 | 0 | 0 | 111.6 | 83.2676
2044 | 42.8393 | 0 | 0 | 12.7 | 0 | 21.4197 | 0 | 0 | 0 | 0 | 147.1 | 76.6143
2045 | 42.7901 | 0 | 0 | 20.9 | 0 | 21.395 | 0 | 0 | 0 | 0 | 178.7 | 81.3713
2046 | 56.9684 | 0 | 0 | 31.9 | 0 | 28.4842 | 0 | 0 | 0 | 0.4 | 200.3 | 128.2775
2047 | 97.0851 | 0 | 42.9 | 212.1 | 56.3 | 48.5425 | 0 | 0 | 0 | 13.6 | 696.7 | 114.1649
2048 | 183.3746 | 0.7 | 43 | 203.2 | 37.6 | 91.6873 | 0 | 0 | 0 | 59.8 | 568.5 | 96.3466
2049 | 274.7032 | 2.1 | 43.2 | 143.5 | 0 | 137.3516 | 0 | 0 | 0 | 52.2 | 58 | 116.4846
2050 | 289.8752 | 3.5 | 43.4 | 92.4 | 0 | 144.9376 | 0 | 0 | 0 | 57.8 | 25.8 | 269.0491
2051 | 289.4924 | 3.5 | 43.4 | 32 | 0 | 144.7462 | 0 | 0 | 0 | 44.4 | 2.9 | 199.0668
2052 | 237.859 | 2.8 | 43.3 | 0 | 0 | 118.9295 | 0 | 0 | 0 | 26.7 | 0 | 313.6959
2053 | 221.6566 | 1.4 | 43.1 | 0 | 75.1 | 110.8283 | 0 | 0 | 0 | 9.2 | 234.8 | 426.7505
2054 | 222.5597 | 2.1 | 43.2 | 0 | 37.6 | 111.2798 | 0 | 0 | 0 | 4 | 136.3 | 162.3987
2055 | 203.9055 | 3.5 | 43.4 | 0 | 0 | 101.9527 | 0 | 0 | 0 | 5.8 | 0 | 101.8612
2056 | 162.2887 | 2.8 | 43.3 | 0 | 0 | 81.1444 | 0 | 0 | 0 | 3.4 | 0 | 108.8494
2057 | 123.4923 | 2.1 | 43.2 | 0 | 0 | 61.7462 | 0 | 0 | 0 | 3 | 0 | 265.824
2058 | 123.1781 | 0.7 | 43 | 0 | 37.6 | 61.589 | 0 | 0 | 0 | 1.5 | 72.3 | 144.864
2059 | 88.6056 | 0 | 42.9 | 0 | 75.1 | 44.3028 | 0 | 0 | 0 | 0 | 69.2 | 436.8213
2060 | 60.5086 | 0 | 42.9 | 0 | 75.1 | 30.2543 | 0 | 0 | 0 | 0 | 33.5 | 203.2565
2061 | 41.9015 | 0 | 42.9 | 0 | 75.1 | 20.9508 | 0 | 0 | 0 | 0 | 95.2 | 260.434
2062 | 42.9887 | 0 | 42.9 | 0 | 93.9 | 21.4944 | 0 | 0 | 0 | 0 | 118 | 257.4519
2063 | 42.8911 | 0 | 0 | 0 | 0 | 21.4456 | 0 | 0 | 0 | 0 | 0 | 246.2112
2064 | 42.6156 | 0 | 0 | 0 | 0 | 21.3078 | 0 | 0 | 0 | 0 | 0 | 188.5611
2065 | 40.1502 | 0 | 0 | 0 | 0 | 20.0751 | 0 | 0 | 0 | 0 | 0 | 113.5618
2066 | 41.7419 | 0 | 0 | 0 | 0 | 20.871 | 0 | 0 | 0 | 0 | 0 | 95.8728
2067 | 41.8687 | 0 | 0 | 0 | 0 | 20.9343 | 0 | 0 | 0 | 0 | 0 | 103.5375
2068 | 41.7332 | 0 | 0 | 0 | 0 | 20.8666 | 0 | 0 | 0 | 0 | 0 | 95.9902
2069 | 43.383 | 0 | 0 | 0 | 0 | 21.6915 | 0 | 0 | 0 | 0 | 0 | 93.0074
2070 | 64.9811 | 0 | 0 | 0 | 0 | 32.4906 | 0 | 0 | 0 | 0 | 0 | 118.3414
2071 | 105.8302 | 0 | 42.9 | 45.1 | 56.3 | 52.9151 | 0 | 0 | 0 | 7.3 | 358.8 | 129.5372
2072 | 167.4927 | 0.7 | 43 | 104.2 | 37.6 | 83.7463 | 0 | 0 | 0 | 53.9 | 318.1 | 165.055
2073 | 260.0206 | 2.1 | 43.2 | 97 | 0 | 130.0103 | 0 | 0 | 0 | 38.5 | 0 | 138.5722
2074 | 357.7665 | 3.5 | 43.4 | 95.8 | 0 | 178.8832 | 0 | 0 | 0 | 41 | 0.6 | 172.2364
2075 | 324.8539 | 3.5 | 43.4 | 91.5 | 0 | 162.427 | 0 | 0 | 0 | 23.9 | 2.6 | 107.6401
2076 | 320.3498 | 2.8 | 43.3 | 86 | 0 | 160.1749 | 0 | 0 | 0 | 3.6 | 4.3 | 139.3031
2077 | 300.9224 | 1.4 | 43.1 | 73.6 | 75.1 | 150.4612 | 0 | 0 | 0 | 0 | 393.5 | 165.8405
2078 | 304.5999 | 2.1 | 43.2 | 26.6 | 37.6 | 152.2999 | 0 | 0 | 0 | 0 | 260.1 | 181.3905
2079 | 259.7811 | 3.5 | 43.4 | 3 | 0 | 129.8905 | 0 | 0 | 0 | 0 | 0 | 304.2301
2080 | 255.9145 | 2.8 | 43.3 | 0 | 0 | 127.9572 | 0 | 0 | 0 | 0 | 0 | 140.2608
2081 | 216.2807 | 2.1 | 43.2 | 0 | 0 | 108.1403 | 0 | 0 | 0 | 0 | 0 | 165.4555
2082 | 130.2762 | 0.7 | 43 | 0 | 37.6 | 65.1381 | 0 | 0 | 0 | 0 | 205.8 | 352.0224
2083 | 84.6401 | 0 | 42.9 | 0 | 75.1 | 42.3201 | 0 | 0 | 0 | 0 | 150.6 | 232.094
2084 | 59.493 | 0 | 42.9 | 0 | 75.1 | 29.7465 | 0 | 0 | 0 | 0 | 116.2 | 220.2646
2085 | 40.0587 | 0 | 42.9 | 0 | 75.1 | 20.0294 | 0 | 0 | 0 | 0 | 190.9 | 287.2903
2086 | 40.8512 | 0 | 42.9 | 0 | 93.9 | 20.4256 | 0 | 0 | 0 | 0 | 224.9 | 212.4895
2087 | 43.405 | 0 | 0 | 0 | 0 | 21.7025 | 0 | 0 | 0 | 0 | 0 | 183.2126
2088 | 42.0146 | 0 | 0 | 0 | 0 | 21.0073 | 0 | 0 | 0 | 0 | 0 | 188.6496
2089 | 41.2389 | 0 | 0 | 0 | 0 | 20.6195 | 0 | 0 | 0 | 0 | 0 | 111.9979
2090 | 40.4709 | 0 | 0 | 0 | 0 | 20.2355 | 0 | 0 | 0 | 0 | 4.7 | 94.0838
2091 | 41.7679 | 0 | 0 | 0.5 | 0 | 20.884 | 0 | 0 | 0 | 0 | 41.7 | 78.7698
2092 | 41.1552 | 0 | 0 | 7.3 | 0 | 20.5776 | 0 | 0 | 0 | 0 | 99.1 | 80.1857
2093 | 42.6044 | 0 | 0 | 14.9 | 0 | 21.3022 | 0 | 0 | 0 | 0 | 146.5 | 84.8044
2094 | 65.3837 | 0 | 0 | 27.2 | 0 | 32.6919 | 0 | 0 | 0 | 0 | 185.7 | 139.162
2095 | 93.9062 | 0 | 42.9 | 212.8 | 56.3 | 46.9531 | 0 | 0 | 0 | 0 | 685.7 | 137.4767
2096 | 129.4983 | 0.7 | 43 | 202 | 37.6 | 64.7492 | 0 | 0 | 0 | 40.7 | 543.3 | 106.4275
2097 | 208.4595 | 2.1 | 43.2 | 135.2 | 0 | 104.2297 | 0 | 0 | 0 | 29.4 | 32.6 | 109.4475
2098 | 244.3584 | 3.5 | 43.4 | 76.9 | 0 | 122.1792 | 0 | 0 | 0 | 36.6 | 6.7 | 99.5959
2099 | 245.366 | 3.5 | 43.4 | 15.4 | 0 | 122.683 | 0 | 0 | 0 | 22 | 0.1 | 108.1276
2100 | 213.1997 | 2.8 | 43.3 | 0 | 0 | 106.5999 | 0 | 0 | 0 | 1.9 | 0 | 104.8603
2101 | 205.1603 | 1.4 | 43.1 | 0 | 75.1 | 102.5802 | 0 | 0 | 0 | 0 | 201.7 | 146.7047
2102 | 201.6111 | 2.1 | 43.2 | 0 | 37.6 | 100.8055 | 0 | 0 | 0 | 0 | 115.8 | 158.5827
2103 | 203.5543 | 3.5 | 43.4 | 0 | 0 | 101.7772 | 0 | 0 | 0 | 0 | 0 | 138.0775
2104 | 180.074 | 2.8 | 43.3 | 0 | 0 | 90.037 | 0 | 0 | 0 | 0 | 0 | 129.5713
2105 | 129.5113 | 2.1 | 43.2 | 0 | 0 | 64.7557 | 0 | 0 | 0 | 0 | 0 | 118.0807
2106 | 116.9372 | 0.7 | 43 | 0 | 37.6 | 58.4686 | 0 | 0 | 0 | 0 | 49.6 | 159.8397
2107 | 94.4247 | 0 | 42.9 | 0 | 75.1 | 47.2124 | 0 | 0 | 0 | 0 | 64.5 | 188.3971
2108 | 62.0456 | 0 | 42.9 | 0 | 75.1 | 31.0228 | 0 | 0 | 0 | 0 | 40.4 | 361.2998
2109 | 43.0991 | 0 | 42.9 | 0 | 75.1 | 21.5495 | 0 | 0 | 0 | 0 | 125.6 | 325.2721
2110 | 44.3673 | 0 | 42.9 | 0 | 93.9 | 22.1836 | 0 | 0 | 0 | 0 | 180.1 | 198.0184
2111 | 41.5479 | 0 | 0 | 0 | 0 | 20.774 | 0 | 0 | 0 | 0 | 0 | 138.2857
2112 | 41.9381 | 0 | 0 | 0 | 0 | 20.969 | 0 | 0 | 0 | 0 | 0 | 143.4379
2113 | 40.1145 | 0 | 0 | 0 | 0 | 20.0573 | 0 | 0 | 0 | 0 | 0 | 106.1853
2114 | 41.1345 | 0 | 0 | 0 | 0 | 20.5672 | 0 | 0 | 0 | 0 | 0 | 95.631
2115 | 39.9447 | 0 | 0 | 0 | 0 | 19.9723 | 0 | 0 | 0 | 0 | 2.3 | 76.7356
2116 | 40.7991 | 0 | 0 | 0 | 0 | 20.3996 | 0 | 0 | 0 | 0 | 11.7 | 79.2377
2117 | 41.8866 | 0 | 0 | 0 | 0 | 20.9433 | 0 | 0 | 0 | 0 | 46.6 | 87.1736
2118 | 43.4477 | 0 | 0 | 3.6 | 0 | 21.7239 | 0 | 0 | 0 | 0 | 92.2 | 127.0076
2119 | 59.842 | 0 | 42.9 | 166.8 | 56.3 | 29.921 | 0 | 0 | 0 | 0 | 616.2 | 125.7019
2120 | 60.9382 | 0.7 | 43 | 170 | 37.6 | 30.4691 | 0 | 0 | 0 | 28.9 | 471.3 | 89.0689
2121 | 57.8653 | 2.1 | 43.2 | 95.8 | 0 | 28.9327 | 0 | 0 | 0 | 22.1 | 0.6 | 101.1422
2122 | 54.4754 | 3.5 | 43.4 | 32.7 | 0 | 27.2377 | 0 | 0 | 0 | 28.6 | 0 | 130.1063
2123 | 50.1324 | 3.5 | 43.4 | 0 | 0 | 25.0662 | 0 | 0 | 0 | 10.6 | 0 | 99.5981
2124 | 52.0974 | 2.8 | 43.3 | 0 | 0 | 26.0487 | 0 | 0 | 0 | 0 | 0 | 123.6336
2125 | 52.7163 | 1.4 | 43.1 | 0 | 75.1 | 26.3581 | 0 | 0 | 0 | 0 | 119.3 | 190.8963
2126 | 54.6093 | 2.1 | 43.2 | 0 | 37.6 | 27.3046 | 0 | 0 | 0 | 0 | 50.6 | 99.5897
2127 | 54.6678 | 3.5 | 43.4 | 0 | 0 | 27.3339 | 0 | 0 | 0 | 0 | 0 | 133.9011
2128 | 52.5954 | 2.8 | 43.3 | 0 | 0 | 26.2977 | 0 | 0 | 0 | 0 | 0 | 111.2703
2129 | 52.6441 | 2.1 | 43.2 | 0 | 0 | 26.322 | 0 | 0 | 0 | 0 | 0 | 137.3564
2130 | 58.9485 | 0.7 | 43 | 0 | 37.6 | 29.4742 | 0 | 0 | 0 | 0 | 0 | 164.1651
2131 | 54.8482 | 0 | 42.9 | 0 | 75.1 | 27.4241 | 0 | 0 | 0 | 0 | 0.3 | 226.4155
2132 | 45.6181 | 0 | 42.9 | 0 | 75.1 | 22.8091 | 0 | 0 | 0 | 0 | 0 | 273.6772
2133 | 43.9191 | 0 | 42.9 | 0 | 75.1 | 21.9596 | 0 | 0 | 0 | 0 | 14 | 215.4814
2134 | 43.1511 | 0 | 42.9 | 0 | 93.9 | 21.5756 | 0 | 0 | 0 | 0 | 57.6 | 208.0384
2135 | 41.4788 | 0 | 0 | 0 | 0 | 20.7394 | 0 | 0 | 0 | 0 | 0 | 215.7674
2136 | 41.5398 | 0 | 0 | 0 | 0 | 20.7699 | 0 | 0 | 0 | 0 | 0 | 188.8899
2137 | 44.163 | 0 | 0 | 0 | 0 | 22.0815 | 0 | 0 | 0 | 0 | 0 | 92.8857
2138 | 43.4477 | 0 | 0 | 0 | 0 | 21.7239 | 0 | 0 | 0 | 0 | 0 | 89.5504
2139 | 40.4483 | 0 | 0 | 0 | 0 | 20.2241 | 0 | 0 | 0 | 0 | 0 | 95.6289
2140 | 42.6642 | 0 | 0 | 0 | 0 | 21.3321 | 0 | 0 | 0 | 0 | 0 | 95.7491
2141 | 42.2827 | 0 | 0 | 0 | 0 | 21.1414 | 0 | 0 | 0 | 0 | 0 | 94.7974
2142 | 53.3823 | 0 | 0 | 0 | 0 | 26.6911 | 0 | 0 | 0 | 0 | 0 | 96.4705
2143 | 74.6913 | 0 | 42.9 | 58.1 | 56.3 | 37.3457 | 0 | 0 | 0 | 0 | 429.1 | 118.4278
2144 | 73.6116 | 0 | 42.9 | 52 | 37.6 | 36.8058 | 0 | 0 | 0 | 0 | 316.9 | 122.6775
2145 | 65.5784 | 0 | 42.9 | 6.2 | 0 | 32.7892 | 0 | 0 | 0 | 0 | 0 | 163.2302
2146 | 62.6759 | 0 | 42.9 | 0 | 0 | 31.338 | 0 | 0 | 0 | 0 | 0 | 158.3647
2147 | 57.8628 | 0 | 42.9 | 0 | 0 | 28.9314 | 0 | 0 | 0 | 0 | 0 | 188.8678
2148 | 56.9089 | 0 | 42.9 | 0 | 0 | 28.4544 | 0 | 0 | 0 | 0 | 0 | 212.021
2149 | 53.6436 | 0 | 42.9 | 0 | 75.1 | 26.8218 | 0 | 0 | 0 | 0 | 3.2 | 203.0123
2150 | 55.2998 | 0 | 42.9 | 0 | 37.6 | 27.6499 | 0 | 0 | 0 | 0 | 0 | 302.0196
2151 | 54.7723 | 0 | 42.9 | 0 | 0 | 27.3861 | 0 | 0 | 0 | 0 | 0 | 314.2127
2152 | 56.2326 | 0 | 42.9 | 0 | 0 | 28.1163 | 0 | 0 | 0 | 0 | 0 | 168.0558
2153 | 55.5431 | 0 | 42.9 | 0 | 0 | 27.7715 | 0 | 0 | 0 | 0 | 0 | 153.5647
2154 | 64.6582 | 0 | 42.9 | 0 | 37.6 | 32.3291 | 0 | 0 | 0 | 0 | 0 | 258.3363
2155 | 71.6702 | 0 | 42.9 | 0 | 75.1 | 35.8351 | 0 | 0 | 0 | 0 | 0 | 246.7808
2156 | 53.9879 | 0 | 42.9 | 0 | 75.1 | 26.9939 | 0 | 0 | 0 | 0 | 0 | 268.8703
2157 | 42.8982 | 0 | 42.9 | 0 | 75.1 | 21.4491 | 0 | 0 | 0 | 0 | 0 | 286.253
2158 | 41.6117 | 0 | 42.9 | 0 | 93.9 | 20.8059 | 0 | 0 | 0 | 0 | 0 | 159.4547
2159 | 40.898 | 0 | 0 | 0 | 0 | 20.449 | 0 | 0 | 0 | 0 | 0 | 144.5214
2160 | 43.3957 | 0 | 0 | 0 | 0 | 21.6978 | 0 | 0 | 0 | 0 | 0 | 120.7982
2161 | 42.403 | 0 | 0 | 0 | 0 | 21.2015 | 0 | 0 | 0 | 0 | 0 | 94.9146
2162 | 40.9039 | 0 | 0 | 0 | 0 | 20.4519 | 0 | 0 | 0 | 0 | 0 | 83.1478
2163 | 40.2208 | 0 | 0 | 0 | 0 | 20.1104 | 0 | 0 | 0 | 0 | 0 | 77.0864
2164 | 42.0335 | 0 | 0 | 0 | 0 | 21.0168 | 0 | 0 | 0 | 0 | 0 | 78.7669
2165 | 40.5425 | 0 | 0 | 0 | 0 | 20.2713 | 0 | 0 | 0 | 0 | 0 | 92.6503
2166 | 44.7745 | 0 | 0 | 0 | 0 | 22.3873 | 0 | 0 | 0 | 0 | 0 | 128.0703
2167 | 53.6993 | 0 | 42.9 | 46.3 | 56.3 | 26.8497 | 0 | 0 | 0 | 0 | 403.2 | 142.559
2168 | 57.1664 | 0 | 42.9 | 33.1 | 37.6 | 28.5832 | 0 | 0 | 0 | 0 | 316.2 | 87.2918
2169 | 52.4975 | 0 | 42.9 | 6.6 | 0 | 26.2487 | 0 | 0 | 0 | 0 | 0 | 130.5886
2170 | 52.0149 | 0 | 42.9 | 0 | 0 | 26.0075 | 0 | 0 | 0 | 0 | 0 | 157.2778
2171 | 49.9607 | 0 | 42.9 | 0 | 0 | 24.9804 | 0 | 0 | 0 | 0 | 0 | 162.9598
2172 | 51.9752 | 0 | 42.9 | 0 | 0 | 25.9876 | 0 | 0 | 0 | 0 | 0 | 74.3921
2173 | 49.0486 | 0 | 42.9 | 0 | 75.1 | 24.5243 | 0 | 0 | 0 | 0 | 81 | 112.1201
2174 | 49.6812 | 0 | 42.9 | 0 | 37.6 | 24.8406 | 0 | 0 | 0 | 0 | 39.6 | 91.3402
2175 | 48.863 | 0 | 42.9 | 0 | 0 | 24.4315 | 0 | 0 | 0 | 0 | 0 | 86.4611
2176 | 49.0768 | 0 | 42.9 | 0 | 0 | 24.5384 | 0 | 0 | 0 | 0 | 0 | 199.5347
2177 | 49.1664 | 0 | 42.9 | 0 | 0 | 24.5832 | 0 | 0 | 0 | 0 | 0 | 140.9043
2178 | 47.3698 | 0 | 42.9 | 0 | 37.6 | 23.6849 | 0 | 0 | 0 | 0 | 7.8 | 160.885
2179 | 42.5031 | 0 | 42.9 | 0 | 75.1 | 21.2515 | 0 | 0 | 0 | 0 | 14 | 180.1664
2180 | 43.0312 | 0 | 42.9 | 0 | 75.1 | 21.5156 | 0 | 0 | 0 | 0 | 7.2 | 198.6683
2181 | 39.6599 | 0 | 42.9 | 0 | 75.1 | 19.8299 | 0 | 0 | 0 | 0 | 56.1 | 213.6163
2182 | 40.567 | 0 | 42.9 | 0 | 93.9 | 20.2835 | 0 | 0 | 0 | 0 | 116.3 | 180.4545
2183 | 41.5023 | 0 | 0 | 0 | 0 | 20.7512 | 0 | 0 | 0 | 0 | 0 | 213.7536
2184 | 39.8188 | 0 | 0 | 0 | 0 | 19.9094 | 0 | 0 | 0 | 0 | 0 | 142.8163
2185 | 40.7223 | 0 | 0 | 0 | 0 | 20.3611 | 0 | 0 | 0 | 0 | 0 | 95.3929
2186 | 41.4487 | 0 | 0 | 0 | 0 | 20.7244 | 0 | 0 | 0 | 0 | 0 | 79.1201
2187 | 43.8519 | 0 | 0 | 0 | 0 | 21.9259 | 0 | 0 | 0 | 0 | 0 | 78.5294
2188 | 40.0956 | 0 | 0 | 0 | 0 | 20.0478 | 0 | 0 | 0 | 0 | 1.3 | 80.0679
2189 | 41.0849 | 0 | 0 | 0 | 0 | 20.5424 | 0 | 0 | 0 | 0 | 7.8 | 84.2074
2190 | 54.7255 | 0 | 0 | 0 | 0 | 27.3627 | 0 | 0 | 0 | 0 | 14.1 | 90.6231
2191 | 68.6791 | 0 | 42.9 | 122.8 | 56.3 | 34.3396 | 0 | 0 | 0 | 0 | 521.7 | 129.1776
2192 | 73.2855 | 0.7 | 43 | 147.5 | 37.6 | 36.6428 | 0 | 0 | 0 | 48.4 | 411.3 | 114.0465
2193 | 71.038 | 2.1 | 43.2 | 111.4 | 0 | 35.519 | 0 | 0 | 0 | 45.1 | 3.4 | 121.7372
2194 | 68.0894 | 3.5 | 43.4 | 76.4 | 0 | 34.0447 | 0 | 0 | 0 | 62.3 | 1.2 | 146.5788
2195 | 62.6824 | 3.5 | 43.4 | 27.4 | 0 | 31.3412 | 0 | 0 | 0 | 60.3 | 0 | 140.2435
2196 | 59.8634 | 2.8 | 43.3 | 1.8 | 0 | 29.9317 | 0 | 0 | 0 | 45.5 | 0 | 182.0161
2197 | 60.945 | 1.4 | 43.1 | 0 | 75.1 | 30.4725 | 0 | 0 | 0 | 26.6 | 208.8 | 182.5108
2198 | 60.6779 | 2.1 | 43.2 | 0 | 37.6 | 30.3389 | 0 | 0 | 0 | 27 | 129.7 | 117.3049
2199 | 59.4608 | 3.5 | 43.4 | 0 | 0 | 29.7304 | 0 | 0 | 0 | 40.7 | 0 | 115.3839
2200 | 57.932 | 2.8 | 43.3 | 0 | 0 | 28.966 | 0 | 0 | 0 | 39.6 | 0 | 275.9813
2201 | 59.4667 | 2.1 | 43.2 | 0 | 0 | 29.7333 | 0 | 0 | 0 | 29.7 | 0 | 156.6544
2202 | 55.46 | 0.7 | 43 | 0 | 37.6 | 27.73 | 0 | 0 | 0 | 15.9 | 82.3 | 206.1854
2203 | 42.566 | 0 | 42.9 | 0 | 75.1 | 21.283 | 0 | 0 | 0 | 0 | 82.1 | 300.1261
2204 | 40.8245 | 0 | 42.9 | 0 | 75.1 | 20.4123 | 0 | 0 | 0 | 0 | 50.6 | 332.3795
2205 | 42.3317 | 0 | 42.9 | 0 | 75.1 | 21.1658 | 0 | 0 | 0 | 0 | 133.6 | 294.5534
2206 | 42.6187 | 0 | 42.9 | 0 | 93.9 | 21.3093 | 0 | 0 | 0 | 0 | 184.6 | 277.0001
2207 | 40.1728 | 0 | 0 | 0 | 0 | 20.0864 | 0 | 0 | 0 | 0 | 0 | 150.7674
2208 | 37.7833 | 0 | 0 | 0 | 0 | 18.8916 | 0 | 0 | 0 | 0 | 0 | 118.7495
2209 | 38.8553 | 0 | 0 | 0 | 0 | 19.4276 | 0 | 0 | 0 | 0 | 0 | 57.3638
2210 | 41.1338 | 0 | 0 | 0 | 0 | 20.5669 | 0 | 0 | 0 | 0 | 0.6 | 49.3197
2211 | 38.3015 | 0 | 0 | 0 | 0 | 19.1507 | 0 | 0 | 0 | 0 | 9.7 | 45.9939
2212 | 42.5474 | 0 | 0 | 0 | 0 | 21.2737 | 0 | 0 | 0 | 0 | 31.2 | 48.6289
2213 | 41.767 | 0 | 0 | 4.1 | 0 | 20.8835 | 0 | 0 | 0 | 0.1 | 87.2 | 50.4662
2214 | 63.6878 | 0 | 0 | 13.3 | 0 | 31.8439 | 0 | 0 | 0 | 3.3 | 138.5 | 79.7138
2215 | 100.8692 | 0 | 42.9 | 186.6 | 56.3 | 50.4346 | 0 | 0 | 0 | 22.5 | 668.6 | 80.3075
2216 | 178.7242 | 0.7 | 43 | 210.5 | 37.6 | 89.3621 | 0 | 0 | 0 | 67.5 | 552.5 | 50.5817
2217 | 290.8455 | 2.1 | 43.2 | 183.2 | 0 | 145.4228 | 0 | 0 | 0 | 64.3 | 89.8 | 118.8486
2218 | 369.6613 | 3.5 | 43.4 | 160.5 | 0 | 184.8307 | 0 | 0 | 0 | 80.4 | 95 | 170.4269
2219 | 363.6417 | 3.5 | 43.4 | 119.4 | 0 | 181.8208 | 0 | 0 | 0 | 73.6 | 65.6 | 59.6667
2220 | 323.7494 | 2.8 | 43.3 | 77.3 | 0 | 161.8747 | 0 | 0 | 0 | 49 | 40.9 | 127.7282
2221 | 291.087 | 1.4 | 43.1 | 42.7 | 75.1 | 145.5435 | 0 | 0 | 0 | 14.5 | 465.5 | 250.287
2222 | 243.4221 | 2.1 | 43.2 | 35.4 | 37.6 | 121.7111 | 0 | 0 | 0 | 9.5 | 361.3 | 68.7476
2223 | 221.9826 | 3.5 | 43.4 | 34 | 0 | 110.9913 | 0 | 0 | 0 | 24.1 | 0 | 97.7944
2224 | 200.9807 | 2.8 | 43.3 | 28.7 | 0 | 100.4904 | 0 | 0 | 0 | 19.4 | 0.4 | 123.0896
2225 | 145.0081 | 2.1 | 43.2 | 22.8 | 0 | 72.504 | 0 | 0 | 0 | 6.4 | 3.2 | 120.2685
2226 | 105.4896 | 0.7 | 43 | 14.7 | 37.6 | 52.7448 | 0 | 0 | 0 | 0.1 | 421.2 | 128.8168
2227 | 84.0513 | 0 | 42.9 | 5.2 | 75.1 | 42.0256 | 0 | 0 | 0 | 0 | 377.9 | 220.2495
2228 | 62.2526 | 0 | 42.9 | 1.6 | 75.1 | 31.1263 | 0 | 0 | 0 | 0 | 348.1 | 660
2229 | 40.5261 | 0 | 42.9 | 11.1 | 75.1 | 20.263 | 0 | 0 | 0 | 0 | 407.5 | 272.1543
2230 | 43.4149 | 0 | 42.9 | 21.2 | 93.9 | 21.7074 | 0 | 0 | 0 | 0 | 445.9 | 208.2802
2231 | 43.5317 | 0 | 0 | 0 | 0 | 21.7659 | 0 | 0 | 0 | 0 | 6.1 | 288.2455
2232 | 43.3783 | 0 | 0 | 0 | 0 | 21.6892 | 0 | 0 | 0 | 0 | 43.3 | 143.1375
2233 | 42.165 | 0 | 0 | 1.1 | 0 | 21.0825 | 0 | 0 | 0 | 0 | 84.2 | 188.5305
2234 | 42.4721 | 0 | 0 | 6.5 | 0 | 21.236 | 0 | 0 | 0 | 0 | 112.3 | 63.4643
2235 | 44.8622 | 0 | 0 | 11.4 | 0 | 22.4311 | 0 | 0 | 0 | 0 | 137.7 | 47.9395
2236 | 42.2775 | 0 | 0 | 15.8 | 0 | 21.1387 | 0 | 0 | 0 | 0 | 163 | 47.1349
2237 | 41.4431 | 0 | 0 | 21.7 | 0 | 20.7216 | 0 | 0 | 0 | 0 | 185.4 | 52.3068
2238 | 64.5668 | 0 | 0 | 29.6 | 0 | 32.2834 | 0 | 0 | 0 | 0 | 200.1 | 53.5683
2239 | 111.6279 | 0 | 42.9 | 201.5 | 56.3 | 55.8139 | 0 | 0 | 0 | 0.2 | 698.1 | 86.343
2240 | 187.624 | 0.7 | 43 | 198.8 | 37.6 | 93.812 | 0 | 0 | 0 | 45.9 | 578.8 | 47.5951
2241 | 283.3014 | 2.1 | 43.2 | 154.3 | 0 | 141.6507 | 0 | 0 | 0 | 28.2 | 86.2 | 52.0763
2242 | 312.3842 | 3.5 | 43.4 | 115.9 | 0 | 156.1921 | 0 | 0 | 0 | 32.1 | 72.2 | 83.8503
2243 | 295.2545 | 3.5 | 43.4 | 78.8 | 0 | 147.6272 | 0 | 0 | 0 | 13.4 | 38.1 | 73.2389
2244 | 278.9581 | 2.8 | 43.3 | 35.5 | 0 | 139.4791 | 0 | 0 | 0 | 0 | 8.6 | 71.6275
2245 | 273.1536 | 1.4 | 43.1 | 3.2 | 75.1 | 136.5768 | 0 | 0 | 0 | 0 | 369.9 | 151.6427
2246 | 234.0683 | 2.1 | 43.2 | 0 | 37.6 | 117.0342 | 0 | 0 | 0 | 0 | 245.1 | 111.8748
2247 | 225.327 | 3.5 | 43.4 | 0 | 0 | 112.6635 | 0 | 0 | 0 | 0 | 0 | 129.4373
2248 | 204.5991 | 2.8 | 43.3 | 0 | 0 | 102.2995 | 0 | 0 | 0 | 0 | 0 | 156.7083
2249 | 148.1278 | 2.1 | 43.2 | 0 | 0 | 74.0639 | 0 | 0 | 0 | 0 | 0 | 89.3084
2250 | 110.377 | 0.7 | 43 | 0 | 37.6 | 55.1885 | 0 | 0 | 0 | 0 | 142 | 107.7597
2251 | 84.188 | 0 | 42.9 | 0 | 75.1 | 42.094 | 0 | 0 | 0 | 0 | 108.2 | 196.8463
2252 | 61.0687 | 0 | 42.9 | 0 | 75.1 | 30.5343 | 0 | 0 | 0 | 0 | 94 | 232.9709
2253 | 42.3859 | 0 | 42.9 | 0 | 75.1 | 21.193 | 0 | 0 | 0 | 0 | 154.2 | 175.6022
2254 | 42.7774 | 0 | 42.9 | 0 | 93.9 | 21.3887 | 0 | 0 | 0 | 0 | 164.9 | 143.2751
2255 | 40.7737 | 0 | 0 | 0 | 0 | 20.3869 | 0 | 0 | 0 | 0 | 0 | 120.2928
2256 | 41.917 | 0 | 0 | 0 | 0 | 20.9585 | 0 | 0 | 0 | 0 | 0 | 93.6063
2257 | 43.1874 | 0 | 0 | 0 | 0 | 21.5937 | 0 | 0 | 0 | 0 | 0 | 90.2658
2258 | 42.1808 | 0 | 0 | 0 | 0 | 21.0904 | 0 | 0 | 0 | 0 | 0 | 78.1674
2259 | 42.8632 | 0 | 0 | 0 | 0 | 21.4316 | 0 | 0 | 0 | 0 | 0 | 77.6826
2260 | 41.0647 | 0 | 0 | 0 | 0 | 20.5324 | 0 | 0 | 0 | 0 | 0 | 81.1355
2261 | 43.3182 | 0 | 0 | 0 | 0 | 21.6591 | 0 | 0 | 0 | 0 | 0 | 82.4367
2262 | 61.0228 | 0 | 0 | 0 | 0 | 30.5114 | 0 | 0 | 0 | 0 | 0 | 107.3974
2263 | 99.4036 | 0 | 42.9 | 49.8 | 56.3 | 49.7018 | 0 | 0 | 0 | 0 | 369.8 | 100.071
2264 | 157.0944 | 0.7 | 43 | 54.1 | 37.6 | 78.5472 | 0 | 0 | 0 | 0 | 256.3 | 93.1225
2265 | 231.9866 | 2.1 | 43.2 | 1.9 | 0 | 115.9933 | 0 | 0 | 0 | 0 | 0 | 94.2051
2266 | 277.1649 | 3.5 | 43.4 | 0 | 0 | 138.5825 | 0 | 0 | 0 | 0 | 0 | 146.8593
2267 | 241.208 | 3.5 | 43.4 | 0 | 0 | 120.604 | 0 | 0 | 0 | 0 | 0 | 122.746
2268 | 204.0861 | 2.8 | 43.3 | 0 | 0 | 102.0431 | 0 | 0 | 0 | 0 | 0 | 110.1779
2269 | 173.6765 | 1.4 | 43.1 | 0 | 75.1 | 86.8383 | 0 | 0 | 0 | 0 | 0 | 177.8934
2270 | 170.3074 | 2.1 | 43.2 | 0 | 37.6 | 85.1537 | 0 | 0 | 0 | 0 | 2 | 228.4523
2271 | 164.9476 | 3.5 | 43.4 | 0 | 0 | 82.4738 | 0 | 0 | 0 | 0 | 0 | 178.9221
2272 | 138.8022 | 2.8 | 43.3 | 0 | 0 | 69.4011 | 0 | 0 | 0 | 0 | 0 | 188.1367
2273 | 93.3338 | 2.1 | 43.2 | 0 | 0 | 46.6669 | 0 | 0 | 0 | 0 | 0 | 155.3872
2274 | 67.4918 | 0.7 | 43 | 0 | 37.6 | 33.7459 | 0 | 0 | 0 | 0 | 0 | 149.4959
2275 | 51.5894 | 0 | 42.9 | 0 | 75.1 | 25.7947 | 0 | 0 | 0 | 0 | 0 | 167.3384
2276 | 46.8863 | 0 | 42.9 | 0 | 75.1 | 23.4432 | 0 | 0 | 0 | 0 | 0 | 206.0887
2277 | 43.625 | 0 | 42.9 | 0 | 75.1 | 21.8125 | 0 | 0 | 0 | 0 | 0 | 177.9819
2278 | 41.5194 | 0 | 42.9 | 0 | 93.9 | 20.7597 | 0 | 0 | 0 | 0 | 0 | 163.1731
2279 | 41.7521 | 0 | 0 | 0 | 0 | 20.8761 | 0 | 0 | 0 | 0 | 0 | 143.0872
2280 | 41.5327 | 0 | 0 | 0 | 0 | 20.7664 | 0 | 0 | 0 | 0 | 0 | 148.1381
2281 | 40.1771 | 0 | 0 | 0 | 0 | 20.0886 | 0 | 0 | 0 | 0 | 0 | 100.9079
2282 | 40.1034 | 0 | 0 | 0 | 0 | 20.0517 | 0 | 0 | 0 | 0 | 0 | 79.4789
2283 | 42.4423 | 0 | 0 | 0 | 0 | 21.2212 | 0 | 0 | 0 | 0 | 0 | 77.3293
2284 | 42.2586 | 0 | 0 | 0 | 0 | 21.1293 | 0 | 0 | 0 | 0 | 0 | 78.1626
2285 | 40.3944 | 0 | 0 | 0 | 0 | 20.1972 | 0 | 0 | 0 | 0 | 0 | 94.4429
2286 | 54.6871 | 0 | 0 | 0 | 0 | 27.3435 | 0 | 0 | 0 | 0 | 0 | 122.9584
2287 | 104.9026 | 0 | 42.9 | 7.4 | 56.3 | 52.4513 | 0 | 0 | 0 | 0 | 205.9 | 108.124
2288 | 182.6271 | 0.7 | 43 | 19.7 | 37.6 | 91.3136 | 0 | 0 | 0 | 0 | 170.7 | 93.2435
2289 | 312.8119 | 2.1 | 43.2 | 8 | 0 | 156.406 | 0 | 0 | 0 | 0 | 0 | 143.9049
2290 | 386.222 | 3.5 | 43.4 | 0.1 | 0 | 193.111 | 0 | 0 | 0 | 0 | 0 | 270.8259
2291 | 329.0193 | 3.5 | 43.4 | 0 | 0 | 164.5097 | 0 | 0 | 0 | 0 | 0 | 320.1211
2292 | 256.0601 | 2.8 | 43.3 | 0 | 0 | 128.0301 | 0 | 0 | 0 | 0 | 0 | 244.5468
2293 | 212.291 | 1.4 | 43.1 | 0 | 75.1 | 106.1455 | 0 | 0 | 0 | 0 | 3.1 | 296.7493
2294 | 199.7559 | 2.1 | 43.2 | 0 | 37.6 | 99.8779 | 0 | 0 | 0 | 0 | 0.5 | 425.0318
2295 | 183.8497 | 3.5 | 43.4 | 0 | 0 | 91.9249 | 0 | 0 | 0 | 0 | 0 | 167.7428
2296 | 150.8724 | 2.8 | 43.3 | 0 | 0 | 75.4362 | 0 | 0 | 0 | 0 | 0 | 229.9312
2297 | 107.7114 | 2.1 | 43.2 | 0 | 0 | 53.8557 | 0 | 0 | 0 | 0 | 0 | 169.6975
2298 | 79.5078 | 0.7 | 43 | 0 | 37.6 | 39.7539 | 0 | 0 | 0 | 0 | 0 | 319.9671
2299 | 74.1982 | 0 | 42.9 | 0 | 75.1 | 37.0991 | 0 | 0 | 0 | 0 | 0 | 233.7466
2300 | 55.3751 | 0 | 42.9 | 0 | 75.1 | 27.6875 | 0 | 0 | 0 | 0 | 0 | 173.3082
2301 | 41.4757 | 0 | 42.9 | 0 | 75.1 | 20.7378 | 0 | 0 | 0 | 0 | 0 | 263.9765
2302 | 42.8728 | 0 | 42.9 | 0 | 93.9 | 21.4364 | 0 | 0 | 0 | 0 | 0 | 310.5467
2303 | 42.9066 | 0 | 0 | 0 | 0 | 21.4533 | 0 | 0 | 0 | 0 | 0 | 154.1315
2304 | 41.5913 | 0 | 0 | 0 | 0 | 20.7956 | 0 | 0 | 0 | 0 | 0 | 122.2252
2305 | 44.0062 | 0 | 0 | 0 | 0 | 22.0031 | 0 | 0 | 0 | 0 | 0 | 81.8427
2306 | 44.4509 | 0 | 0 | 0 | 0 | 22.2255 | 0 | 0 | 0 | 0 | 0 | 71.7413
2307 | 40.6798 | 0 | 0 | 0 | 0 | 20.3399 | 0 | 0 | 0 | 0 | 0 | 70.4731
2308 | 41.0427 | 0 | 0 | 0 | 0 | 20.5214 | 0 | 0 | 0 | 0 | 0 | 52.765
2309 | 43.0895 | 0 | 0 | 0 | 0 | 21.5447 | 0 | 0 | 0 | 0 | 0 | 55.8645
2310 | 54.0923 | 0 | 0 | 0 | 0 | 27.0462 | 0 | 0 | 0 | 0 | 0 | 96.3445
2311 | 64.8138 | 0 | 42.9 | 0 | 56.3 | 32.4069 | 0 | 0 | 0 | 0 | 108.2 | 68.2868
2312 | 73.9249 | 0 | 42.9 | 3.7 | 37.6 | 36.9624 | 0 | 0 | 0 | 0 | 100 | 87.1724
2313 | 68.9106 | 0 | 42.9 | 0 | 0 | 34.4553 | 0 | 0 | 0 | 0 | 0 | 56.5518
2314 | 69.5156 | 0 | 42.9 | 0 | 0 | 34.7578 | 0 | 0 | 0 | 0 | 0 | 71.5101
2315 | 65.9366 | 0 | 42.9 | 0 | 0 | 32.9683 | 0 | 0 | 0 | 0 | 0 | 47.2497
2316 | 52.8275 | 0 | 42.9 | 0 | 0 | 26.4138 | 0 | 0 | 0 | 0 | 0 | 63.3473
2317 | 52.1578 | 0 | 42.9 | 0 | 75.1 | 26.0789 | 0 | 0 | 0 | 0 | 0 | 93.3673
2318 | 52.94 | 0 | 42.9 | 0 | 37.6 | 26.47 | 0 | 0 | 0 | 0 | 0 | 100.4323
2319 | 53.9181 | 0 | 42.9 | 0 | 0 | 26.9591 | 0 | 0 | 0 | 0 | 0 | 97.7973
2320 | 53.4483 | 0 | 42.9 | 0 | 0 | 26.7242 | 0 | 0 | 0 | 0 | 0 | 96.3452
2321 | 55.5576 | 0 | 42.9 | 0 | 0 | 27.7788 | 0 | 0 | 0 | 0 | 0 | 89.5454
2322 | 54.1134 | 0 | 42.9 | 0 | 37.6 | 27.0567 | 0 | 0 | 0 | 0 | 0 | 70.7062
2323 | 51.0439 | 0 | 42.9 | 0 | 75.1 | 25.522 | 0 | 0 | 0 | 0 | 0 | 208.711
2324 | 45.6327 | 0 | 42.9 | 0 | 75.1 | 22.8163 | 0 | 0 | 0 | 0 | 0 | 196.1625
2325 | 43.3495 | 0 | 42.9 | 0 | 75.1 | 21.6747 | 0 | 0 | 0 | 0 | 0 | 139.7272
2326 | 39.5625 | 0 | 42.9 | 0 | 93.9 | 19.7813 | 0 | 0 | 0 | 0 | 0 | 185.6471
2327 | 40.8174 | 0 | 0 | 0 | 0 | 20.4087 | 0 | 0 | 0 | 0 | 0 | 107.8847
2328 | 42.8161 | 0 | 0 | 0 | 0 | 21.4081 | 0 | 0 | 0 | 0 | 0 | 80.6614
2329 | 42.6522 | 0 | 0 | 0 | 0 | 21.3261 | 0 | 0 | 0 | 0 | 0 | 69.3238
2330 | 42.6444 | 0 | 0 | 0 | 0 | 21.3222 | 0 | 0 | 0 | 0 | 0 | 59.207
2331 | 40.9231 | 0 | 0 | 0 | 0 | 20.4615 | 0 | 0 | 0 | 0 | 0 | 46.7908
2332 | 44.5734 | 0 | 0 | 0 | 0 | 22.2867 | 0 | 0 | 0 | 0 | 0 | 46.7906
2333 | 44.8693 | 0 | 0 | 0 | 0 | 22.4347 | 0 | 0 | 0 | 0 | 0 | 50.1225
2334 | 46.1292 | 0 | 0 | 0 | 0 | 23.0646 | 0 | 0 | 0 | 0 | 0 | 61.5096
2335 | 72.5138 | 0 | 42.9 | 10 | 56.3 | 36.2569 | 0 | 0 | 0 | 0 | 178.9 | 51.9588
2336 | 78.4962 | 0 | 42.9 | 1.6 | 37.6 | 39.2481 | 0 | 0 | 0 | 0 | 129 | 114.5325
2337 | 77.3796 | 0 | 42.9 | 0 | 0 | 38.6898 | 0 | 0 | 0 | 0 | 0 | 75.3233
2338 | 72.8284 | 0 | 42.9 | 0 | 0 | 36.4142 | 0 | 0 | 0 | 0 | 0 | 139.6311
2339 | 71.6665 | 0 | 42.9 | 0 | 0 | 35.8332 | 0 | 0 | 0 | 0 | 0 | 173.7712
2340 | 71.9662 | 0 | 42.9 | 0 | 0 | 35.9831 | 0 | 0 | 0 | 0 | 0 | 130.2842
2341 | 64.7453 | 0 | 42.9 | 0 | 75.1 | 32.3726 | 0 | 0 | 0 | 0 | 0 | 98.515
2342 | 62.313 | 0 | 42.9 | 0 | 37.6 | 31.1565 | 0 | 0 | 0 | 0 | 0 | 153.844
2343 | 57.163 | 0 | 42.9 | 0 | 0 | 28.5815 | 0 | 0 | 0 | 0 | 0 | 95.0354
2344 | 60.6518 | 0 | 42.9 | 0 | 0 | 30.3259 | 0 | 0 | 0 | 0 | 0 | 114.411
2345 | 58.0479 | 0 | 42.9 | 0 | 0 | 29.0239 | 0 | 0 | 0 | 0 | 0 | 126.8145
2346 | 55.9137 | 0 | 42.9 | 0 | 37.6 | 27.9569 | 0 | 0 | 0 | 0 | 0 | 131.2974
2347 | 41.5327 | 0 | 42.9 | 0 | 75.1 | 20.7664 | 0 | 0 | 0 | 0 | 0 | 139.5626
2348 | 42.1098 | 0 | 42.9 | 0 | 75.1 | 21.0549 | 0 | 0 | 0 | 0 | 0 | 328.6098
2349 | 43.2866 | 0 | 42.9 | 0 | 75.1 | 21.6433 | 0 | 0 | 0 | 0 | 0 | 243.2006
2350 | 40.417 | 0 | 42.9 | 0 | 93.9 | 20.2085 | 0 | 0 | 0 | 0 | 0 | 182.4506
2351 | 42.6822 | 0 | 0 | 0 | 0 | 21.3411 | 0 | 0 | 0 | 0 | 0 | 388.4942
2352 | 42.5155 | 0 | 0 | 0 | 0 | 21.2577 | 0 | 0 | 0 | 0 | 0 | 149.972
2353 | 44.0524 | 0 | 0 | 0 | 0 | 22.0262 | 0 | 0 | 0 | 0 | 0 | 53.1073
2354 | 40.4117 | 0 | 0 | 0 | 0 | 20.2059 | 0 | 0 | 0 | 0 | 0 | 48.2835
2355 | 42.8028 | 0 | 0 | 0 | 0 | 21.4014 | 0 | 0 | 0 | 0 | 0 | 52.4206
2356 | 41.2243 | 0 | 0 | 0 | 0 | 20.6122 | 0 | 0 | 0 | 0 | 0 | 48.167
2357 | 43.0114 | 0 | 0 | 0 | 0 | 21.5057 | 0 | 0 | 0 | 0 | 0 | 54.4855
2358 | 62.0483 | 0 | 0 | 0 | 0 | 31.0242 | 0 | 0 | 0 | 0 | 0 | 104.132
2359 | 116.7428 | 0 | 42.9 | 0 | 56.3 | 58.3714 | 0 | 0 | 0 | 0 | 47.9 | 76.8547
2360 | 188.2023 | 0.7 | 43 | 5.3 | 37.6 | 94.1011 | 0 | 0 | 0 | 0 | 32.6 | 69.439
2361 | 300.7271 | 2.1 | 43.2 | 0 | 0 | 150.3636 | 0 | 0 | 0 | 0 | 0 | 155.2018
2362 | 368.9364 | 3.5 | 43.4 | 0 | 0 | 184.4682 | 0 | 0 | 0 | 0 | 0 | 105.7027
2363 | 298.9141 | 3.5 | 43.4 | 0 | 0 | 149.457 | 0 | 0 | 0 | 0 | 0 | 99.472
2364 | 259.9983 | 2.8 | 43.3 | 0 | 0 | 129.9992 | 0 | 0 | 0 | 0 | 0 | 104.616
2365 | 206.9278 | 1.4 | 43.1 | 0 | 75.1 | 103.4639 | 0 | 0 | 0 | 0 | 0 | 149.8532
2366 | 205.8003 | 2.1 | 43.2 | 0 | 37.6 | 102.9002 | 0 | 0 | 0 | 0 | 0 | 125.6668
2367 | 203.889 | 3.5 | 43.4 | 0 | 0 | 101.9445 | 0 | 0 | 0 | 0 | 0 | 104.8645
2368 | 172.492 | 2.8 | 43.3 | 0 | 0 | 86.246 | 0 | 0 | 0 | 0 | 0 | 63.5795
2369 | 132.5222 | 2.1 | 43.2 | 0 | 0 | 66.2611 | 0 | 0 | 0 | 0 | 0 | 178.5617
2370 | 104.1327 | 0.7 | 43 | 0 | 37.6 | 52.0664 | 0 | 0 | 0 | 0 | 0 | 198.5383
2371 | 62.7218 | 0 | 42.9 | 0 | 75.1 | 31.3609 | 0 | 0 | 0 | 0 | 0 | 254.7706
2372 | 45.7377 | 0 | 42.9 | 0 | 75.1 | 22.8689 | 0 | 0 | 0 | 0 | 0 | 242.9285
2373 | 41.5901 | 0 | 42.9 | 0 | 75.1 | 20.795 | 0 | 0 | 0 | 0 | 0 | 195.3214
2374 | 45.3082 | 0 | 42.9 | 0 | 93.9 | 22.6541 | 0 | 0 | 0 | 0 | 0 | 175.2817
2375 | 42.3131 | 0 | 0 | 0 | 0 | 21.1565 | 0 | 0 | 0 | 0 | 0 | 124.0491
2376 | 42.4916 | 0 | 0 | 0 | 0 | 21.2458 | 0 | 0 | 0 | 0 | 0 | 83.9691
2377 | 42.7612 | 0 | 0 | 0 | 0 | 21.3806 | 0 | 0 | 0 | 0 | 0 | 68.1724
2378 | 42.9949 | 0 | 0 | 0 | 0 | 21.4975 | 0 | 0 | 0 | 0 | 0 | 61.0483
2379 | 42.8601 | 0 | 0 | 0 | 0 | 21.4301 | 0 | 0 | 0 | 0 | 0 | 52.5344
2380 | 40.9817 | 0 | 0 | 0 | 0 | 20.4908 | 0 | 0 | 0 | 0 | 0 | 52.1914
2381 | 40.6395 | 0 | 0 | 0 | 0 | 20.3198 | 0 | 0 | 0 | 0 | 0 | 48.7448
2382 | 54.3889 | 0 | 0 | 0 | 0 | 27.1945 | 0 | 0 | 0 | 0 | 0 | 51.3853
2383 | 95.7481 | 0 | 42.9 | 11.5 | 56.3 | 47.874 | 0 | 0 | 0 | 0 | 145.1 | 53.9119
2384 | 169.7864 | 0.7 | 43 | 10.6 | 37.6 | 84.8932 | 0 | 0 | 0 | 0 | 79 | 58.4041
2385 | 234.1372 | 2.1 | 43.2 | 0 | 0 | 117.0686 | 0 | 0 | 0 | 0 | 0 | 48.4006
2386 | 282.6831 | 3.5 | 43.4 | 0 | 0 | 141.3416 | 0 | 0 | 0 | 0 | 0 | 52.0773
2387 | 286.7614 | 3.5 | 43.4 | 0 | 0 | 143.3807 | 0 | 0 | 0 | 0 | 0 | 54.7145
2388 | 256.0744 | 2.8 | 43.3 | 0 | 0 | 128.0372 | 0 | 0 | 0 | 0 | 0 | 66.678
2389 | 214.3464 | 1.4 | 43.1 | 0 | 75.1 | 107.1732 | 0 | 0 | 0 | 0 | 0 | 48.2831
2390 | 205.0689 | 2.1 | 43.2 | 0 | 37.6 | 102.5345 | 0 | 0 | 12.3 | 0 | 0 | 58.2871
2391 | 179.8397 | 3.5 | 43.4 | 0 | 0 | 89.9198 | 0 | 0 | 34.7 | 0 | 0 | 64.6081
2392 | 135.5046 | 2.8 | 43.3 | 0 | 0 | 67.7523 | 0 | 0 | 52.8 | 0 | 0 | 84.4492
2393 | 98.5166 | 2.1 | 43.2 | 0 | 0 | 49.2583 | 0 | 0 | 65.8 | 0 | 0 | 171.9596
2394 | 71.6479 | 0.7 | 43 | 0 | 37.6 | 35.8239 | 0 | 0 | 63.1 | 0 | 0 | 75.5569
2395 | 68.0525 | 0 | 42.9 | 0 | 75.1 | 34.0262 | 0 | 0 | 7 | 0 | 0 | 111.1512
2396 | 53.8996 | 0 | 42.9 | 0 | 75.1 | 26.9498 | 0 | 0 | 0 | 0 | 0 | 83.9686
2397 | 42.2502 | 0 | 42.9 | 0 | 75.1 | 21.1251 | 0 | 0 | 0 | 0 | 0 | 93.9618
2398 | 41.5467 | 0 | 42.9 | 0 | 93.9 | 20.7733 | 0 | 0 | 0 | 0 | 0 | 69.6688
2399 | 42.0187 | 0 | 0 | 0 | 0 | 21.0093 | 0 | 0 | 0 | 0 | 0 | 52.6512
2400 | 45.2397 | 0 | 0 | 0 | 0 | 22.6198 | 0 | 0 | 0 | 0 | 0 | 47.3648
2401 | 43.4753 | 0 | 0 | 0 | 0 | 21.7377 | 0 | 0 | 0 | 0 | 0 | 46.2224
2402 | 40.275 | 0 | 0 | 0 | 0 | 20.1375 | 0 | 0 | 0 | 0 | 0 | 47.5954
2403 | 43.1105 | 0 | 0 | 0 | 0 | 21.5553 | 0 | 0 | 0 | 0 | 0 | 48.2828
2404 | 44.1581 | 0 | 0 | 0 | 0 | 22.079 | 0 | 0 | 0 | 0 | 0 | 47.2483
2405 | 40.7421 | 0 | 0 | 0 | 0 | 20.3711 | 0 | 0 | 0 | 0 | 0 | 54.5988
2406 | 46.3811 | 0 | 0 | 0 | 0 | 23.1906 | 0 | 0 | 0 | 0 | 0 | 69.2081
2407 | 77.7341 | 0 | 42.9 | 0 | 56.3 | 38.8671 | 0 | 0 | 0 | 0 | 0 | 60.8172
2408 | 133.6497 | 0.7 | 43 | 0 | 37.6 | 66.8249 | 0 | 0 | 0 | 0 | 0 | 63.3501
2409 | 203.6674 | 2.1 | 43.2 | 0 | 0 | 101.8337 | 0 | 0 | 0 | 0 | 0 | 147.8568
2410 | 232.5996 | 3.5 | 43.4 | 0 | 0 | 116.2998 | 0 | 0 | 0 | 0 | 0 | 68.172
2411 | 230.8024 | 3.5 | 43.4 | 0 | 0 | 115.4012 | 0 | 0 | 0 | 0 | 0 | 59.666
2412 | 213.0912 | 2.8 | 43.3 | 0 | 0 | 106.5456 | 0 | 0 | 0 | 0 | 0 | 74.2783
2413 | 183.5993 | 1.4 | 43.1 | 0 | 75.1 | 91.7997 | 0 | 0 | 0 | 0 | 0 | 110.9016
2414 | 185.6894 | 2.1 | 43.2 | 0 | 37.6 | 92.8447 | 0 | 0 | 0.2 | 0 | 0 | 96.3488
2415 | 176.2442 | 3.5 | 43.4 | 0 | 0 | 88.1221 | 0 | 0 | 8 | 0 | 0 | 61.0496
2416 | 142.3759 | 2.8 | 43.3 | 0 | 0 | 71.188 | 0 | 0 | 17.3 | 0 | 0 | 72.779
2417 | 94.4083 | 2.1 | 43.2 | 0 | 0 | 47.2041 | 0 | 0 | 28.4 | 0 | 0 | 77.3265
2418 | 71.7808 | 0.7 | 43 | 0 | 37.6 | 35.8904 | 0 | 0 | 35.9 | 0 | 0 | 65.5257
2419 | 56.1099 | 0 | 42.9 | 0 | 75.1 | 28.055 | 0 | 0 | 5.4 | 0 | 0 | 111.3885
2420 | 43.3628 | 0 | 42.9 | 0 | 75.1 | 21.6814 | 0 | 0 | 0 | 0 | 0 | 114.6551
2421 | 42.84 | 0 | 42.9 | 0 | 75.1 | 21.42 | 0 | 0 | 0 | 0 | 0 | 101.6188
2422 | 39.7606 | 0 | 42.9 | 0 | 93.9 | 19.8803 | 0 | 0 | 0 | 0 | 0 | 110.4187
2423 | 44.7757 | 0 | 0 | 0 | 0 | 22.3879 | 0 | 0 | 0 | 0 | 0 | 94.3264
2424 | 42.2269 | 0 | 0 | 0 | 0 | 21.1135 | 0 | 0 | 0 | 0 | 0 | 62.5475
2425 | 42.6689 | 0 | 0 | 0 | 0 | 21.3344 | 0 | 0 | 0 | 0 | 0 | 63.8082
2426 | 41.4797 | 0 | 0 | 0 | 0 | 20.7399 | 0 | 0 | 0 | 0 | 0 | 58.2868
2427 | 41.8169 | 0 | 0 | 0 | 0 | 20.9085 | 0 | 0 | 0 | 0 | 0 | 56.5527
2428 | 42.6509 | 0 | 0 | 0 | 0 | 21.3255 | 0 | 0 | 0 | 0 | 0 | 57.1301
2429 | 43.3684 | 0 | 0 | 0 | 0 | 21.6842 | 0 | 0 | 0 | 0 | 0 | 62.5464
2430 | 53.3318 | 0 | 0 | 0 | 0 | 26.6659 | 0 | 0 | 0 | 0 | 0 | 109.6927
2431 | 112.0367 | 0 | 42.9 | 0 | 56.3 | 56.0183 | 0 | 0 | 0 | 0 | 0 | 78.5313
2432 | 166.3515 | 0.7 | 43 | 0 | 37.6 | 83.1758 | 0 | 0 | 0 | 0 | 0 | 62.2016
2433 | 224.2038 | 2.1 | 43.2 | 0 | 0 | 112.1019 | 0 | 0 | 0 | 0 | 0 | 48.7439
2434 | 225.0986 | 3.5 | 43.4 | 0 | 0 | 112.5493 | 0 | 0 | 0 | 0 | 0 | 89.1868
2435 | 228.9583 | 3.5 | 43.4 | 0 | 0 | 114.4792 | 0 | 0 | 0 | 0 | 0 | 62.4313
2436 | 209.4258 | 2.8 | 43.3 | 0 | 0 | 104.7129 | 0 | 0 | 0 | 0 | 0 | 57.938
2437 | 197.4485 | 1.4 | 43.1 | 0 | 75.1 | 98.7243 | 0 | 0 | 0 | 0 | 0 | 52.1922
2438 | 212.5867 | 2.1 | 43.2 | 0 | 37.6 | 106.2933 | 0 | 0 | 0 | 0 | 0 | 72.8945
2439 | 214.6449 | 3.5 | 43.4 | 0 | 0 | 107.3224 | 0 | 0 | 0 | 0 | 0 | 184.3872
2440 | 184.0503 | 2.8 | 43.3 | 0 | 0 | 92.0251 | 0 | 2.7 | 0 | 0 | 0 | 134.132
2441 | 126.5764 | 2.1 | 43.2 | 0 | 0 | 63.2882 | 0 | 11.9 | 0 | 0 | 0 | 180.4616
2442 | 90.763 | 0.7 | 43 | 0 | 37.6 | 45.3815 | 0 | 14.9 | 0 | 0 | 0 | 106.3029
2443 | 72.0595 | 0 | 42.9 | 0 | 75.1 | 36.0297 | 0 | 0 | 0 | 0 | 0 | 152.0756
2444 | 46.7998 | 0 | 42.9 | 0 | 75.1 | 23.3999 | 0 | 0 | 0 | 0 | 0 | 104.4994
2445 | 42.8331 | 0 | 42.9 | 0 | 75.1 | 21.4166 | 0 | 0 | 0 | 0 | 0 | 115.0179
2446 | 41.2312 | 0 | 42.9 | 0 | 93.9 | 20.6156 | 0 | 0 | 0 | 0 | 0 | 201.3414
2447 | 42.0794 | 0 | 0 | 0 | 0 | 21.0397 | 0 | 0 | 0 | 0 | 0 | 133.1147
2448 | 42.641 | 0 | 0 | 0 | 0 | 21.3205 | 0 | 0 | 0 | 0 | 0 | 63.693
2449 | 39.3704 | 0 | 0 | 0 | 0 | 19.6852 | 0 | 0 | 0 | 0 | 0 | 61.0503
2450 | 43.6817 | 0 | 0 | 0 | 0 | 21.8409 | 0 | 0 | 0 | 0 | 0 | 55.4023
2451 | 43.0572 | 0 | 0 | 0 | 0 | 21.5286 | 0 | 0 | 0 | 0 | 0 | 56.5536
2452 | 44.8715 | 0 | 0 | 0 | 0 | 22.4358 | 0 | 0 | 0 | 0 | 0 | 56.4362
2453 | 42.1529 | 0 | 0 | 0 | 0 | 21.0764 | 0 | 0 | 0 | 0 | 0 | 57.7081
2454 | 56.6644 | 0 | 0 | 0 | 0 | 28.3322 | 0 | 0 | 0 | 0 | 0 | 58.9794
2455 | 96.0843 | 0 | 42.9 | 13.9 | 56.3 | 48.0422 | 0 | 0 | 0 | 0 | 110.9 | 52.9924
2456 | 172.4353 | 0.7 | 43 | 13.3 | 37.6 | 86.2177 | 0 | 0 | 0 | 0 | 58.9 | 49.3202
2457 | 291.2243 | 2.1 | 43.2 | 0 | 0 | 145.6121 | 0 | 0 | 0 | 0 | 0 | 68.9777
2458 | 381.2756 | 3.5 | 43.4 | 0 | 0 | 190.6378 | 0 | 0 | 0 | 0 | 0 | 77.2106
2459 | 373.6116 | 3.5 | 43.4 | 0 | 0 | 186.8058 | 0 | 0 | 0 | 0 | 0 | 63.2328
2460 | 348.6414 | 2.8 | 43.3 | 0 | 0 | 174.3207 | 0 | 0 | 0 | 0 | 0 | 94.2003
2461 | 312.1636 | 1.4 | 43.1 | 0 | 75.1 | 156.0818 | 0 | 0 | 0 | 0 | 0 | 80.4278
2462 | 273.5962 | 2.1 | 43.2 | 0 | 37.6 | 136.7981 | 0 | 3.8 | 0 | 0 | 0 | 181.1479
2463 | 263.5088 | 3.5 | 43.4 | 0 | 0 | 131.7544 | 0 | 15.2 | 0 | 0 | 0 | 115.5014
2464 | 197.4712 | 2.8 | 43.3 | 0 | 0 | 98.7356 | 0 | 26.2 | 0 | 0 | 0 | 96.1111
2465 | 157.9167 | 2.1 | 43.2 | 0 | 0 | 78.9583 | 0 | 45 | 0 | 0 | 0 | 99.1081
2466 | 104.5158 | 0.7 | 43 | 0 | 37.6 | 52.2579 | 0 | 45.7 | 0 | 0 | 0 | 81.6109
2467 | 88.026 | 0 | 42.9 | 0 | 75.1 | 44.013 | 0 | 0 | 0 | 0 | 0 | 84.9235
2468 | 57.3205 | 0 | 42.9 | 0 | 75.1 | 28.6602 | 0 | 0 | 0 | 0 | 0 | 190.4635
2469 | 41.9558 | 0 | 42.9 | 0 | 75.1 | 20.9779 | 0 | 0 | 0 | 0 | 0 | 267.2477
2470 | 40.761 | 0 | 42.9 | 0 | 93.9 | 20.3805 | 0 | 0 | 0 | 0 | 0.8 | 137.6149
2471 | 41.2488 | 0 | 0 | 0 | 0 | 20.6244 | 0 | 0 | 0 | 0 | 0 | 146.1986
2472 | 40.5047 | 0 | 0 | 0 | 0 | 20.2524 | 0 | 0 | 0 | 0 | 0 | 124.1411
2473 | 41.6666 | 0 | 0 | 0 | 0 | 20.8333 | 0 | 0 | 0 | 0 | 0 | 64.6099
2474 | 40.4973 | 0 | 0 | 0 | 0 | 20.2486 | 0 | 0 | 0 | 0 | 0 | 59.5511
2475 | 39.8433 | 0 | 0 | 0 | 0 | 19.9217 | 0 | 0 | 0 | 0 | 0 | 49.7786
2476 | 39.2418 | 0 | 0 | 0 | 0 | 19.6209 | 0 | 0 | 0 | 0 | 0 | 50.8121
2477 | 41.1859 | 0 | 0 | 0 | 0 | 20.593 | 0 | 0 | 0 | 0 | 0 | 51.0413
2478 | 46.7847 | 0 | 0 | 0 | 0 | 23.3923 | 0 | 0 | 0 | 0 | 0 | 62.3151
2479 | 48.0095 | 0 | 42.9 | 23.2 | 56.3 | 24.0047 | 0 | 0 | 0 | 0 | 231 | 49.4338
2480 | 47.4975 | 0 | 42.9 | 38.6 | 37.6 | 23.7487 | 0 | 0 | 0 | 0 | 218.2 | 107.5161
2481 | 50.1005 | 0 | 42.9 | 19.7 | 0 | 25.0503 | 0 | 0 | 0 | 0 | 0 | 79.4759
2482 | 46.8879 | 0 | 42.9 | 14.9 | 0 | 23.4439 | 0 | 0 | 0 | 0 | 0 | 129.2853
2483 | 48.6033 | 0 | 42.9 | 5.6 | 0 | 24.3016 | 0 | 0 | 0 | 0 | 0 | 134.5463
2484 | 46.5054 | 0 | 42.9 | 0 | 0 | 23.2527 | 0 | 0 | 0 | 0 | 0 | 132.4614
2485 | 46.48 | 0 | 42.9 | 0 | 75.1 | 23.24 | 0 | 0 | 0 | 0 | 28.2 | 96.9519
2486 | 44.6446 | 0 | 42.9 | 0 | 37.6 | 22.3223 | 0 | 0 | 0 | 0 | 2.3 | 233.7241
2487 | 44.0081 | 0 | 42.9 | 0 | 0 | 22.004 | 0 | 0 | 0 | 0 | 0 | 275.7393
2488 | 44.2018 | 0 | 42.9 | 0 | 0 | 22.1009 | 0 | 0 | 0 | 0 | 0 | 121.714
2489 | 42.1371 | 0 | 42.9 | 0 | 0 | 21.0685 | 0 | 0 | 0 | 0 | 0 | 228.0526
2490 | 44.9003 | 0 | 42.9 | 0 | 37.6 | 22.4502 | 0 | 0 | 0 | 0 | 1 | 133.1904
2491 | 42.2874 | 0 | 42.9 | 0 | 75.1 | 21.1437 | 0 | 0 | 0 | 0 | 0 | 121.9898
2492 | 41.6781 | 0 | 42.9 | 0 | 75.1 | 20.839 | 0 | 0 | 0 | 0 | 0 | 322.3433
2493 | 42.8672 | 0 | 42.9 | 0 | 75.1 | 21.4336 | 0 | 0 | 0 | 0 | 4.8 | 161.0281
2494 | 39.5421 | 0 | 42.9 | 0 | 93.9 | 19.771 | 0 | 0 | 0 | 0 | 14.5 | 181.6954
2495 | 41.6375 | 0 | 0 | 0 | 0 | 20.8187 | 0 | 0 | 0 | 0 | 0 | 159.7558
2496 | 39.4172 | 0 | 0 | 0 | 0 | 19.7086 | 0 | 0 | 0 | 0 | 0 | 191.3124
2497 | 42.2657 | 0 | 0 | 0 | 0 | 21.1328 | 0 | 0 | 0 | 0 | 0 | 68.0572
2498 | 43.7288 | 0 | 0 | 0 | 0 | 21.8644 | 0 | 0 | 0 | 0 | 0 | 47.5933
2499 | 42.1464 | 0 | 0 | 0 | 0 | 21.0732 | 0 | 0 | 0 | 0 | 0 | 46.1086
2500 | 41.3477 | 0 | 0 | 0 | 0 | 20.6738 | 0 | 0 | 0 | 0 | 0 | 46.4493
2501 | 41.4912 | 0 | 0 | 0 | 0 | 20.7456 | 0 | 0 | 0 | 0 | 0 | 53.4528
2502 | 47.4008 | 0 | 0 | 0 | 0 | 23.7004 | 0 | 0 | 0 | 0 | 0 | 106.4258
2503 | 57.1255 | 0 | 42.9 | 38.3 | 56.3 | 28.5628 | 0 | 0 | 0 | 0 | 349 | 121.6839
2504 | 59.2029 | 0 | 42.9 | 11.2 | 37.6 | 29.6015 | 0 | 0 | 0 | 0 | 237.6 | 106.6707
2505 | 55.9959 | 0 | 42.9 | 0 | 0 | 27.9979 | 0 | 0 | 0 | 0 | 0 | 174.6163
2506 | 56.2485 | 0 | 42.9 | 0 | 0 | 28.1242 | 0 | 0 | 0 | 0 | 0 | 157.5682
2507 | 51.2937 | 0 | 42.9 | 0 | 0 | 25.6469 | 0 | 0 | 0 | 0 | 0 | 64.7241
2508 | 52.7051 | 0 | 42.9 | 0 | 0 | 26.3526 | 0 | 0 | 0 | 0 | 0 | 279.6061
2509 | 53.1954 | 0 | 42.9 | 0 | 75.1 | 26.5977 | 0 | 0 | 0 | 0 | 5.3 | 120.3852
2510 | 52.2368 | 0 | 42.9 | 0 | 37.6 | 26.1184 | 0 | 0 | 0 | 0 | 3 | 183.0659
2511 | 51.1316 | 0 | 42.9 | 0 | 0 | 25.5658 | 0 | 0 | 0 | 0 | 0 | 101.9816
2512 | 49.7088 | 0 | 42.9 | 0 | 0 | 24.8544 | 0 | 0 | 0 | 0 | 0 | 102.1005
2513 | 48.2314 | 0 | 42.9 | 0 | 0 | 24.1157 | 0 | 0 | 0 | 0 | 0 | 124.573
2514 | 48.5587 | 0 | 42.9 | 0 | 37.6 | 24.2793 | 0 | 0 | 0 | 0 | 0 | 329.7168
2515 | 49.7255 | 0 | 42.9 | 0 | 75.1 | 24.8628 | 0 | 0 | 0 | 0 | 0 | 180.0402
2516 | 44.4069 | 0 | 42.9 | 0 | 75.1 | 22.2035 | 0 | 0 | 0 | 0 | 0 | 155.7638
2517 | 43.5289 | 0 | 42.9 | 0 | 75.1 | 21.7645 | 0 | 0 | 0 | 0 | 7 | 137.9091
2518 | 43.0101 | 0 | 42.9 | 0 | 93.9 | 21.5051 | 0 | 0 | 0 | 0 | 27.5 | 134.8102
2519 | 42.6044 | 0 | 0 | 0 | 0 | 21.3022 | 0 | 0 | 0 | 0 | 0 | 97.1927
2520 | 43.1694 | 0 | 0 | 0 | 0 | 21.5847 | 0 | 0 | 0 | 0 | 0 | 81.015
2521 | 41.6322 | 0 | 0 | 0 | 0 | 20.8161 | 0 | 0 | 0 | 0 | 0 | 72.3184
2522 | 42.6122 | 0 | 0 | 0 | 0 | 21.3061 | 0 | 0 | 0 | 0 | 0 | 61.625
2523 | 42.186 | 0 | 0 | 0 | 0 | 21.093 | 0 | 0 | 0 | 0 | 0 | 56.6694
2524 | 44.177 | 0 | 0 | 0 | 0 | 22.0885 | 0 | 0 | 0 | 0 | 0 | 47.1345
2525 | 41.1847 | 0 | 0 | 0 | 0 | 20.5923 | 0 | 0 | 0 | 0 | 2 | 57.0162
2526 | 63.4368 | 0 | 0 | 0 | 0 | 31.7184 | 0 | 0 | 0 | 0 | 7.5 | 107.3912
2527 | 100.8615 | 0 | 42.9 | 78.5 | 56.3 | 50.4307 | 0 | 0 | 0 | 0 | 439.2 | 99.2319
2528 | 172.5196 | 0.7 | 43 | 98 | 37.6 | 86.2598 | 0 | 0 | 0 | 1.8 | 329.2 | 86.819
2529 | 264.1764 | 2.1 | 43.2 | 40.3 | 0 | 132.0882 | 0 | 0 | 0 | 0 | 0 | 119.9368
2530 | 335.2422 | 3.5 | 43.4 | 10 | 0 | 167.6211 | 0 | 0 | 0 | 1.5 | 0 | 107.7633
2531 | 336.9059 | 3.5 | 43.4 | 0 | 0 | 168.453 | 0 | 0 | 0 | 0 | 0 | 133.8585
2532 | 308.3701 | 2.8 | 43.3 | 0 | 0 | 154.1851 | 0 | 0 | 0 | 0 | 0 | 75.7941
2533 | 294.828 | 1.4 | 43.1 | 0 | 75.1 | 147.414 | 0 | 0 | 0 | 0 | 55.8 | 120.4002
2534 | 283.8462 | 2.1 | 43.2 | 0 | 37.6 | 141.9231 | 0 | 0 | 0 | 0 | 19.5 | 84.6854
2535 | 266.5709 | 3.5 | 43.4 | 0 | 0 | 133.2854 | 0 | 0 | 0 | 0 | 0 | 104.7385
2536 | 201.2872 | 2.8 | 43.3 | 0 | 0 | 100.6436 | 0 | 0 | 0 | 0 | 0 | 86.5815
2537 | 151.2846 | 2.1 | 43.2 | 0 | 0 | 75.6423 | 0 | 0 | 0 | 0 | 0 | 94.4422
2538 | 117.081 | 0.7 | 43 | 0 | 37.6 | 58.5405 | 0 | 0 | 0 | 0 | 0 | 126.643
2539 | 83.5613 | 0 | 42.9 | 0 | 75.1 | 41.7807 | 0 | 0 | 0 | 0 | 0 | 138.0674
2540 | 60.1073 | 0 | 42.9 | 0 | 75.1 | 30.0536 | 0 | 0 | 0 | 0 | 0 | 188.8067
2541 | 42.6528 | 0 | 42.9 | 0 | 75.1 | 21.3264 | 0 | 0 | 0 | 0 | 4.5 | 158.9883
2542 | 41.6062 | 0 | 42.9 | 0 | 93.9 | 20.8031 | 0 | 0 | 0 | 0 | 18.9 | 142.3335
2543 | 40.7003 | 0 | 0 | 0 | 0 | 20.3501 | 0 | 0 | 0 | 0 | 0 | 112.8446
2544 | 40.9916 | 0 | 0 | 0 | 0 | 20.4958 | 0 | 0 | 0 | 0 | 0 | 73.2401
2545 | 41.8126 | 0 | 0 | 0 | 0 | 20.9063 | 0 | 0 | 0 | 0 | 0 | 58.0556
2546 | 43.1672 | 0 | 0 | 0 | 0 | 21.5836 | 0 | 0 | 0 | 0 | 0 | 48.1679
2547 | 42.072 | 0 | 0 | 0 | 0 | 21.036 | 0 | 0 | 0 | 0 | 0 | 45.2023
2548 | 40.3488 | 0 | 0 | 0 | 0 | 20.1744 | 0 | 0 | 0 | 0 | 0 | 45.5408
2549 | 41.1255 | 0 | 0 | 0 | 0 | 20.5627 | 0 | 0 | 0 | 0 | 0 | 59.6663
2550 | 65.6053 | 0 | 0 | 0 | 0 | 32.8027 | 0 | 0 | 0 | 0 | 0 | 68.058
2551 | 100.7539 | 0 | 42.9 | 37 | 56.3 | 50.377 | 0 | 0 | 0 | 0 | 356.2 | 119.6097
2552 | 190.6268 | 0.7 | 43 | 51.7 | 37.6 | 95.3134 | 0 | 0 | 0 | 0 | 262.4 | 66.1027
2553 | 266.2371 | 2.1 | 43.2 | 18 | 0 | 133.1185 | 0 | 0 | 0 | 0 | 0 | 132.1095
2554 | 303.7299 | 3.5 | 43.4 | 1.5 | 0 | 151.865 | 0 | 0 | 0 | 0 | 0 | 142.1657
2555 | 274.909 | 3.5 | 43.4 | 0 | 0 | 137.4545 | 0 | 0 | 0 | 0 | 0 | 261.6675
2556 | 235.4351 | 2.8 | 43.3 | 0 | 0 | 117.7176 | 0 | 0 | 0 | 0 | 0 | 200.8991
2557 | 229.5903 | 1.4 | 43.1 | 0 | 75.1 | 114.7951 | 0 | 0 | 0 | 0 | 8.4 | 143.2915
2558 | 234.6721 | 2.1 | 43.2 | 0 | 37.6 | 117.336 | 0 | 0 | 0 | 0 | 0.5 | 248.0679
2559 | 198.5658 | 3.5 | 43.4 | 0 | 0 | 99.2829 | 0 | 0 | 0 | 0 | 0 | 171.5876
2560 | 150.7531 | 2.8 | 43.3 | 0 | 0 | 75.3766 | 0 | 0 | 0 | 0 | 0 | 118.9499
2561 | 113.8572 | 2.1 | 43.2 | 0 | 0 | 56.9286 | 0 | 0 | 0 | 0 | 0 | 123.4105
2562 | 82.3768 | 0.7 | 43 | 0 | 37.6 | 41.1884 | 0 | 0 | 0 | 0 | 0 | 224.5396
2563 | 58.6094 | 0 | 42.9 | 0 | 75.1 | 29.3047 | 0 | 0 | 0 | 0 | 0 | 148.5417
2564 | 44.2907 | 0 | 42.9 | 0 | 75.1 | 22.1454 | 0 | 0 | 0 | 0 | 0 | 314.9096
2565 | 45.6395 | 0 | 42.9 | 0 | 75.1 | 22.8197 | 0 | 0 | 0 | 0 | 0 | 230.003
2566 | 42.8908 | 0 | 42.9 | 0 | 93.9 | 21.4454 | 0 | 0 | 0 | 0 | 1.5 | 220.9439
2567 | 41.6015 | 0 | 0 | 0 | 0 | 20.8008 | 0 | 0 | 0 | 0 | 0 | 138.1088
2568 | 43.4607 | 0 | 0 | 0 | 0 | 21.7304 | 0 | 0 | 0 | 0 | 0 | 70.4727
2569 | 41.5727 | 0 | 0 | 0 | 0 | 20.7863 | 0 | 0 | 0 | 0 | 0 | 63.8086
2570 | 41.0833 | 0 | 0 | 0 | 0 | 20.5417 | 0 | 0 | 0 | 0 | 0 | 55.2878
2571 | 42.275 | 0 | 0 | 0 | 0 | 21.1375 | 0 | 0 | 0 | 0 | 0 | 51.0403
2572 | 42.1002 | 0 | 0 | 0 | 0 | 21.0501 | 0 | 0 | 0 | 0 | 0 | 50.0078
2573 | 44.1726 | 0 | 0 | 0 | 0 | 22.0863 | 0 | 0 | 0 | 0 | 0 | 46.9058
2574 | 63.7799 | 0 | 0 | 0 | 0 | 31.8899 | 0 | 0 | 0 | 0 | 1.1 | 103.2978
2575 | 108.2606 | 0 | 42.9 | 56.1 | 56.3 | 54.1303 | 0 | 0 | 0 | 0 | 417.1 | 78.2877
2576 | 203.6383 | 0.7 | 43 | 87.6 | 37.6 | 101.8191 | 0 | 0 | 0 | 1.4 | 326.3 | 83.2655
2577 | 322.6826 | 2.1 | 43.2 | 49.1 | 0 | 161.3413 | 0 | 0 | 0 | 0.6 | 0 | 77.0901
2578 | 377.4097 | 3.5 | 43.4 | 24.2 | 0 | 188.7048 | 0 | 0 | 0 | 11.9 | 0 | 166.4607
2579 | 372.6369 | 3.5 | 43.4 | 5.4 | 0 | 186.3184 | 0 | 0 | 0 | 2.6 | 0 | 107.8838
2580 | 346.7103 | 2.8 | 43.3 | 0 | 0 | 173.3552 | 0 | 0 | 0 | 0 | 0 | 210.2658
2581 | 272.7544 | 1.4 | 43.1 | 0 | 75.1 | 136.3772 | 0 | 0 | 0 | 0 | 139.8 | 151.9627
2582 | 256.8263 | 2.1 | 43.2 | 0 | 37.6 | 128.4131 | 0 | 0 | 0 | 0 | 91.1 | 248.8156
2583 | 240.8653 | 3.5 | 43.4 | 0 | 0 | 120.4326 | 0 | 0 | 0 | 0 | 0 | 157.0427
2584 | 216.5816 | 2.8 | 43.3 | 0 | 0 | 108.2908 | 0 | 0 | 0 | 0 | 0 | 212.7466
2585 | 154.7121 | 2.1 | 43.2 | 0 | 0 | 77.356 | 0 | 0 | 0 | 0 | 0 | 245.6283
2586 | 117.0819 | 0.7 | 43 | 0 | 37.6 | 58.541 | 0 | 0 | 0 | 0 | 54.7 | 143.8357
2587 | 97.5497 | 0 | 42.9 | 0 | 75.1 | 48.7748 | 0 | 0 | 0 | 0 | 51 | 251.2766
2588 | 56.1567 | 0 | 42.9 | 0 | 75.1 | 28.0784 | 0 | 0 | 0 | 0 | 32.5 | 451.9984
2589 | 43.7226 | 0 | 42.9 | 0 | 75.1 | 21.8613 | 0 | 0 | 0 | 0 | 109.6 | 198.3831
2590 | 41.7679 | 0 | 42.9 | 0 | 93.9 | 20.884 | 0 | 0 | 0 | 0 | 157.4 | 139.219
2591 | 41.2944 | 0 | 0 | 0 | 0 | 20.6472 | 0 | 0 | 0 | 0 | 0 | 91.6967
2592 | 42.0797 | 0 | 0 | 0 | 0 | 21.0399 | 0 | 0 | 0 | 0 | 0 | 64.2647
2593 | 44.1543 | 0 | 0 | 0 | 0 | 22.0772 | 0 | 0 | 0 | 0 | 0 | 62.8899
2594 | 43.908 | 0 | 0 | 0 | 0 | 21.954 | 0 | 0 | 0 | 0 | 0 | 48.5139
2595 | 39.9915 | 0 | 0 | 0 | 0 | 19.9957 | 0 | 0 | 0 | 0 | 0 | 47.4787
2596 | 42.2942 | 0 | 0 | 0 | 0 | 21.1471 | 0 | 0 | 0 | 0 | 4.3 | 47.3638
2597 | 41.5947 | 0 | 0 | 0 | 0 | 20.7973 | 0 | 0 | 0 | 0 | 7.3 | 52.5352
2598 | 55.5942 | 0 | 0 | 0 | 0 | 27.7971 | 0 | 0 | 0 | 0 | 8.8 | 83.1483
2599 | 89.6398 | 0 | 42.9 | 95.9 | 56.3 | 44.8199 | 0 | 0 | 0 | 0 | 469.9 | 158.7583
2600 | 165.4989 | 0.7 | 43 | 157 | 37.6 | 82.7495 | 0 | 0 | 0 | 2.4 | 423.4 | 171.7664
2601 | 241.2728 | 2.1 | 43.2 | 157.3 | 0 | 120.6364 | 0 | 0 | 0 | 1.8 | 29.9 | 93.6056
2602 | 246.5492 | 3.5 | 43.4 | 158.4 | 0 | 123.2746 | 0 | 0 | 0 | 19.8 | 51 | 73.9307
2603 | 247.4468 | 3.5 | 43.4 | 152.7 | 0 | 123.7234 | 0 | 0 | 0 | 8.6 | 64.7 | 77.8085
2604 | 235.2634 | 2.8 | 43.3 | 146.8 | 0 | 117.6317 | 0 | 0 | 0 | 0 | 82 | 175.1567
2605 | 233.5632 | 1.4 | 43.1 | 138.4 | 75.1 | 116.7816 | 0 | 0 | 0 | 0 | 541.1 | 152.4268
2606 | 247.1672 | 2.1 | 43.2 | 138.1 | 37.6 | 123.5836 | 0 | 0 | 0 | 0 | 458.8 | 134.5157
2607 | 239.7846 | 3.5 | 43.4 | 147.1 | 0 | 119.8923 | 0 | 0 | 0 | 0 | 58.1 | 195.1413
2608 | 198.6901 | 2.8 | 43.3 | 145.7 | 0 | 99.345 | 0 | 0 | 0 | 0 | 103.9 | 161.457
2609 | 146.4976 | 2.1 | 43.2 | 139 | 0 | 73.2488 | 0 | 0 | 0 | 0 | 125.7 | 102.3374
2610 | 109.0369 | 0.7 | 43 | 139.4 | 37.6 | 54.5185 | 0 | 0 | 0 | 0 | 592.6 | 137.086
2611 | 94.8505 | 0 | 42.9 | 89.2 | 75.1 | 47.4253 | 0 | 0 | 0 | 0 | 516.6 | 154.48
2612 | 75.2321 | 0 | 42.9 | 52.6 | 75.1 | 37.6161 | 0 | 0 | 0 | 0 | 446.5 | 278.7941
2613 | 51.811 | 0 | 42.9 | 69.7 | 75.1 | 25.9055 | 0 | 0 | 0 | 0 | 500.5 | 241.7364
2614 | 41.106 | 0 | 42.9 | 82.7 | 93.9 | 20.553 | 0 | 0 | 0 | 0 | 531.1 | 150.027
2615 | 43.5612 | 0 | 0 | 2.2 | 0 | 21.7806 | 0 | 0 | 0 | 0 | 81.9 | 124.3262
2616 | 42.8806 | 0 | 0 | 9.4 | 0 | 21.4403 | 0 | 0 | 0 | 0 | 146.2 | 90.2607
2617 | 41.7091 | 0 | 0 | 19.5 | 0 | 20.8545 | 0 | 0 | 0 | 0 | 193 | 56.9009
2618 | 40.4762 | 0 | 0 | 37.4 | 0 | 20.2381 | 0 | 0 | 0 | 0 | 247.8 | 47.0213
2619 | 43.6895 | 0 | 0 | 58 | 0 | 21.8447 | 0 | 0 | 0 | 0 | 292.5 | 48.2826
2620 | 40.0544 | 0 | 0 | 76.2 | 0 | 20.0272 | 0 | 0 | 0 | 0 | 330 | 50.9258
2621 | 41.957 | 0 | 0 | 91.8 | 0 | 20.9785 | 0 | 0 | 0 | 0 | 362.5 | 60.2441
2622 | 57 | 0 | 0 | 101.1 | 0 | 28.5 | 0 | 0 | 0 | 0 | 378.1 | 85.6312
2623 | 93.1757 | 0 | 42.9 | 248.3 | 56.3 | 46.5879 | 0 | 0 | 0 | 0 | 851.7 | 72.0884
2624 | 174.2198 | 0.7 | 43 | 244.4 | 37.6 | 87.1099 | 0 | 0 | 0 | 0.1 | 726.2 | 66.795
2625 | 255.5274 | 2.1 | 43.2 | 193.3 | 0 | 127.7637 | 0 | 0 | 0 | 0 | 179.1 | 76.1471
2626 | 290.8353 | 3.5 | 43.4 | 156.5 | 0 | 145.4177 | 0 | 0 | 0 | 6.7 | 170.5 | 70.9356
2627 | 261.2702 | 3.5 | 43.4 | 111 | 0 | 130.6351 | 0 | 0 | 0 | 0.4 | 120.9 | 81.4877
2628 | 246.1005 | 2.8 | 43.3 | 62.8 | 0 | 123.0502 | 0 | 0 | 0 | 0 | 77.4 | 140.7934
2629 | 238.6568 | 1.4 | 43.1 | 17 | 75.1 | 119.3284 | 0 | 0 | 0 | 0 | 454.4 | 103.4193
2630 | 246.3766 | 2.1 | 43.2 | 0.5 | 37.6 | 123.1883 | 0 | 0 | 0 | 0 | 320.2 | 134.9437
2631 | 233.23 | 3.5 | 43.4 | 0 | 0 | 116.615 | 0 | 0 | 0 | 0 | 0 | 97.0752
2632 | 217.4949 | 2.8 | 43.3 | 0 | 0 | 108.7475 | 0 | 0 | 0 | 0 | 0 | 89.9061
2633 | 173.2346 | 2.1 | 43.2 | 0 | 0 | 86.6173 | 0 | 0 | 0 | 0 | 0 | 123.2315
2634 | 134.8058 | 0.7 | 43 | 0 | 37.6 | 67.4029 | 0 | 0 | 0 | 0 | 267.8 | 105.8203
2635 | 128.4003 | 0 | 42.9 | 0 | 75.1 | 64.2001 | 0 | 0 | 0 | 0 | 223.3 | 135.4446
2636 | 89.1142 | 0 | 42.9 | 0 | 75.1 | 44.5571 | 0 | 0 | 0 | 0 | 216.6 | 146.8433
2637 | 59.1028 | 0 | 42.9 | 0 | 75.1 | 29.5514 | 0 | 0 | 0 | 0 | 298.1 | 162.0469
2638 | 57.8914 | 0 | 42.9 | 0 | 93.9 | 28.9457 | 0 | 0 | 0 | 0 | 346.3 | 207.1936
2639 | 57.6806 | 0 | 0 | 0 | 0 | 28.8403 | 0 | 0 | 0 | 0 | 0 | 228.2956
2640 | 55.8645 | 0 | 0 | 0 | 0 | 27.9322 | 0 | 0 | 0 | 0 | 0.4 | 85.5144
2641 | 55.8573 | 0 | 0 | 0 | 0 | 27.9287 | 0 | 0 | 0 | 0 | 14.3 | 65.7568
2642 | 56.7921 | 0 | 0 | 0 | 0 | 28.396 | 0 | 0 | 0 | 0 | 64.9 | 59.2083
2643 | 45.9897 | 0 | 0 | 2 | 0 | 22.9949 | 0 | 0 | 0 | 0 | 113.2 | 50.5822
2644 | 43.1905 | 0 | 0 | 10.2 | 0 | 21.5952 | 0 | 0 | 0 | 0 | 156.3 | 47.7098
2645 | 45.2434 | 0 | 0 | 17.6 | 0 | 22.6217 | 0 | 0 | 0 | 0 | 193.9 | 68.7456
2646 | 55.5809 | 0 | 0 | 26.7 | 0 | 27.7904 | 0 | 0 | 0 | 0 | 213.4 | 62.4296
2647 | 72.5088 | 0 | 42.9 | 193.1 | 56.3 | 36.2544 | 0 | 0 | 0 | 0 | 663.7 | 51.7294
2648 | 69.7707 | 0 | 42.9 | 165.4 | 37.6 | 34.8853 | 0 | 0 | 0 | 0 | 530.4 | 75.7909
2649 | 67.2302 | 0 | 42.9 | 94.8 | 0 | 33.6151 | 0 | 0 | 0 | 0 | 19.4 | 186.8417
2650 | 61.8704 | 0 | 42.9 | 38.4 | 0 | 30.9352 | 0 | 0 | 0 | 0 | 6.6 | 130.2619
2651 | 68.8542 | 0 | 42.9 | 0.2 | 0 | 34.4271 | 0 | 0 | 0 | 0 | 0.5 | 112.963
2652 | 78.1107 | 0 | 42.9 | 0 | 0 | 39.0553 | 0 | 0 | 0 | 0 | 0 | 148.1802
2653 | 80.5696 | 0 | 42.9 | 0 | 75.1 | 40.2848 | 0 | 0 | 0 | 0 | 324.5 | 215.5294
2654 | 86.121 | 0 | 42.9 | 0 | 37.6 | 43.0605 | 0 | 0 | 0 | 0 | 246.1 | 204.1466
2655 | 82.9836 | 0 | 42.9 | 0 | 0 | 41.4918 | 0 | 0 | 0 | 0 | 0 | 155.7356
2656 | 87.559 | 0 | 42.9 | 0 | 0 | 43.7795 | 0 | 0 | 0 | 0 | 0 | 131.7158
2657 | 84.3392 | 0 | 42.9 | 4.4 | 0 | 42.1696 | 0 | 0 | 0 | 0 | 0 | 118.7621
2658 | 82.7586 | 0 | 42.9 | 23 | 37.6 | 41.3793 | 0 | 0 | 0 | 0 | 391.7 | 129.0309
2659 | 85.3353 | 0 | 42.9 | 17.1 | 75.1 | 42.6677 | 0 | 0 | 0 | 0 | 345.9 | 246.3676
2660 | 74.1053 | 0 | 42.9 | 6.5 | 75.1 | 37.0526 | 0 | 0 | 0 | 0 | 318.6 | 339.1379
2661 | 64.4062 | 0 | 42.9 | 17.8 | 75.1 | 32.2031 | 0 | 0 | 0 | 0 | 384.1 | 215.6157
2662 | 63.3795 | 0 | 42.9 | 38.5 | 93.9 | 31.6897 | 0 | 0 | 0 | 0 | 422.9 | 217.9082
2663 | 54.4962 | 0 | 0 | 0 | 0 | 27.2481 | 0 | 0 | 0 | 0 | 3.3 | 130.6379
2664 | 45.8815 | 0 | 0 | 0 | 0 | 22.9408 | 0 | 0 | 0 | 0 | 38.8 | 90.3832
2665 | 41.5414 | 0 | 0 | 5.1 | 0 | 20.7707 | 0 | 0 | 0 | 0 | 86.3 | 64.4946
2666 | 44.4451 | 0 | 0 | 12 | 0 | 22.2225 | 0 | 0 | 0 | 0 | 126.2 | 65.6393
2667 | 43.4908 | 0 | 0 | 19.9 | 0 | 21.7454 | 0 | 0 | 0 | 0 | 162.2 | 58.2858
2668 | 43.2075 | 0 | 0 | 31.8 | 0 | 21.6038 | 0 | 0 | 0 | 0 | 194.3 | 61.6253
2669 | 44.0372 | 0 | 0 | 46 | 0 | 22.0186 | 0 | 0 | 0 | 0 | 222.2 | 63.0041
2670 | 48.5683 | 0 | 0 | 56.6 | 0 | 24.2841 | 0 | 0 | 0 | 0 | 237.8 | 73.1242
2671 | 64.4382 | 0 | 42.9 | 212.8 | 56.3 | 32.2191 | 0 | 0 | 0 | 0 | 701.4 | 67.6001
2672 | 68.2858 | 0 | 42.9 | 171.8 | 37.6 | 34.1429 | 0 | 0 | 0 | 0 | 588.3 | 74.6264
2673 | 64.0935 | 0 | 42.9 | 139.3 | 0 | 32.0468 | 0 | 0 | 0 | 0 | 108.9 | 90.2633
2674 | 63.3209 | 0 | 42.9 | 107.8 | 0 | 31.6604 | 0 | 0 | 0 | 0 | 113.4 | 64.3789
2675 | 73.103 | 0 | 42.9 | 71.3 | 0 | 36.5515 | 0 | 0 | 0 | 0 | 72.9 | 70.4735
2676 | 84.0578 | 0 | 42.9 | 27.5 | 0 | 42.0289 | 0 | 0 | 0 | 0 | 29.1 | 94.2037
2677 | 88.7971 | 0 | 42.9 | 3.2 | 75.1 | 44.3986 | 0 | 0 | 0 | 0 | 405.4 | 97.6775
2678 | 89.2896 | 0 | 42.9 | 0 | 37.6 | 44.6448 | 0 | 0 | 0 | 0 | 292.4 | 96.5944
2679 | 88.9456 | 0 | 42.9 | 0 | 0 | 44.4728 | 0 | 0 | 0 | 0 | 0 | 85.2795
2680 | 87.8305 | 0 | 42.9 | 0 | 0 | 43.9152 | 0 | 0 | 0 | 0 | 0 | 153.224
2681 | 87.2643 | 0 | 42.9 | 0 | 0 | 43.6321 | 0 | 0 | 0 | 0 | 0 | 83.8519
2682 | 85.6155 | 0 | 42.9 | 0 | 37.6 | 42.8077 | 0 | 0 | 0 | 0 | 294.8 | 100.6666
2683 | 88.6682 | 0 | 42.9 | 0 | 75.1 | 44.3341 | 0 | 0 | 0 | 0 | 225 | 247.6454
2684 | 77.153 | 0 | 42.9 | 0 | 75.1 | 38.5765 | 0 | 0 | 0 | 0 | 204.9 | 299.6191
2685 | 63.3314 | 0 | 42.9 | 0 | 75.1 | 31.6657 | 0 | 0 | 0 | 0 | 274.1 | 250.5876
2686 | 60.9825 | 0 | 42.9 | 2.6 | 93.9 | 30.4913 | 0 | 0 | 0 | 0 | 303 | 176.487
2687 | 60.0819 | 0 | 0 | 0 | 0 | 30.0409 | 0 | 0 | 0 | 0 | 0 | 181.1371
2688 | 51.0972 | 0 | 0 | 0 | 0 | 25.5486 | 0 | 0 | 0 | 0 | 0 | 243.996
2689 | 41.3812 | 0 | 0 | 0 | 0 | 20.6906 | 0 | 0 | 0 | 0 | 0.1 | 92.4116
2690 | 41.9421 | 0 | 0 | 0 | 0 | 20.9711 | 0 | 0 | 0 | 0 | 5.3 | 54.9433
2691 | 42.129 | 0 | 0 | 0 | 0 | 21.0645 | 0 | 0 | 0 | 0 | 20.6 | 48.3999
2692 | 40.8456 | 0 | 0 | 1.9 | 0 | 20.4228 | 0 | 0 | 0 | 0 | 52.3 | 51.6151
2693 | 43.2106 | 0 | 0 | 6.8 | 0 | 21.6053 | 0 | 0 | 0 | 0 | 81.8 | 64.9551
2694 | 63.7356 | 0 | 0 | 10.3 | 0 | 31.8678 | 0 | 0 | 0 | 0 | 99.5 | 67.4849
2695 | 112.5688 | 0 | 42.9 | 161.7 | 56.3 | 56.2844 | 0 | 0 | 0 | 0 | 572.7 | 60.9332
2696 | 150.6347 | 0.7 | 43 | 161.5 | 37.6 | 75.3174 | 0 | 0 | 0 | 0 | 468.2 | 93.2489
2697 | 256.3949 | 2.1 | 43.2 | 129.7 | 0 | 128.1974 | 0 | 0 | 0 | 0 | 30.9 | 71.3951
2698 | 288.6813 | 3.5 | 43.4 | 106.9 | 0 | 144.3407 | 0 | 0 | 0 | 0 | 25.5 | 122.5893
2699 | 299.0786 | 3.5 | 43.4 | 78.7 | 0 | 149.5393 | 0 | 0 | 0 | 0 | 8.6 | 202.1288
2700 | 232.6346 | 2.8 | 43.3 | 48.1 | 0 | 116.3173 | 0 | 0 | 0 | 0 | 2.5 | 126.1286
2701 | 224.4725 | 1.4 | 43.1 | 17.7 | 75.1 | 112.2363 | 0 | 0 | 0 | 0 | 342.4 | 172.4084
2702 | 231.9987 | 2.1 | 43.2 | 2.1 | 37.6 | 115.9993 | 0 | 0 | 0 | 0 | 243.5 | 104.1303
2703 | 224.617 | 3.5 | 43.4 | 0 | 0 | 112.3085 | 0 | 0 | 0 | 0 | 0 | 61.164
2704 | 191.9899 | 2.8 | 43.3 | 0 | 0 | 95.9949 | 0 | 0 | 0 | 0 | 0 | 95.8721
2705 | 136.572 | 2.1 | 43.2 | 0 | 0 | 68.286 | 0 | 0 | 0 | 0 | 0 | 90.5044
2706 | 96.843 | 0.7 | 43 | 0.5 | 37.6 | 48.4215 | 0 | 0 | 0 | 0 | 265.8 | 159.0544
2707 | 74.7719 | 0 | 42.9 | 0 | 75.1 | 37.386 | 0 | 0 | 0 | 0 | 209.9 | 220.7863
2708 | 49.1763 | 0 | 42.9 | 0 | 75.1 | 24.5882 | 0 | 0 | 0 | 0 | 168 | 236.566
2709 | 43.5401 | 0 | 42.9 | 0 | 75.1 | 21.77 | 0 | 0 | 0 | 0 | 243.9 | 196.8572
2710 | 41.0821 | 0 | 42.9 | 2.8 | 93.9 | 20.541 | 0 | 0 | 0 | 0 | 293.1 | 254.3228
2711 | 43.766 | 0 | 0 | 0 | 0 | 21.883 | 0 | 0 | 0 | 0 | 0 | 211.1288
2712 | 41.7515 | 0 | 0 | 0 | 0 | 20.8758 | 0 | 0 | 0 | 0 | 0 | 306.2692
2713 | 44.9577 | 0 | 0 | 0 | 0 | 22.4788 | 0 | 0 | 0 | 0 | 2.3 | 81.3708
2714 | 42.4718 | 0 | 0 | 0 | 0 | 21.2359 | 0 | 0 | 0 | 0 | 23.3 | 56.9012
2715 | 43.122 | 0 | 0 | 1.7 | 0 | 21.561 | 0 | 0 | 0 | 0 | 69.3 | 53.7969
2716 | 42.5183 | 0 | 0 | 8 | 0 | 21.2591 | 0 | 0 | 0 | 0 | 106.4 | 45.8805
2717 | 42.2582 | 0 | 0 | 13.3 | 0 | 21.1291 | 0 | 0 | 0 | 0 | 138 | 57.362
2718 | 56.2671 | 0 | 0 | 20.8 | 0 | 28.1335 | 0 | 0 | 0 | 0 | 158.5 | 79.9522
2719 | 108.7326 | 0 | 42.9 | 192 | 56.3 | 54.3663 | 0 | 0 | 0 | 0 | 641.1 | 61.6257
2720 | 173.4751 | 0.7 | 43 | 202.3 | 37.6 | 86.7375 | 0 | 0 | 0 | 17.8 | 549.3 | 53.5672
2721 | 234.805 | 2.1 | 43.2 | 175.3 | 0 | 117.4025 | 0 | 0 | 0 | 18 | 94.7 | 71.0506
2722 | 266.5315 | 3.5 | 43.4 | 161.9 | 0 | 133.2657 | 0 | 0 | 0 | 35.9 | 111.1 | 89.3053
2723 | 260.2965 | 3.5 | 43.4 | 139.2 | 0 | 130.1482 | 0 | 0 | 0 | 32.1 | 89.8 | 132.1944
2724 | 227.1109 | 2.8 | 43.3 | 109.3 | 0 | 113.5554 | 0 | 0 | 0 | 16.5 | 66.6 | 101.1406
2725 | 223.0221 | 1.4 | 43.1 | 82.2 | 75.1 | 111.511 | 0 | 0 | 0 | 0 | 467.7 | 111.1493
2726 | 219.9557 | 2.1 | 43.2 | 68.8 | 37.6 | 109.9779 | 0 | 0 | 0 | 0 | 367.7 | 170.9779
2727 | 208.9789 | 3.5 | 43.4 | 63.5 | 0 | 104.4894 | 0 | 0 | 0 | 19 | 0.2 | 149.6831
2728 | 177.8183 | 2.8 | 43.3 | 58.9 | 0 | 88.9092 | 0 | 0 | 0 | 23.1 | 2.7 | 156.502
2729 | 137.4664 | 2.1 | 43.2 | 55.5 | 0 | 68.7332 | 0 | 0 | 0 | 14.3 | 7.6 | 137.7026
2730 | 115.8342 | 0.7 | 43 | 63 | 37.6 | 57.9171 | 0 | 0 | 0 | 0.4 | 450 | 150.1314
2731 | 89.1064 | 0 | 42.9 | 23.7 | 75.1 | 44.5532 | 0 | 0 | 0 | 0 | 373.8 | 193.2836
2732 | 60.8214 | 0 | 42.9 | 6.8 | 75.1 | 30.4107 | 0 | 0 | 0 | 0 | 325.5 | 225.3246
2733 | 41.9052 | 0 | 42.9 | 20.7 | 75.1 | 20.9526 | 0 | 0 | 0 | 0 | 384.5 | 191.2028
2734 | 41.127 | 0 | 42.9 | 40.5 | 93.9 | 20.5635 | 0 | 0 | 0 | 0 | 419.8 | 134.3193
2735 | 42.9608 | 0 | 0 | 0 | 0 | 21.4804 | 0 | 0 | 0 | 0 | 13.1 | 211.9446
2736 | 40.2744 | 0 | 0 | 0.2 | 0 | 20.1372 | 0 | 0 | 0 | 0 | 75.6 | 100.9032
2737 | 42.8195 | 0 | 0 | 3.2 | 0 | 21.4098 | 0 | 0 | 0 | 0 | 101.2 | 64.4942
2738 | 40.9178 | 0 | 0 | 7.5 | 0 | 20.4589 | 0 | 0 | 0 | 0 | 118.8 | 56.4365
2739 | 41.9344 | 0 | 0 | 12.2 | 0 | 20.9672 | 0 | 0 | 0 | 0 | 143 | 54.9435
2740 | 41.313 | 0 | 0 | 19.4 | 0 | 20.6565 | 0 | 0 | 0 | 0 | 164.8 | 49.664
2741 | 45.3066 | 0 | 0 | 28.2 | 0 | 22.6533 | 0 | 0 | 0 | 0 | 185.3 | 59.093
2742 | 65.3661 | 0 | 0 | 36.3 | 0 | 32.683 | 0 | 0 | 0 | 0 | 195.3 | 101.5016
2743 | 99.3739 | 0 | 42.9 | 191.5 | 56.3 | 49.6869 | 0 | 0 | 0 | 0 | 665.6 | 93.3653
2744 | 157.277 | 0.7 | 43 | 186.3 | 37.6 | 78.6385 | 0 | 0 | 0 | 38.1 | 554.7 | 46.5627
2745 | 239.9987 | 2.1 | 43.2 | 149.3 | 0 | 119.9994 | 0 | 0 | 0 | 32.8 | 79.6 | 106.6699
2746 | 309.3739 | 3.5 | 43.4 | 121.3 | 0 | 154.687 | 0 | 0 | 0 | 44.6 | 76.1 | 66.103
2747 | 310.3133 | 3.5 | 43.4 | 88.9 | 0 | 155.1567 | 0 | 0 | 0 | 37.6 | 42 | 84.8039
2748 | 297.3617 | 2.8 | 43.3 | 50.7 | 0 | 148.6808 | 0 | 0 | 0 | 21.2 | 10.7 | 172.8561
2749 | 280.7201 | 1.4 | 43.1 | 10.9 | 75.1 | 140.36 | 0 | 0 | 0 | 0.4 | 364 | 128.3522
2750 | 256.6391 | 2.1 | 43.2 | 0 | 37.6 | 128.3195 | 0 | 0 | 0 | 0 | 243.9 | 102.5792
2751 | 252.6566 | 3.5 | 43.4 | 0 | 0 | 126.3283 | 0 | 0 | 0 | 0.3 | 0 | 144.0339
2752 | 214.242 | 2.8 | 43.3 | 0 | 0 | 107.121 | 0 | 0 | 0 | 0 | 0 | 198.1685
2753 | 160.8417 | 2.1 | 43.2 | 0 | 0 | 80.4209 | 0 | 0 | 0 | 0 | 0 | 132.1624
2754 | 104.8843 | 0.7 | 43 | 0 | 37.6 | 52.4421 | 0 | 0 | 0 | 0 | 209.5 | 184.4363
2755 | 80.8129 | 0 | 42.9 | 0 | 75.1 | 40.4065 | 0 | 0 | 0 | 0 | 155.2 | 182.2182
2756 | 53.6209 | 0 | 42.9 | 0 | 75.1 | 26.8105 | 0 | 0 | 0 | 0 | 126.9 | 291.3255
2757 | 46.1955 | 0 | 42.9 | 0 | 75.1 | 23.0977 | 0 | 0 | 0 | 0 | 197.2 | 166.1398
2758 | 43.4654 | 0 | 42.9 | 0 | 93.9 | 21.7327 | 0 | 0 | 0 | 0 | 226.9 | 151.8353
2759 | 43.7831 | 0 | 0 | 0 | 0 | 21.8915 | 0 | 0 | 0 | 0 | 0 | 113.6822
2760 | 43.4068 | 0 | 0 | 0 | 0 | 21.7034 | 0 | 0 | 0 | 0 | 0 | 70.4718
2761 | 42.6512 | 0 | 0 | 0 | 0 | 21.3256 | 0 | 0 | 0 | 0 | 0 | 74.9754
2762 | 43.1403 | 0 | 0 | 0 | 0 | 21.5701 | 0 | 0 | 0 | 0 | 0 | 57.4773
2763 | 41.9353 | 0 | 0 | 0 | 0 | 20.9677 | 0 | 0 | 0 | 0 | 0.3 | 49.5481
2764 | 43.6854 | 0 | 0 | 0 | 0 | 21.8427 | 0 | 0 | 0 | 0 | 4.1 | 46.3353
2765 | 44.6713 | 0 | 0 | 0 | 0 | 22.3356 | 0 | 0 | 0 | 0 | 10.9 | 53.9111
2766 | 58.178 | 0 | 0 | 0 | 0 | 29.089 | 0 | 0 | 0 | 0 | 24.4 | 93.6023
2767 | 84.2004 | 0 | 42.9 | 123 | 56.3 | 42.1002 | 0 | 0 | 0 | 0 | 510.1 | 77.9268
2768 | 157.4769 | 0.7 | 43 | 153 | 37.6 | 78.7384 | 0 | 0 | 0 | 31.9 | 436.2 | 70.0134
2769 | 214.2597 | 2.1 | 43.2 | 144.5 | 0 | 107.1298 | 0 | 0 | 0 | 19.6 | 44.6 | 111.1474
2770 | 249.6683 | 3.5 | 43.4 | 149.2 | 0 | 124.8341 | 0 | 0 | 0 | 24.9 | 79.6 | 137.5347
2771 | 237.3278 | 3.5 | 43.4 | 129.1 | 0 | 118.6639 | 0 | 0 | 0 | 8.7 | 64.5 | 131.3209
2772 | 225.6896 | 2.8 | 43.3 | 105.6 | 0 | 112.8448 | 0 | 0 | 0 | 0 | 47.3 | 153.5437
2773 | 228.1219 | 1.4 | 43.1 | 77.7 | 75.1 | 114.0609 | 0 | 0 | 0 | 0 | 435 | 106.0616
2774 | 210.3813 | 2.1 | 43.2 | 46.3 | 37.6 | 105.1906 | 0 | 0 | 0 | 0 | 317.4 | 133.3643
2775 | 187.1235 | 3.5 | 43.4 | 23.6 | 0 | 93.5617 | 0 | 0 | 0 | 0 | 0 | 162.4734
2776 | 151.6023 | 2.8 | 43.3 | 8.6 | 0 | 75.8012 | 0 | 0 | 0 | 0 | 0 | 112.602
2777 | 123.8205 | 2.1 | 43.2 | 5.6 | 0 | 61.9103 | 0 | 0 | 0 | 0 | 0 | 108.4866
2778 | 103.5783 | 0.7 | 43 | 10.9 | 37.6 | 51.7891 | 0 | 0 | 0 | 0 | 321.4 | 79.834
2779 | 83.0626 | 0 | 42.9 | 0 | 75.1 | 41.5313 | 0 | 0 | 0 | 0 | 249.9 | 159.5113
2780 | 53.9473 | 0 | 42.9 | 0 | 75.1 | 26.9736 | 0 | 0 | 0 | 0 | 189.5 | 248.17
2781 | 41.8941 | 0 | 42.9 | 0 | 75.1 | 20.947 | 0 | 0 | 0 | 0 | 259.8 | 443.2171
2782 | 39.0493 | 0 | 42.9 | 5.8 | 93.9 | 19.5247 | 0 | 0 | 0 | 0 | 301.3 | 192.6366
2783 | 43.1428 | 0 | 0 | 0 | 0 | 21.5714 | 0 | 0 | 0 | 0 | 0 | 123.1652
2784 | 44.2142 | 0 | 0 | 0 | 0 | 22.1071 | 0 | 0 | 0 | 0 | 1.4 | 98.9896
2785 | 43.1992 | 0 | 0 | 0 | 0 | 21.5996 | 0 | 0 | 0 | 0 | 20.4 | 77.6864
2786 | 42.7368 | 0 | 0 | 2.3 | 0 | 21.3684 | 0 | 0 | 0 | 0 | 78.8 | 64.264
2787 | 41.5098 | 0 | 0 | 10.5 | 0 | 20.7549 | 0 | 0 | 0 | 0 | 129.1 | 58.0565
2788 | 43.5026 | 0 | 0 | 19.5 | 0 | 21.7513 | 0 | 0 | 0 | 0 | 170.9 | 58.7484
2789 | 43.7062 | 0 | 0 | 34 | 0 | 21.8531 | 0 | 0 | 0 | 0 | 209.2 | 64.6088
2790 | 57.4426 | 0 | 0 | 43.7 | 0 | 28.7213 | 0 | 0 | 0 | 0 | 222.2 | 72.7807
2791 | 86.6131 | 0 | 42.9 | 188.4 | 56.3 | 43.3066 | 0 | 0 | 0 | 0 | 643.7 | 68.9784
2792 | 145.7376 | 0.7 | 43 | 161.8 | 37.6 | 72.8688 | 0 | 0 | 0 | 0 | 482.9 | 78.4028
2793 | 241.7516 | 2.1 | 43.2 | 95.9 | 0 | 120.8758 | 0 | 0 | 0 | 0 | 2.4 | 96.7097
2794 | 267.0429 | 3.5 | 43.4 | 37.3 | 0 | 133.5214 | 0 | 0 | 0 | 0 | 0 | 122.8609
2795 | 232.9852 | 3.5 | 43.4 | 0.6 | 0 | 116.4926 | 0 | 0 | 0 | 0 | 0 | 125.7148
2796 | 226.3231 | 2.8 | 43.3 | 0 | 0 | 113.1615 | 0 | 0 | 0 | 0 | 0 | 269.5299
2797 | 215.5778 | 1.4 | 43.1 | 0 | 75.1 | 107.7889 | 0 | 0 | 0 | 0 | 118.1 | 179.2915
2798 | 221.8363 | 2.1 | 43.2 | 0 | 37.6 | 110.9182 | 0 | 0 | 0 | 0 | 53.7 | 201.8354
2799 | 228.6714 | 3.5 | 43.4 | 0 | 0 | 114.3357 | 0 | 0 | 0 | 0 | 0 | 152.0223
2800 | 210.4857 | 2.8 | 43.3 | 0 | 0 | 105.2429 | 0 | 0 | 0 | 0 | 0 | 137.8779
2801 | 146.6324 | 2.1 | 43.2 | 0 | 0 | 73.3162 | 0 | 0 | 0 | 0 | 0 | 204.6937
2802 | 90.9096 | 0.7 | 43 | 0 | 37.6 | 45.4548 | 0 | 0 | 0 | 0 | 0 | 239.2063
2803 | 63.8127 | 0 | 42.9 | 0 | 75.1 | 31.9064 | 0 | 0 | 0 | 0 | 0 | 204.9151
2804 | 46.6238 | 0 | 42.9 | 0 | 75.1 | 23.3119 | 0 | 0 | 0 | 0 | 0 | 227.8314
2805 | 43.8209 | 0 | 42.9 | 0 | 75.1 | 21.9104 | 0 | 0 | 0 | 0 | 0.1 | 123.2826
2806 | 42.1008 | 0 | 42.9 | 0 | 93.9 | 21.0504 | 0 | 0 | 0 | 0 | 30.6 | 124.2306
2807 | 43.8807 | 0 | 0 | 0 | 0 | 21.9403 | 0 | 0 | 0 | 0 | 0 | 112.1191
2808 | 41.4255 | 0 | 0 | 0 | 0 | 20.7127 | 0 | 0 | 0 | 0 | 0 | 98.0385
2809 | 42.7083 | 0 | 0 | 0 | 0 | 21.3541 | 0 | 0 | 0 | 0 | 0 | 70.5908
2810 | 42.8799 | 0 | 0 | 0 | 0 | 21.44 | 0 | 0 | 0 | 0 | 0 | 55.9783
2811 | 42.4454 | 0 | 0 | 0 | 0 | 21.2227 | 0 | 0 | 0 | 0 | 0 | 48.1689
2812 | 44.282 | 0 | 0 | 0 | 0 | 22.141 | 0 | 0 | 0 | 0 | 0 | 47.8249
2813 | 41.6995 | 0 | 0 | 0 | 0 | 20.8497 | 0 | 0 | 0 | 0 | 0.9 | 63.0037
2814 | 49.4977 | 0 | 0 | 0 | 0 | 24.7489 | 0 | 0 | 0 | 0 | 5.5 | 61.6247
2815 | 62.3803 | 0 | 42.9 | 88.5 | 56.3 | 31.1901 | 0 | 0 | 0 | 0 | 470.4 | 74.0476
2816 | 65.1194 | 0 | 42.9 | 76.4 | 37.6 | 32.5597 | 0 | 0 | 0 | 0 | 346.6 | 46.9054
2817 | 60.5809 | 0 | 42.9 | 24.8 | 0 | 30.2904 | 0 | 0 | 0 | 0 | 0 | 55.2884
2818 | 55.8676 | 0 | 42.9 | 3.1 | 0 | 27.9338 | 0 | 0 | 0 | 0 | 0 | 52.0776
2819 | 56.5224 | 0 | 42.9 | 0 | 0 | 28.2612 | 0 | 0 | 0 | 0 | 0 | 66.5622
2820 | 53.6873 | 0 | 42.9 | 0 | 0 | 26.8436 | 0 | 0 | 0 | 0 | 0 | 74.9724
2821 | 52.7395 | 0 | 42.9 | 0 | 75.1 | 26.3698 | 0 | 0 | 0 | 0 | 108.5 | 123.0235
2822 | 55.0072 | 0 | 42.9 | 0 | 37.6 | 27.5036 | 0 | 0 | 0 | 0 | 56.9 | 113.0863
2823 | 63.0553 | 0 | 42.9 | 0 | 0 | 31.5276 | 0 | 0 | 0 | 0 | 0 | 78.7693
2824 | 65.5821 | 0 | 42.9 | 0 | 0 | 32.791 | 0 | 0 | 0 | 0 | 0 | 123.4058
2825 | 65.5973 | 0 | 42.9 | 0 | 0 | 32.7986 | 0 | 0 | 0 | 0 | 0 | 123.4732
2826 | 61.6346 | 0 | 42.9 | 0 | 37.6 | 30.8173 | 0 | 0 | 0 | 0 | 0 | 257.0797
2827 | 49.8603 | 0 | 42.9 | 0 | 75.1 | 24.9302 | 0 | 0 | 0 | 0 | 0 | 260.1833
2828 | 45.58 | 0 | 42.9 | 0 | 75.1 | 22.79 | 0 | 0 | 0 | 0 | 0 | 156.9605
2829 | 41.277 | 0 | 42.9 | 0 | 75.1 | 20.6385 | 0 | 0 | 0 | 0 | 7.4 | 260.0534
2830 | 41.3294 | 0 | 42.9 | 0 | 93.9 | 20.6647 | 0 | 0 | 0 | 0 | 48.4 | 133.5146
2831 | 40.2369 | 0 | 0 | 0 | 0 | 20.1185 | 0 | 0 | 0 | 0 | 0 | 151.7039
2832 | 43.7998 | 0 | 0 | 0 | 0 | 21.8999 | 0 | 0 | 0 | 0 | 0 | 98.8741
2833 | 42.1842 | 0 | 0 | 0 | 0 | 21.0921 | 0 | 0 | 0 | 0 | 0 | 53.6825
2834 | 43.3693 | 0 | 0 | 0 | 0 | 21.6847 | 0 | 0 | 0 | 0 | 0 | 44.7508
2835 | 42.535 | 0 | 0 | 0 | 0 | 21.2675 | 0 | 0 | 0 | 0 | 0 | 49.4336
2836 | 41.9012 | 0 | 0 | 0 | 0 | 20.9506 | 0 | 0 | 0 | 0 | 0 | 48.1686
2837 | 43.1765 | 0 | 0 | 0 | 0 | 21.5883 | 0 | 0 | 0 | 0 | 2.5 | 53.7972
2838 | 46.2504 | 0 | 0 | 0 | 0 | 23.1252 | 0 | 0 | 0 | 0 | 9.5 | 90.267
2839 | 60.0004 | 0 | 42.9 | 117.2 | 56.3 | 30.0002 | 0 | 0 | 0 | 0 | 505.4 | 87.053
2840 | 72.8696 | 0 | 42.9 | 109.3 | 37.6 | 36.4348 | 0 | 0 | 0 | 0 | 417.7 | 88.3626
2841 | 65.1609 | 0 | 42.9 | 87 | 0 | 32.5804 | 0 | 0 | 0 | 0 | 6.4 | 97.3139
2842 | 57.8709 | 0 | 42.9 | 72 | 0 | 28.9354 | 0 | 0 | 0 | 0 | 9.3 | 83.1462
2843 | 58.3082 | 0 | 42.9 | 61.8 | 0 | 29.1541 | 0 | 0 | 0 | 0 | 11.5 | 94.0824
2844 | 67.128 | 0 | 42.9 | 43.1 | 0 | 33.564 | 0 | 0 | 0 | 0 | 8.6 | 85.8673
2845 | 72.3037 | 0 | 42.9 | 32.7 | 75.1 | 36.1518 | 0 | 0 | 0 | 0 | 418.6 | 64.3793
2846 | 81.835 | 0 | 42.9 | 23.3 | 37.6 | 40.9175 | 0 | 0 | 0 | 0 | 326.1 | 86.1011
2847 | 82.1484 | 0 | 42.9 | 18.6 | 0 | 41.0742 | 0 | 0 | 0 | 0 | 0 | 92.2887
2848 | 85.8287 | 0 | 42.9 | 16.4 | 0 | 42.9143 | 0 | 0 | 0 | 0 | 0.1 | 102.0981
2849 | 82.8194 | 0 | 42.9 | 17.3 | 0 | 41.4097 | 0 | 0 | 0 | 0 | 1.8 | 209.9343
2850 | 78.2967 | 0 | 42.9 | 26.4 | 37.6 | 39.1483 | 0 | 0 | 0 | 0 | 399.5 | 171.0152
2851 | 74.0901 | 0 | 42.9 | 32.8 | 75.1 | 37.045 | 0 | 0 | 0 | 0 | 344.7 | 139.9204
2852 | 58.8819 | 0 | 42.9 | 14.1 | 75.1 | 29.4409 | 0 | 0 | 0 | 0 | 312.2 | 246.5731
2853 | 50.5158 | 0 | 42.9 | 31.4 | 75.1 | 25.2579 | 0 | 0 | 0 | 0 | 383.5 | 168.4207
2854 | 43.3941 | 0 | 42.9 | 53.7 | 93.9 | 21.6971 | 0 | 0 | 0 | 0 | 436.5 | 150.4449
2855 | 43.3002 | 0 | 0 | 0.3 | 0 | 21.6501 | 0 | 0 | 0 | 0 | 14.1 | 129.5738
2856 | 40.907 | 0 | 0 | 8.5 | 0 | 20.4535 | 0 | 0 | 0 | 0 | 71.9 | 93.2415
2857 | 44.1358 | 0 | 0 | 18.2 | 0 | 22.0679 | 0 | 0 | 0 | 0 | 131.5 | 57.8235
2858 | 42.9438 | 0 | 0 | 34.6 | 0 | 21.4719 | 0 | 0 | 0 | 0 | 188.8 | 48.8584
2859 | 42.0001 | 0 | 0 | 52.5 | 0 | 21 | 0 | 0 | 0 | 0 | 241 | 47.0208
2860 | 41.8023 | 0 | 0 | 74.3 | 0 | 20.9012 | 0 | 0 | 0 | 0 | 286.9 | 50.5804
2861 | 42.2049 | 0 | 0 | 93.8 | 0 | 21.1025 | 0 | 0 | 0 | 0 | 328.9 | 54.1406
2862 | 63.4201 | 0 | 0 | 104.8 | 0 | 31.71 | 0 | 0 | 0 | 0 | 351.9 | 81.9628
2863 | 92.8441 | 0 | 42.9 | 259.4 | 56.3 | 46.4221 | 0 | 0 | 0 | 0 | 813.3 | 77.6873
2864 | 136.1843 | 0.7 | 43 | 253.1 | 37.6 | 68.0921 | 0 | 0 | 0 | 52.7 | 667.3 | 106.6725
2865 | 222.2944 | 2.1 | 43.2 | 205.4 | 0 | 111.1472 | 0 | 0 | 0 | 54.2 | 138.3 | 123.1477
2866 | 221.6256 | 3.5 | 43.4 | 172.3 | 0 | 110.8128 | 0 | 0 | 0 | 78.8 | 132.9 | 141.8357
2867 | 223.4842 | 3.5 | 43.4 | 130.5 | 0 | 111.7421 | 0 | 0 | 0 | 73.2 | 98.4 | 121.128
2868 | 213.7195 | 2.8 | 43.3 | 85.4 | 0 | 106.8597 | 0 | 0 | 0 | 45.2 | 69.1 | 176.0872
2869 | 189.8753 | 1.4 | 43.1 | 43.6 | 75.1 | 94.9376 | 0 | 0 | 0 | 7.9 | 484.5 | 175.5529
2870 | 178.7016 | 2.1 | 43.2 | 21 | 37.6 | 89.3508 | 0 | 0 | 0 | 3.9 | 351.8 | 201.2751
2871 | 183.0452 | 3.5 | 43.4 | 13.2 | 0 | 91.5226 | 0 | 0 | 0 | 23.5 | 0 | 104.0129
2872 | 156.0748 | 2.8 | 43.3 | 1.2 | 0 | 78.0374 | 0 | 0 | 0 | 21.3 | 0 | 180.1605
2873 | 111.843 | 2.1 | 43.2 | 0 | 0 | 55.9215 | 0 | 0 | 0 | 8.9 | 0 | 135.8479
2874 | 83.1953 | 0.7 | 43 | 0 | 37.6 | 41.5976 | 0 | 0 | 0 | 0 | 351.2 | 195.0873
2875 | 57.6093 | 0 | 42.9 | 0 | 75.1 | 28.8047 | 0 | 0 | 0 | 0 | 329.3 | 263.0445
2876 | 47.5793 | 0 | 42.9 | 0 | 75.1 | 23.7897 | 0 | 0 | 0 | 0 | 320.9 | 316.8036
2877 | 40.1455 | 0 | 42.9 | 0.5 | 75.1 | 20.0728 | 0 | 0 | 0 | 0 | 385.7 | 224.6873
2878 | 43.6737 | 0 | 42.9 | 8.5 | 93.9 | 21.8368 | 0 | 0 | 0 | 0 | 414.8 | 155.2275
2879 | 43.0848 | 0 | 0 | 0 | 0 | 21.5424 | 0 | 0 | 0 | 0 | 0 | 123.1791
2880 | 42.2226 | 0 | 0 | 0 | 0 | 21.1113 | 0 | 0 | 0 | 0 | 0 | 105.7001
2881 | 40.7523 | 0 | 0 | 0 | 0 | 20.3762 | 0 | 0 | 0 | 0 | 0 | 98.8726
2882 | 44.3586 | 0 | 0 | 0 | 0 | 22.1793 | 0 | 0 | 0 | 0 | 0.7 | 94.5588
2883 | 42.2713 | 0 | 0 | 0 | 0 | 21.1356 | 0 | 0 | 0 | 0 | 3.6 | 92.7706
2884 | 41.2352 | 0 | 0 | 0 | 0 | 20.6176 | 0 | 0 | 0 | 0 | 5.7 | 93.7234
2885 | 41.2851 | 0 | 0 | 0 | 0 | 20.6425 | 0 | 0 | 0 | 0 | 8.6 | 95.6303
2886 | 48.8621 | 0 | 0 | 0 | 0 | 24.431 | 0 | 0 | 0 | 0 | 11.4 | 90.98
2887 | 68.9398 | 0 | 42.9 | 117.9 | 56.3 | 34.4699 | 0 | 0 | 0 | 0 | 489.9 | 92.5339
2888 | 64.5274 | 0.7 | 43 | 144.7 | 37.6 | 32.2637 | 0 | 0 | 0 | 2.8 | 415.6 | 78.5255
2889 | 56.5949 | 2.1 | 43.2 | 106.1 | 0 | 28.2975 | 0 | 0 | 0 | 0 | 2.9 | 81.4924
2890 | 51.4831 | 3.5 | 43.4 | 72.5 | 0 | 25.7415 | 0 | 0 | 0 | 0 | 0.8 | 100.3075
2891 | 52.7398 | 3.5 | 43.4 | 44.1 | 0 | 26.3699 | 0 | 0 | 0 | 0 | 0 | 119.2428
2892 | 51.3678 | 2.8 | 43.3 | 17.6 | 0 | 25.6839 | 0 | 0 | 0 | 0 | 0 | 112.9669
2893 | 54.2098 | 1.4 | 43.1 | 3.5 | 75.1 | 27.1049 | 0 | 0 | 0 | 0 | 251.9 | 187.2937
2894 | 51.6591 | 2.1 | 43.2 | 0 | 37.6 | 25.8296 | 0 | 0 | 0 | 0 | 178.5 | 117.6445
2895 | 52.4724 | 3.5 | 43.4 | 0 | 0 | 26.2362 | 0 | 0 | 0 | 0 | 0 | 224.438
2896 | 56.1335 | 2.8 | 43.3 | 0 | 0 | 28.0667 | 0 | 0 | 0 | 0 | 0 | 118.3067
2897 | 51.7298 | 2.1 | 43.2 | 0 | 0 | 25.8649 | 0 | 0 | 0 | 0 | 0 | 109.2088
2898 | 54.062 | 0.7 | 43 | 0 | 37.6 | 27.031 | 0 | 0 | 0 | 0 | 173.9 | 206.9828
2899 | 51.087 | 0 | 42.9 | 0 | 75.1 | 25.5435 | 0 | 0 | 0 | 0 | 107.5 | 173.1397
2900 | 45.0026 | 0 | 42.9 | 0 | 75.1 | 22.5013 | 0 | 0 | 0 | 0 | 62.9 | 125.1733
2901 | 41.2296 | 0 | 42.9 | 0 | 75.1 | 20.6148 | 0 | 0 | 0 | 0 | 125.7 | 123.6418
2902 | 42.4879 | 0 | 42.9 | 0 | 93.9 | 21.2439 | 0 | 0 | 0 | 0 | 129.3 | 158.9588
2903 | 39.5985 | 0 | 0 | 0 | 0 | 19.7992 | 0 | 0 | 0 | 0 | 0 | 157.5741
2904 | 42.2691 | 0 | 0 | 0 | 0 | 21.1345 | 0 | 0 | 0 | 0 | 0 | 119.2058
2905 | 41.8959 | 0 | 0 | 0 | 0 | 20.948 | 0 | 0 | 0 | 0 | 0 | 55.7496
2906 | 41.074 | 0 | 0 | 0 | 0 | 20.537 | 0 | 0 | 0 | 0 | 0 | 61.3941
2907 | 42.9187 | 0 | 0 | 0 | 0 | 21.4593 | 0 | 0 | 0 | 0 | 0 | 57.3629
2908 | 40.2664 | 0 | 0 | 0 | 0 | 20.1332 | 0 | 0 | 0 | 0 | 0 | 47.7091
2909 | 43.6191 | 0 | 0 | 0 | 0 | 21.8096 | 0 | 0 | 0 | 0 | 0 | 53.2223
2910 | 61.8791 | 0 | 0 | 0 | 0 | 30.9396 | 0 | 0 | 0 | 0 | 0 | 60.2425
2911 | 112.1603 | 0 | 42.9 | 49.3 | 56.3 | 56.0802 | 0 | 0 | 0 | 0 | 345.1 | 64.7256
2912 | 203.2134 | 0.7 | 43 | 69 | 37.6 | 101.6067 | 0 | 0 | 0 | 0 | 263.3 | 75.0898
2913 | 353.3994 | 2.1 | 43.2 | 36.3 | 0 | 176.6997 | 0 | 0 | 0 | 0 | 0 | 63.5784
2914 | 360.1972 | 3.5 | 43.4 | 9.6 | 0 | 180.0986 | 0 | 0 | 0 | 0 | 0 | 204.7814
2915 | 324.1083 | 3.5 | 43.4 | 0.2 | 0 | 162.0541 | 0 | 0 | 0 | 0 | 0 | 285.0632
2916 | 296.051 | 2.8 | 43.3 | 0 | 0 | 148.0255 | 0 | 0 | 0 | 0 | 0 | 71.3947
2917 | 292.913 | 1.4 | 43.1 | 0 | 75.1 | 146.4565 | 0 | 0 | 0 | 0 | 93.7 | 85.2761
2918 | 284.7955 | 2.1 | 43.2 | 0 | 37.6 | 142.3978 | 0 | 0 | 0 | 0 | 70.3 | 72.4351
2919 | 235.7624 | 3.5 | 43.4 | 0 | 0 | 117.8812 | 0 | 0 | 0 | 0 | 0 | 77.8075
2920 | 199.9319 | 2.8 | 43.3 | 0 | 0 | 99.966 | 0 | 0 | 0 | 0 | 0 | 85.0419
2921 | 154.8965 | 2.1 | 43.2 | 0 | 0 | 77.4482 | 0 | 0 | 0 | 0 | 0 | 74.0463
2922 | 129.9846 | 0.7 | 43 | 0 | 37.6 | 64.9923 | 0 | 0 | 0 | 0 | 48 | 215.0739
2923 | 108.3037 | 0 | 42.9 | 0 | 75.1 | 54.1518 | 0 | 0 | 0 | 0 | 17.7 | 159.88
2924 | 66.4412 | 0 | 42.9 | 0 | 75.1 | 33.2206 | 0 | 0 | 0 | 0 | 1.7 | 263.4698
2925 | 44.7953 | 0 | 42.9 | 0 | 75.1 | 22.3976 | 0 | 0 | 0 | 0 | 34.2 | 231.0187
2926 | 40.6476 | 0 | 42.9 | 0 | 93.9 | 20.3238 | 0 | 0 | 0 | 0 | 60.9 | 278.5594
2927 | 43.1053 | 0 | 0 | 0 | 0 | 21.5526 | 0 | 0 | 0 | 0 | 0 | 168.9599
2928 | 41.5169 | 0 | 0 | 0 | 0 | 20.7585 | 0 | 0 | 0 | 0 | 0 | 77.3279
2929 | 42.4299 | 0 | 0 | 0 | 0 | 21.215 | 0 | 0 | 0 | 0 | 0 | 56.8994
2930 | 44.3552 | 0 | 0 | 0 | 0 | 22.1776 | 0 | 0 | 0 | 0 | 0 | 50.0083
2931 | 42.3909 | 0 | 0 | 0 | 0 | 21.1954 | 0 | 0 | 0 | 0 | 0 | 48.1684
2932 | 40.5769 | 0 | 0 | 0 | 0 | 20.2885 | 0 | 0 | 0 | 0 | 0 | 49.7776
2933 | 41.4717 | 0 | 0 | 0 | 0 | 20.7358 | 0 | 0 | 0 | 0 | 0 | 51.9614
2934 | 55.7513 | 0 | 0 | 0 | 0 | 27.8757 | 0 | 0 | 0 | 0 | 0 | 57.0147
2935 | 91.7671 | 0 | 42.9 | 10.9 | 56.3 | 45.8836 | 0 | 0 | 0 | 0 | 214.2 | 62.201
2936 | 164.5642 | 0.7 | 43 | 23.3 | 37.6 | 82.2821 | 0 | 0 | 0 | 0 | 168.5 | 92.409
2937 | 262.566 | 2.1 | 43.2 | 8.8 | 0 | 131.283 | 0 | 0 | 0 | 0 | 0 | 58.6344
2938 | 319.6956 | 3.5 | 43.4 | 1.5 | 0 | 159.8478 | 0 | 0 | 0 | 0 | 0 | 75.7954
2939 | 287.419 | 3.5 | 43.4 | 0 | 0 | 143.7095 | 0 | 0 | 0 | 0 | 0 | 233.564
2940 | 258.1155 | 2.8 | 43.3 | 0 | 0 | 129.0578 | 0 | 0 | 0 | 0 | 0 | 160.1187
2941 | 241.8545 | 1.4 | 43.1 | 0 | 75.1 | 120.9273 | 0 | 0 | 0 | 0 | 24.2 | 97.1949
2942 | 235.6781 | 2.1 | 43.2 | 0 | 37.6 | 117.839 | 0 | 0 | 0 | 0 | 17.5 | 92.5293
2943 | 202.3844 | 3.5 | 43.4 | 0 | 0 | 101.1922 | 0 | 0 | 0 | 0 | 0 | 96.7126
2944 | 175.744 | 2.8 | 43.3 | 0 | 0 | 87.872 | 0 | 0 | 0 | 0 | 0 | 95.1562
2945 | 170.6446 | 2.1 | 43.2 | 0 | 0 | 85.3223 | 0 | 0 | 0 | 0 | 0 | 105.1046
2946 | 130.4169 | 0.7 | 43 | 0 | 37.6 | 65.2085 | 0 | 0 | 0 | 0 | 9.8 | 122.3631
2947 | 85.0288 | 0 | 42.9 | 0 | 75.1 | 42.5144 | 0 | 0 | 0 | 0 | 1.6 | 149.0567
2948 | 57.4528 | 0 | 42.9 | 0 | 75.1 | 28.7264 | 0 | 0 | 0 | 0 | 0 | 143.851
2949 | 41.7311 | 0 | 42.9 | 0 | 75.1 | 20.8655 | 0 | 0 | 0 | 0 | 4.9 | 204.1373
2950 | 41.4899 | 0 | 42.9 | 0 | 93.9 | 20.745 | 0 | 0 | 0 | 0 | 10.1 | 168.619
2951 | 41.7069 | 0 | 0 | 0 | 0 | 20.8534 | 0 | 0 | 0 | 0 | 0 | 89.5467
2952 | 41.568 | 0 | 0 | 0 | 0 | 20.784 | 0 | 0 | 0 | 0 | 0 | 65.985
2953 | 40.4278 | 0 | 0 | 0 | 0 | 20.2139 | 0 | 0 | 0 | 0 | 0 | 52.0755
2954 | 43.5432 | 0 | 0 | 0 | 0 | 21.7716 | 0 | 0 | 0 | 0 | 0 | 47.4796
2955 | 40.2713 | 0 | 0 | 0 | 0 | 20.1357 | 0 | 0 | 0 | 0 | 0 | 47.1354
2956 | 44.1351 | 0 | 0 | 0 | 0 | 22.0676 | 0 | 0 | 0 | 0 | 0 | 49.0894
2957 | 43.6854 | 0 | 0 | 0 | 0 | 21.8427 | 0 | 0 | 0 | 0 | 0 | 66.2181
2958 | 54.5755 | 0 | 0 | 0 | 0 | 27.2877 | 0 | 0 | 0 | 0 | 0 | 67.5993
2959 | 99.505 | 0 | 42.9 | 7.8 | 56.3 | 49.7525 | 0 | 0 | 0 | 0 | 180.6 | 73.1251
2960 | 180.0445 | 0.7 | 43 | 18.3 | 37.6 | 90.0223 | 0 | 0 | 0 | 0 | 151.4 | 111.1455
2961 | 278.9709 | 2.1 | 43.2 | 7.9 | 0 | 139.4854 | 0 | 0 | 0 | 0 | 0 | 126.9761
2962 | 337.8149 | 3.5 | 43.4 | 1.4 | 0 | 168.9075 | 0 | 0 | 0 | 0 | 0 | 64.38
2963 | 291.1211 | 3.5 | 43.4 | 0 | 0 | 145.5605 | 0 | 0 | 0 | 0 | 0 | 259.8489
2964 | 270.1219 | 2.8 | 43.3 | 0 | 0 | 135.061 | 0 | 0 | 0 | 0 | 0 | 185.8911
2965 | 221.9804 | 1.4 | 43.1 | 0 | 75.1 | 110.9902 | 0 | 0 | 0 | 0 | 24.4 | 84.6865
2966 | 228.4557 | 2.1 | 43.2 | 0 | 37.6 | 114.2278 | 0 | 0 | 0 | 0 | 21.4 | 90.0247
2967 | 221.7774 | 3.5 | 43.4 | 0 | 0 | 110.8887 | 0 | 0 | 0 | 0 | 0 | 229.5832
2968 | 198.9445 | 2.8 | 43.3 | 0 | 0 | 99.4723 | 0 | 0 | 0 | 0 | 0 | 104.4985
2969 | 161.7489 | 2.1 | 43.2 | 0 | 0 | 80.8744 | 0 | 0 | 0 | 0 | 0 | 178.5169
2970 | 162.8069 | 0.7 | 43 | 0 | 37.6 | 81.4035 | 0 | 0 | 0 | 0 | 16.7 | 125.2305
2971 | 118.4778 | 0 | 42.9 | 0 | 75.1 | 59.2389 | 0 | 0 | 0 | 0 | 4.5 | 106.7911
2972 | 66.4074 | 0 | 42.9 | 0 | 75.1 | 33.2037 | 0 | 0 | 0 | 0 | 0 | 138.6035
2973 | 43.7226 | 0 | 42.9 | 0 | 75.1 | 21.8613 | 0 | 0 | 0 | 0 | 10 | 268.0305
2974 | 40.4709 | 0 | 42.9 | 0 | 93.9 | 20.2355 | 0 | 0 | 0 | 0 | 22.6 | 121.1998
2975 | 40.1818 | 0 | 0 | 0 | 0 | 20.0909 | 0 | 0 | 0 | 0 | 0 | 100.9055
2976 | 42.923 | 0 | 0 | 0 | 0 | 21.4615 | 0 | 0 | 0 | 0 | 0 | 80.6594
2977 | 41.2265 | 0 | 0 | 0 | 0 | 20.6133 | 0 | 0 | 0 | 0 | 0 | 54.484
2978 | 41.9601 | 0 | 0 | 0 | 0 | 20.98 | 0 | 0 | 0 | 0 | 0 | 48.9739
2979 | 41.3015 | 0 | 0 | 0 | 0 | 20.6508 | 0 | 0 | 0 | 0 | 0 | 48.0539
2980 | 43.6318 | 0 | 0 | 0 | 0 | 21.8159 | 0 | 0 | 0 | 0 | 0 | 48.7429
2981 | 44.1928 | 0 | 0 | 0 | 0 | 22.0964 | 0 | 0 | 0 | 0 | 0 | 58.6322
2982 | 51.0092 | 0 | 0 | 0 | 0 | 25.5046 | 0 | 0 | 0 | 0 | 0 | 66.7938
2983 | 61.7341 | 0 | 42.9 | 9.5 | 56.3 | 30.867 | 0 | 0 | 0 | 0 | 208.6 | 60.0112
2984 | 60.0252 | 0 | 42.9 | 0.9 | 37.6 | 30.0126 | 0 | 0 | 0 | 0 | 106.3 | 82.0819
2985 | 56.8277 | 0 | 42.9 | 0 | 0 | 28.4138 | 0 | 0 | 0 | 0 | 0 | 78.4085
2986 | 57.4643 | 0 | 42.9 | 0 | 0 | 28.7321 | 0 | 0 | 0 | 0 | 0 | 61.6264
2987 | 55.7427 | 0 | 42.9 | 0 | 0 | 27.8713 | 0 | 0 | 0 | 0 | 0 | 56.2066
2988 | 55.1265 | 0 | 42.9 | 0 | 0 | 27.5633 | 0 | 0 | 0 | 0 | 0 | 82.2021
2989 | 52.9887 | 0 | 42.9 | 0 | 75.1 | 26.4943 | 0 | 0 | 0 | 0 | 0 | 74.742
2990 | 54.8495 | 0 | 42.9 | 0 | 37.6 | 27.4247 | 0 | 0 | 0 | 0 | 0 | 128.8429
2991 | 54.0833 | 0 | 42.9 | 0 | 0 | 27.0417 | 0 | 0 | 0 | 0 | 0 | 103.893
2992 | 53.5016 | 0 | 42.9 | 0 | 0 | 26.7508 | 0 | 0 | 0 | 0 | 0 | 84.6877
2993 | 52.063 | 0 | 42.9 | 0 | 0 | 26.0315 | 0 | 0 | 0 | 0 | 0 | 104.4977
2994 | 51.2271 | 0 | 42.9 | 0 | 37.6 | 25.6135 | 0 | 0 | 0 | 0 | 0 | 150.0392
2995 | 49.953 | 0 | 42.9 | 0 | 75.1 | 24.9765 | 0 | 0 | 0 | 0 | 0 | 154.9391
2996 | 45.1461 | 0 | 42.9 | 0 | 75.1 | 22.5731 | 0 | 0 | 0 | 0 | 0 | 190.3565
2997 | 43.2996 | 0 | 42.9 | 0 | 75.1 | 21.6498 | 0 | 0 | 0 | 0 | 0 | 214.881
2998 | 43.854 | 0 | 42.9 | 0 | 93.9 | 21.927 | 0 | 0 | 0 | 0 | 0 | 178.6848
2999 | 40.827 | 0 | 0 | 0 | 0 | 20.4135 | 0 | 0 | 0 | 0 | 0 | 127.7296
3000 | 40.5537 | 0 | 0 | 0 | 0 | 20.2768 | 0 | 0 | 0 | 0 | 0 | 81.8443
3001 | 40.5558 | 0 | 0 | 0 | 0 | 20.2779 | 0 | 0 | 0 | 0 | 0 | 67.2562
3002 | 42.0968 | 0 | 0 | 0 | 0 | 21.0484 | 0 | 0 | 0 | 0 | 0 | 56.6691
3003 | 41.2364 | 0 | 0 | 0 | 0 | 20.6182 | 0 | 0 | 0 | 0 | 0 | 47.478
3004 | 41.5386 | 0 | 0 | 0 | 0 | 20.7693 | 0 | 0 | 0 | 0 | 0 | 60.8188
3005 | 44.1032 | 0 | 0 | 0 | 0 | 22.0516 | 0 | 0 | 0 | 0 | 0 | 56.5539
3006 | 57.2306 | 0 | 0 | 0 | 0 | 28.6153 | 0 | 0 | 0 | 0 | 0 | 64.9544
3007 | 71.8434 | 0 | 42.9 | 0 | 56.3 | 35.9217 | 0 | 0 | 0 | 0 | 3.3 | 122.4292
3008 | 72.5364 | 0 | 42.9 | 0 | 37.6 | 36.2682 | 0 | 0 | 0 | 0 | 0 | 143.1334
3009 | 69.5739 | 0 | 42.9 | 0 | 0 | 34.7869 | 0 | 0 | 0 | 0 | 0 | 77.4442
3010 | 62.6511 | 0 | 42.9 | 0 | 0 | 31.3256 | 0 | 0 | 0 | 0 | 0 | 55.6338
3011 | 61.1397 | 0 | 42.9 | 0 | 0 | 30.5698 | 0 | 0 | 0 | 0 | 0 | 132.824
3012 | 60.4848 | 0 | 42.9 | 0 | 0 | 30.2424 | 0 | 0 | 0 | 0 | 0 | 115.5229
3013 | 61.6374 | 0 | 42.9 | 0 | 75.1 | 30.8187 | 0 | 0 | 0 | 0 | 0 | 167.4063
3014 | 67.2352 | 0 | 42.9 | 0 | 37.6 | 33.6176 | 0 | 0 | 0 | 0 | 0 | 152.5207
3015 | 71.7136 | 0 | 42.9 | 0 | 0 | 35.8568 | 0 | 0 | 0 | 0 | 0 | 131.6888
3016 | 74.643 | 0 | 42.9 | 0 | 0 | 37.3215 | 0 | 0 | 0 | 0 | 0 | 116.6397
3017 | 77.6343 | 0 | 42.9 | 0 | 0 | 38.8172 | 0 | 0 | 0 | 0 | 0 | 78.7674
3018 | 72.8888 | 0 | 42.9 | 0 | 37.6 | 36.4444 | 0 | 0 | 0 | 0 | 0 | 221.7485
3019 | 56.9498 | 0 | 42.9 | 0 | 75.1 | 28.4749 | 0 | 0 | 0 | 0 | 0 | 201.0261
3020 | 50.5301 | 0 | 42.9 | 0 | 75.1 | 25.265 | 0 | 0 | 0 | 0 | 0 | 173.6652
3021 | 40.8431 | 0 | 42.9 | 0 | 75.1 | 20.4216 | 0 | 0 | 0 | 0 | 0 | 221.0118
3022 | 42.4888 | 0 | 42.9 | 0 | 93.9 | 21.2444 | 0 | 0 | 0 | 0 | 0 | 201.2137
3023 | 41.0148 | 0 | 0 | 0 | 0 | 20.5074 | 0 | 0 | 0 | 0 | 0 | 196.932
3024 | 41.7872 | 0 | 0 | 0 | 0 | 20.8936 | 0 | 0 | 0 | 0 | 0 | 126.8932
3025 | 41.5572 | 0 | 0 | 0 | 0 | 20.7786 | 0 | 0 | 0 | 0 | 0 | 79.2402
3026 | 43.8838 | 0 | 0 | 0 | 0 | 21.9419 | 0 | 0 | 0 | 0 | 0 | 58.401
3027 | 42.7901 | 0 | 0 | 0 | 0 | 21.395 | 0 | 0 | 0 | 0 | 0 | 56.438
3028 | 40.6916 | 0 | 0 | 0 | 0 | 20.3458 | 0 | 0 | 0 | 0 | 0 | 61.0489
3029 | 42.782 | 0 | 0 | 0 | 0 | 21.391 | 0 | 0 | 0 | 0 | 0 | 60.0115
3030 | 59.5832 | 0 | 0 | 0 | 0 | 29.7916 | 0 | 0 | 0 | 0 | 0 | 53.2239
3031 | 87.0284 | 0 | 42.9 | 0 | 56.3 | 43.5142 | 0 | 0 | 0 | 0 | 12.8 | 67.0237
3032 | 147.4782 | 0.7 | 43 | 0 | 37.6 | 73.7391 | 0 | 0 | 0 | 0 | 2.3 | 152.5045
3033 | 218.7328 | 2.1 | 43.2 | 0 | 0 | 109.3664 | 0 | 0 | 0 | 0 | 0 | 170.7199
3034 | 227.6021 | 3.5 | 43.4 | 0 | 0 | 113.8011 | 0 | 0 | 0 | 0 | 0 | 92.4136
3035 | 245.8615 | 3.5 | 43.4 | 0 | 0 | 122.9308 | 0 | 0 | 0 | 0 | 0 | 76.6162
3036 | 248.8706 | 2.8 | 43.3 | 0 | 0 | 124.4353 | 0 | 0 | 0 | 0 | 0 | 84.0874
3037 | 241.3614 | 1.4 | 43.1 | 0 | 75.1 | 120.6807 | 0 | 0 | 0 | 0 | 0 | 217.5539
3038 | 230.9434 | 2.1 | 43.2 | 0 | 37.6 | 115.4717 | 0 | 0 | 3.1 | 0 | 0 | 221.1823
3039 | 226.222 | 3.5 | 43.4 | 0 | 0 | 113.111 | 0 | 0 | 16.5 | 0 | 0 | 90.3851
3040 | 194.1327 | 2.8 | 43.3 | 0 | 0 | 97.0663 | 0 | 0 | 33.9 | 0 | 0 | 107.7669
3041 | 146.9671 | 2.1 | 43.2 | 0 | 0 | 73.4836 | 0 | 0 | 58.8 | 0 | 0 | 110.9025
3042 | 116.1949 | 0.7 | 43 | 0 | 37.6 | 58.0975 | 0 | 0 | 69.9 | 0 | 0 | 245.3244
3043 | 88.12 | 0 | 42.9 | 0 | 75.1 | 44.06 | 0 | 0 | 15 | 0 | 0 | 293.4252
3044 | 67.5696 | 0 | 42.9 | 0 | 75.1 | 33.7848 | 0 | 0 | 0 | 0 | 0 | 153.8278
3045 | 60.0912 | 0 | 42.9 | 0 | 75.1 | 30.0456 | 0 | 0 | 0 | 0 | 0 | 140.1393
3046 | 54.2767 | 0 | 42.9 | 0 | 93.9 | 27.1384 | 0 | 0 | 0 | 0 | 0 | 169.4891
3047 | 41.2067 | 0 | 0 | 0 | 0 | 20.6033 | 0 | 0 | 0 | 0 | 0 | 271.451
3048 | 45.7594 | 0 | 0 | 0 | 0 | 22.8797 | 0 | 0 | 0 | 0 | 0 | 122.2078
3049 | 41.1806 | 0 | 0 | 0 | 0 | 20.5903 | 0 | 0 | 0 | 0 | 0 | 66.5614
3050 | 42.2824 | 0 | 0 | 0 | 0 | 21.1412 | 0 | 0 | 0 | 0 | 0 | 72.7803
3051 | 43.1363 | 0 | 0 | 0 | 0 | 21.5681 | 0 | 0 | 0 | 0 | 0 | 60.7032
3052 | 44.6818 | 0 | 0 | 0 | 0 | 22.3409 | 0 | 0 | 0 | 0 | 0 | 51.3843
3053 | 40.54 | 0 | 0 | 0 | 0 | 20.27 | 0 | 0 | 0 | 0 | 0 | 60.4728
3054 | 65.0843 | 0 | 0 | 0 | 0 | 32.5422 | 0 | 0 | 0 | 0 | 0 | 69.7825
3055 | 106.4237 | 0 | 42.9 | 0 | 56.3 | 53.2118 | 0 | 0 | 0 | 0 | 3.2 | 57.0159
3056 | 179.4832 | 0.7 | 43 | 0 | 37.6 | 89.7416 | 0 | 0 | 0 | 0 | 1.4 | 70.5904
3057 | 269.9081 | 2.1 | 43.2 | 0 | 0 | 134.954 | 0 | 0 | 0 | 0 | 0 | 123.2814
3058 | 321.5743 | 3.5 | 43.4 | 0 | 0 | 160.7872 | 0 | 0 | 0 | 0 | 0 | 169.1913
3059 | 326.1944 | 3.5 | 43.4 | 0 | 0 | 163.0972 | 0 | 0 | 0 | 0 | 0 | 96.8358
3060 | 294.4846 | 2.8 | 43.3 | 0 | 0 | 147.2423 | 0 | 0 | 0 | 0 | 0 | 66.3317
3061 | 260.576 | 1.4 | 43.1 | 0 | 75.1 | 130.288 | 0 | 0 | 0 | 0 | 0 | 92.887
3062 | 264.6555 | 2.1 | 43.2 | 0 | 37.6 | 132.3278 | 0 | 0 | 0 | 0 | 0 | 231.1354
3063 | 253.5866 | 3.5 | 43.4 | 0 | 0 | 126.7933 | 0 | 0 | 0 | 0 | 0 | 84.3269
3064 | 231.5217 | 2.8 | 43.3 | 0 | 0 | 115.7609 | 0 | 0 | 0 | 0 | 0 | 95.1548
3065 | 160.9601 | 2.1 | 43.2 | 0 | 0 | 80.4801 | 0 | 0 | 0 | 0 | 0 | 130.4363
3066 | 128.1021 | 0.7 | 43 | 0 | 37.6 | 64.0511 | 0 | 0 | 0 | 0 | 0 | 101.744
3067 | 104.156 | 0 | 42.9 | 0 | 75.1 | 52.078 | 0 | 0 | 0 | 0 | 0 | 198.5482
3068 | 76.3333 | 0 | 42.9 | 0 | 75.1 | 38.1666 | 0 | 0 | 0 | 0 | 0 | 214.8098
3069 | 62.8163 | 0 | 42.9 | 0 | 75.1 | 31.4082 | 0 | 0 | 0 | 0 | 0 | 156.5664
3070 | 62.9632 | 0 | 42.9 | 0 | 93.9 | 31.4816 | 0 | 0 | 0 | 0 | 0 | 225.4006
3071 | 60.2176 | 0 | 0 | 0 | 0 | 30.1088 | 0 | 0 | 0 | 0 | 0 | 424.4285
3072 | 56.1663 | 0 | 0 | 0 | 0 | 28.0832 | 0 | 0 | 0 | 0 | 0 | 117.3739
3073 | 56.925 | 0 | 0 | 0 | 0 | 28.4625 | 0 | 0 | 0 | 0 | 0 | 71.2781
3074 | 56.9607 | 0 | 0 | 0 | 0 | 28.4803 | 0 | 0 | 0 | 0 | 0 | 66.1023
3075 | 52.8858 | 0 | 0 | 0 | 0 | 26.4429 | 0 | 0 | 0 | 0 | 0 | 52.0744
3076 | 43.074 | 0 | 0 | 0 | 0 | 21.537 | 0 | 0 | 0 | 0 | 0 | 48.5144
3077 | 42.6769 | 0 | 0 | 0 | 0 | 21.3385 | 0 | 0 | 0 | 0 | 0 | 57.7072
3078 | 63.0993 | 0 | 0 | 0 | 0 | 31.5496 | 0 | 0 | 0 | 0 | 0 | 79.7168
3079 | 89.5546 | 0 | 42.9 | 3.4 | 56.3 | 44.7773 | 0 | 0 | 0 | 0 | 51 | 53.2237
3080 | 153.7222 | 0.7 | 43 | 17.2 | 37.6 | 76.8611 | 0 | 0 | 0 | 1.5 | 44.9 | 88.0057
3081 | 232.1301 | 2.1 | 43.2 | 5.9 | 0 | 116.065 | 0 | 0 | 0 | 3.2 | 0 | 95.0347
3082 | 262.5068 | 3.5 | 43.4 | 0.4 | 0 | 131.2534 | 0 | 0 | 0 | 20.1 | 0 | 90.2614
3083 | 258.1273 | 3.5 | 43.4 | 0 | 0 | 129.0637 | 0 | 0 | 0 | 17.3 | 0 | 55.2872
3084 | 262.2942 | 2.8 | 43.3 | 0 | 0 | 131.1471 | 0 | 0 | 0 | 4 | 0 | 105.3423
3085 | 257.2964 | 1.4 | 43.1 | 0 | 75.1 | 128.6482 | 0 | 0 | 0 | 0 | 6.9 | 235.3766
3086 | 257.1446 | 2.1 | 43.2 | 0 | 37.6 | 128.5723 | 0 | 0 | 0 | 0 | 6.4 | 167.3684
3087 | 249.4207 | 3.5 | 43.4 | 0 | 0 | 124.7103 | 0 | 0 | 0 | 1 | 0 | 175.4385
3088 | 228.3218 | 2.8 | 43.3 | 0 | 0 | 114.1609 | 0 | 0 | 0 | 1.6 | 0 | 180.0616
3089 | 178.5237 | 2.1 | 43.2 | 0 | 0 | 89.2619 | 0 | 0 | 0 | 0 | 0 | 133.679
3090 | 133.6091 | 0.7 | 43 | 0 | 37.6 | 66.8046 | 0 | 0 | 0 | 0 | 6.3 | 201.439
3091 | 108.1459 | 0 | 42.9 | 0 | 75.1 | 54.073 | 0 | 0 | 0 | 0 | 3.4 | 131.7789
3092 | 63.3336 | 0 | 42.9 | 0 | 75.1 | 31.6668 | 0 | 0 | 0 | 0 | 0 | 171.2865
3093 | 42.9525 | 0 | 42.9 | 0 | 75.1 | 21.4762 | 0 | 0 | 0 | 0 | 10.1 | 129.756
3094 | 42.575 | 0 | 42.9 | 0 | 93.9 | 21.2875 | 0 | 0 | 0 | 0 | 23.3 | 114.169
3095 | 42.9497 | 0 | 0 | 0 | 0 | 21.4748 | 0 | 0 | 0 | 0 | 0 | 121.8693
3096 | 41.2219 | 0 | 0 | 0 | 0 | 20.6109 | 0 | 0 | 0 | 0 | 0 | 104.2594
3097 | 41.9638 | 0 | 0 | 0 | 0 | 20.9819 | 0 | 0 | 0 | 0 | 0 | 71.5105
3098 | 43.1301 | 0 | 0 | 0 | 0 | 21.565 | 0 | 0 | 0 | 0 | 0 | 52.4201
3099 | 41.8966 | 0 | 0 | 0 | 0 | 20.9483 | 0 | 0 | 0 | 0 | 0 | 46.5645
3100 | 41.0982 | 0 | 0 | 0 | 0 | 20.5491 | 0 | 0 | 0 | 0 | 0 | 53.3389
3101 | 42.9249 | 0 | 0 | 0 | 0 | 21.4624 | 0 | 0 | 0 | 0 | 0 | 56.3222
3102 | 51.3266 | 0 | 0 | 0 | 0 | 25.6633 | 0 | 0 | 0 | 0 | 0 | 57.3617
3103 | 70.494 | 0 | 42.9 | 43.8 | 56.3 | 35.247 | 0 | 0 | 0 | 0 | 320.6 | 60.8179
3104 | 64.5572 | 0.7 | 43 | 38 | 37.6 | 32.2786 | 0 | 0 | 0 | 18.7 | 204.8 | 78.4018
3105 | 63.2756 | 2.1 | 43.2 | 6.6 | 0 | 31.6378 | 0 | 0 | 0 | 19.3 | 0 | 87.056
3106 | 60.5186 | 3.5 | 43.4 | 0 | 0 | 30.2593 | 0 | 0 | 0 | 35.5 | 0 | 64.4935
3107 | 60.8908 | 3.5 | 43.4 | 0 | 0 | 30.4454 | 0 | 0 | 0 | 33.3 | 0 | 92.2907
3108 | 59.0771 | 2.8 | 43.3 | 0 | 0 | 29.5386 | 0 | 0 | 0 | 21.5 | 0 | 93.8453
3109 | 58.3032 | 1.4 | 43.1 | 0 | 75.1 | 29.1516 | 0 | 0 | 0 | 1.9 | 24.6 | 72.7782
3110 | 55.2071 | 2.1 | 43.2 | 0 | 37.6 | 27.6036 | 0 | 0 | 0 | 1.3 | 40.1 | 60.9342
3111 | 54.6427 | 3.5 | 43.4 | 0 | 0 | 27.3214 | 0 | 0 | 0 | 13.4 | 0 | 76.9724
3112 | 58.5967 | 2.8 | 43.3 | 0 | 0 | 29.2984 | 0 | 0 | 0 | 12.9 | 0 | 99.7144
3113 | 58.5307 | 2.1 | 43.2 | 0 | 0 | 29.2654 | 0 | 0 | 0 | 5.6 | 0 | 69.5539
3114 | 56.9352 | 0.7 | 43 | 0 | 37.6 | 28.4676 | 0 | 0 | 0 | 0 | 32 | 109.0899
3115 | 57.6952 | 0 | 42.9 | 0 | 75.1 | 28.8476 | 0 | 0 | 0 | 0 | 14.5 | 222.5172
3116 | 54.1537 | 0 | 42.9 | 0 | 75.1 | 27.0768 | 0 | 0 | 0 | 0 | 6.6 | 226.8043
3117 | 44.7413 | 0 | 42.9 | 0 | 75.1 | 22.3707 | 0 | 0 | 0 | 0 | 38.1 | 176.0684
3118 | 41.5829 | 0 | 42.9 | 0 | 93.9 | 20.7915 | 0 | 0 | 0 | 0 | 67.2 | 157.2696
3119 | 41.4447 | 0 | 0 | 0 | 0 | 20.7223 | 0 | 0 | 0 | 0 | 0 | 133.7635
3120 | 41.6802 | 0 | 0 | 0 | 0 | 20.8401 | 0 | 0 | 0 | 0 | 0 | 80.7803
3121 | 41.0663 | 0 | 0 | 0 | 0 | 20.5331 | 0 | 0 | 0 | 0 | 0 | 57.8232
3122 | 42.0949 | 0 | 0 | 0 | 0 | 21.0475 | 0 | 0 | 0 | 0 | 0 | 55.8636
3123 | 41.2687 | 0 | 0 | 0 | 0 | 20.6343 | 0 | 0 | 0 | 0 | 0 | 47.021
3124 | 43.202 | 0 | 0 | 0 | 0 | 21.601 | 0 | 0 | 0 | 0 | 0 | 58.0546
3125 | 43.7425 | 0 | 0 | 0 | 0 | 21.8712 | 0 | 0 | 0 | 0 | 0 | 58.4022
3126 | 55.8868 | 0 | 0 | 0 | 0 | 27.9434 | 0 | 0 | 0 | 0 | 0 | 64.9548
3127 | 87.5729 | 0 | 42.9 | 14.8 | 56.3 | 43.7865 | 0 | 0 | 0 | 0 | 246.2 | 51.8434
3128 | 127.5272 | 0.7 | 43 | 6.8 | 37.6 | 63.7636 | 0 | 0 | 0 | 14.6 | 124.4 | 64.7252
3129 | 209.1893 | 2.1 | 43.2 | 0 | 0 | 104.5947 | 0 | 0 | 0 | 2.6 | 0 | 59.8959
3130 | 214.6502 | 3.5 | 43.4 | 0 | 0 | 107.3251 | 0 | 0 | 0 | 2.4 | 0 | 69.323
3131 | 209.2191 | 3.5 | 43.4 | 0 | 0 | 104.6095 | 0 | 0 | 0 | 0 | 0 | 71.7417
3132 | 205.4895 | 2.8 | 43.3 | 0 | 0 | 102.7447 | 0 | 0 | 0 | 0 | 0 | 114.7726
3133 | 201.6374 | 1.4 | 43.1 | 0 | 75.1 | 100.8187 | 0 | 0 | 0 | 0 | 0 | 185.7466
3134 | 197.1216 | 2.1 | 43.2 | 0 | 37.6 | 98.5608 | 0 | 0 | 0 | 0 | 0 | 110.8978
3135 | 193.3266 | 3.5 | 43.4 | 0 | 0 | 96.6633 | 0 | 0 | 0 | 0 | 0 | 61.7408
3136 | 162.9848 | 2.8 | 43.3 | 0 | 0 | 81.4924 | 0 | 0 | 0 | 0 | 0 | 56.9
3137 | 113.1716 | 2.1 | 43.2 | 0 | 0 | 56.5858 | 0 | 0 | 0 | 0 | 0 | 89.188
3138 | 78.142 | 0.7 | 43 | 0 | 37.6 | 39.071 | 0 | 0 | 0 | 0 | 0 | 106.6742
3139 | 53.9842 | 0 | 42.9 | 0 | 75.1 | 26.9921 | 0 | 0 | 0 | 0 | 0 | 161.1204
3140 | 42.5254 | 0 | 42.9 | 0 | 75.1 | 21.2627 | 0 | 0 | 0 | 0 | 0 | 130.3391
3141 | 40.836 | 0 | 42.9 | 0 | 75.1 | 20.418 | 0 | 0 | 0 | 0 | 0 | 239.2869
3142 | 42.0255 | 0 | 42.9 | 0 | 93.9 | 21.0127 | 0 | 0 | 0 | 0 | 0 | 188.46
3143 | 38.8113 | 0 | 0 | 0 | 0 | 19.4056 | 0 | 0 | 0 | 0 | 0 | 146.7736
3144 | 42.774 | 0 | 0 | 0 | 0 | 21.387 | 0 | 0 | 0 | 0 | 0 | 107.1513
3145 | 42.2961 | 0 | 0 | 0 | 0 | 21.148 | 0 | 0 | 0 | 0 | 0 | 72.5489
3146 | 41.6145 | 0 | 0 | 0 | 0 | 20.8073 | 0 | 0 | 0 | 0 | 0 | 53.3383
3147 | 42.1526 | 0 | 0 | 0 | 0 | 21.0763 | 0 | 0 | 0 | 0 | 0 | 47.3629
3148 | 42.8418 | 0 | 0 | 0 | 0 | 21.4209 | 0 | 0 | 0 | 0 | 0 | 62.7754
3149 | 43.1511 | 0 | 0 | 0 | 0 | 21.5756 | 0 | 0 | 0 | 0 | 0 | 52.1906
3150 | 43.506 | 0 | 0 | 0 | 0 | 21.753 | 0 | 0 | 0 | 0 | 0 | 60.8175
3151 | 62.4252 | 0 | 42.9 | 21.7 | 56.3 | 31.2126 | 0 | 0 | 0 | 0 | 247.6 | 100.0725
3152 | 66.4592 | 0 | 42.9 | 33.5 | 37.6 | 33.2296 | 0 | 0 | 0 | 0 | 223.5 | 66.5625
3153 | 65.5 | 0 | 42.9 | 26.3 | 0 | 32.75 | 0 | 0 | 0 | 0 | 0 | 81.2529
3154 | 62.9174 | 0 | 42.9 | 22.2 | 0 | 31.4587 | 0 | 0 | 0 | 0 | 0 | 189.5851
3155 | 64.4022 | 0 | 42.9 | 15.5 | 0 | 32.2011 | 0 | 0 | 0 | 0 | 0 | 158.9187
3156 | 68.3017 | 0 | 42.9 | 8.9 | 0 | 34.1508 | 0 | 0 | 0 | 0 | 0 | 214.9653
3157 | 72.2256 | 0 | 42.9 | 4.5 | 75.1 | 36.1128 | 0 | 0 | 0 | 0 | 201.3 | 97.4329
3158 | 77.3715 | 0 | 42.9 | 1.1 | 37.6 | 38.6858 | 0 | 0 | 0 | 0 | 167.6 | 184.6564
3159 | 84.7678 | 0 | 42.9 | 1.3 | 0 | 42.3839 | 0 | 0 | 0 | 0 | 0 | 160.548
3160 | 85.3725 | 0 | 42.9 | 1 | 0 | 42.6862 | 0 | 0 | 0 | 0 | 0 | 145.6611
3161 | 87.4967 | 0 | 42.9 | 1.9 | 0 | 43.7484 | 0 | 0 | 0 | 0 | 0 | 170.0588
3162 | 78.7761 | 0 | 42.9 | 6.2 | 37.6 | 39.3881 | 0 | 0 | 0 | 0 | 220.1 | 167.1791
3163 | 69.1251 | 0 | 42.9 | 1.9 | 75.1 | 34.5626 | 0 | 0 | 0 | 0 | 192.2 | 182.4579
3164 | 56.7849 | 0 | 42.9 | 0 | 75.1 | 28.3925 | 0 | 0 | 0 | 0 | 170.3 | 199.5906
3165 | 47.0242 | 0 | 42.9 | 3 | 75.1 | 23.5121 | 0 | 0 | 0 | 0 | 231.9 | 235.6601
3166 | 41.6765 | 0 | 42.9 | 9.4 | 93.9 | 20.8383 | 0 | 0 | 0 | 0 | 262.5 | 302.5056
3167 | 42.2381 | 0 | 0 | 0 | 0 | 21.119 | 0 | 0 | 0 | 0 | 0 | 178.9467
3168 | 41.8863 | 0 | 0 | 0 | 0 | 20.9432 | 0 | 0 | 0 | 0 | 0 | 98.3951
3169 | 44.0202 | 0 | 0 | 0 | 0 | 22.0101 | 0 | 0 | 0 | 0 | 2.1 | 68.5172
3170 | 41.2194 | 0 | 0 | 0 | 0 | 20.6097 | 0 | 0 | 0 | 0 | 8.9 | 57.5936
3171 | 44.5554 | 0 | 0 | 3.4 | 0 | 22.2777 | 0 | 0 | 0 | 0 | 18.7 | 46.9056
3172 | 40.1213 | 0 | 0 | 9.1 | 0 | 20.0607 | 0 | 0 | 0 | 0 | 35.4 | 46.7911
3173 | 43.1443 | 0 | 0 | 14 | 0 | 21.5722 | 0 | 0 | 0 | 0 | 62.2 | 61.5082
3174 | 48.0522 | 0 | 0 | 14.6 | 0 | 24.0261 | 0 | 0 | 0 | 0 | 70.9 | 66.561
3175 | 54.4683 | 0 | 42.9 | 118.6 | 56.3 | 27.2341 | 0 | 0 | 0 | 0 | 496.5 | 51.5004
3176 | 53.6876 | 0 | 42.9 | 47.3 | 37.6 | 26.8438 | 0 | 0 | 0 | 0 | 322.8 | 75.2081
3177 | 54.5643 | 0 | 42.9 | 4.2 | 0 | 27.2822 | 0 | 0 | 0 | 0 | 0 | 55.749
3178 | 51.6306 | 0 | 42.9 | 0 | 0 | 25.8153 | 0 | 0 | 0 | 0 | 0 | 84.8056
3179 | 50.9339 | 0 | 42.9 | 0 | 0 | 25.467 | 0 | 0 | 0 | 0 | 0 | 64.6106
3180 | 51.9477 | 0 | 42.9 | 0 | 0 | 25.9738 | 0 | 0 | 0 | 0 | 0 | 269.3723
3181 | 51.7465 | 0 | 42.9 | 0 | 75.1 | 25.8733 | 0 | 0 | 0 | 0 | 2.8 | 142.3428
3182 | 51.502 | 0 | 42.9 | 0 | 37.6 | 25.751 | 0 | 0 | 0 | 0 | 0 | 228.5528
3183 | 49.6781 | 0 | 42.9 | 0 | 0 | 24.839 | 0 | 0 | 0 | 0 | 0 | 132.7339
3184 | 50.1668 | 0 | 42.9 | 0 | 0 | 25.0834 | 0 | 0 | 0 | 0 | 0 | 87.6442
3185 | 53.3656 | 0 | 42.9 | 0 | 0 | 26.6828 | 0 | 0 | 0 | 0 | 0 | 107.1504
3186 | 54.9149 | 0 | 42.9 | 0 | 37.6 | 27.4574 | 0 | 0 | 0 | 0 | 0 | 137.6859
3187 | 46.3188 | 0 | 42.9 | 0 | 75.1 | 23.1594 | 0 | 0 | 0 | 0 | 0 | 182.8143
3188 | 45.5298 | 0 | 42.9 | 0 | 75.1 | 22.7649 | 0 | 0 | 0 | 0 | 0 | 174.1357
3189 | 44.6171 | 0 | 42.9 | 0 | 75.1 | 22.3085 | 0 | 0 | 0 | 0 | 0 | 128.9199
3190 | 43.6954 | 0 | 42.9 | 0 | 93.9 | 21.8477 | 0 | 0 | 0 | 0 | 0 | 146.5563
3191 | 42.4005 | 0 | 0 | 0 | 0 | 21.2002 | 0 | 0 | 0 | 0 | 0 | 107.2726
3192 | 43.241 | 0 | 0 | 0 | 0 | 21.6205 | 0 | 0 | 0 | 0 | 0 | 71.5109
3193 | 42.2954 | 0 | 0 | 0 | 0 | 21.1477 | 0 | 0 | 0 | 0 | 0 | 54.0258
3194 | 41.887 | 0 | 0 | 0 | 0 | 20.9435 | 0 | 0 | 0 | 0 | 0 | 47.939
3195 | 42.5322 | 0 | 0 | 0 | 0 | 21.2661 | 0 | 0 | 0 | 0 | 0 | 52.9932
3196 | 41.4961 | 0 | 0 | 0 | 0 | 20.7481 | 0 | 0 | 0 | 0 | 0 | 47.594
3197 | 44.2495 | 0 | 0 | 0 | 0 | 22.1247 | 0 | 0 | 0 | 0 | 0 | 65.7557
3198 | 58.3767 | 0 | 0 | 0 | 0 | 29.1883 | 0 | 0 | 0 | 0 | 0 | 73.9316
3199 | 97.8131 | 0 | 42.9 | 6.6 | 56.3 | 48.9065 | 0 | 0 | 0 | 0 | 177.1 | 80.4228
3200 | 183.5628 | 0.7 | 43 | 8.4 | 37.6 | 91.7814 | 0 | 0 | 0 | 0 | 95.3 | 51.9591
3201 | 269.1655 | 2.1 | 43.2 | 0 | 0 | 134.5828 | 0 | 0 | 0 | 0 | 0 | 58.0562
3202 | 322.1344 | 3.5 | 43.4 | 0 | 0 | 161.0672 | 0 | 0 | 0 | 0 | 0 | 125.4851
3203 | 317.4874 | 3.5 | 43.4 | 0 | 0 | 158.7437 | 0 | 0 | 0 | 0 | 0 | 74.971
3204 | 298.1944 | 2.8 | 43.3 | 0 | 0 | 149.0972 | 0 | 0 | 0 | 0 | 0 | 81.0171
3205 | 299.1992 | 1.4 | 43.1 | 0 | 75.1 | 149.5996 | 0 | 0 | 0 | 0 | 0 | 68.632
3206 | 322.0101 | 2.1 | 43.2 | 0 | 37.6 | 161.005 | 0 | 0 | 0 | 0 | 0 | 89.7857
3207 | 255.7285 | 3.5 | 43.4 | 0 | 0 | 127.8643 | 0 | 0 | 0 | 0 | 0 | 98.8734
3208 | 204.7624 | 2.8 | 43.3 | 0 | 0 | 102.3812 | 0 | 0 | 0 | 0 | 0 | 130.5451
3209 | 167.6464 | 2.1 | 43.2 | 0 | 0 | 83.8232 | 0 | 0 | 0 | 0 | 0 | 275.2344
3210 | 153.4073 | 0.7 | 43 | 0 | 37.6 | 76.7036 | 0 | 0 | 0.6 | 0 | 0 | 202.1783
3211 | 109.9686 | 0 | 42.9 | 0 | 75.1 | 54.9843 | 0 | 0 | 0 | 0 | 0 | 201.0664
3212 | 57.1956 | 0 | 42.9 | 0 | 75.1 | 28.5978 | 0 | 0 | 0 | 0 | 0 | 208.9784
3213 | 43.625 | 0 | 42.9 | 0 | 75.1 | 21.8125 | 0 | 0 | 0 | 0 | 0 | 204.9747
3214 | 42.8796 | 0 | 42.9 | 0 | 93.9 | 21.4398 | 0 | 0 | 0 | 0 | 0 | 138.076
3215 | 39.6202 | 0 | 0 | 0 | 0 | 19.8101 | 0 | 0 | 0 | 0 | 0 | 98.7564
3216 | 43.7682 | 0 | 0 | 0 | 0 | 21.8841 | 0 | 0 | 0 | 0 | 0 | 71.8575
3217 | 41.5916 | 0 | 0 | 0 | 0 | 20.7958 | 0 | 0 | 0 | 0 | 0 | 60.2412
3218 | 41.1723 | 0 | 0 | 0 | 0 | 20.5861 | 0 | 0 | 0 | 0 | 0 | 53.225
3219 | 40.2971 | 0 | 0 | 0 | 0 | 20.1485 | 0 | 0 | 0 | 0 | 0 | 45.8801
3220 | 42.6435 | 0 | 0 | 0 | 0 | 21.3217 | 0 | 0 | 0 | 0 | 0 | 50.0066
3221 | 39.9574 | 0 | 0 | 0 | 0 | 19.9787 | 0 | 0 | 0 | 0 | 0 | 54.8279
3222 | 59.7168 | 0 | 0 | 0 | 0 | 29.8584 | 0 | 0 | 0 | 0 | 0 | 67.1391
3223 | 104.2511 | 0 | 42.9 | 0 | 56.3 | 52.1256 | 0 | 0 | 0 | 0 | 18 | 70.3581
3224 | 170.7084 | 0.7 | 43 | 0 | 37.6 | 85.3542 | 0 | 0 | 0 | 0 | 2.3 | 72.4339
3225 | 263.6291 | 2.1 | 43.2 | 0 | 0 | 131.8145 | 0 | 0 | 0 | 0 | 0 | 95.7512
3226 | 321.6013 | 3.5 | 43.4 | 0 | 0 | 160.8007 | 0 | 0 | 0 | 0 | 0 | 63.2324
3227 | 265.2431 | 3.5 | 43.4 | 0 | 0 | 132.6216 | 0 | 0 | 0 | 0 | 0 | 85.0414
3228 | 251.6093 | 2.8 | 43.3 | 0 | 0 | 125.8047 | 0 | 0 | 3.5 | 0 | 0 | 118.0265
3229 | 232.2286 | 1.4 | 43.1 | 0 | 75.1 | 116.1143 | 0 | 0.2 | 28.1 | 0 | 0 | 193.6998
3230 | 224.1471 | 2.1 | 43.2 | 0 | 37.6 | 112.0736 | 0 | 6.9 | 56.5 | 0 | 0 | 122.0235
3231 | 214.8507 | 3.5 | 43.4 | 0 | 0 | 107.4253 | 0 | 29.2 | 86 | 0 | 0 | 129.7077
3232 | 173.4351 | 2.8 | 43.3 | 0 | 0 | 86.7176 | 0 | 39.9 | 115.3 | 0 | 0 | 103.6557
3233 | 123.3405 | 2.1 | 43.2 | 0 | 0 | 61.6702 | 0 | 50.7 | 140.8 | 0 | 0 | 244.0682
3234 | 86.4715 | 0.7 | 43 | 0 | 37.6 | 43.2357 | 0 | 46.2 | 151.6 | 0 | 0 | 178.5571
3235 | 62.0372 | 0 | 42.9 | 0 | 75.1 | 31.0186 | 2.4 | 0 | 74.5 | 0 | 0 | 373.374
3236 | 44.0353 | 0 | 42.9 | 0 | 75.1 | 22.0177 | 0 | 0 | 4.7 | 0 | 0 | 325.9086
3237 | 41.4475 | 0 | 42.9 | 0 | 75.1 | 20.7237 | 0 | 0 | 0 | 0 | 0 | 358.9342
3238 | 41.71 | 0 | 42.9 | 0 | 93.9 | 20.855 | 0 | 0 | 0 | 0 | 0 | 276.7069
3239 | 40.576 | 0 | 0 | 0 | 0 | 20.288 | 0 | 0 | 0 | 0 | 0 | 178.5004
3240 | 44.1367 | 0 | 0 | 0 | 0 | 22.0683 | 0 | 0 | 0 | 0 | 0 | 128.6738
3241 | 42.028 | 0 | 0 | 0 | 0 | 21.014 | 0 | 0 | 0 | 0 | 0 | 67.255
3242 | 41.6725 | 0 | 0 | 0 | 0 | 20.8362 | 0 | 0 | 0 | 0 | 0 | 57.5927
3243 | 39.9977 | 0 | 0 | 0 | 0 | 19.9988 | 0 | 0 | 0 | 0 | 0 | 57.593
3244 | 42.5868 | 0 | 0 | 0 | 0 | 21.2934 | 0 | 0 | 0 | 0 | 0 | 57.9395
3245 | 42.0122 | 0 | 0 | 0 | 0 | 21.0061 | 0 | 0 | 0 | 0 | 0 | 60.1259
3246 | 58.0593 | 0 | 0 | 0 | 0 | 29.0297 | 0 | 0 | 0 | 0 | 0 | 85.8655
3247 | 106.8157 | 0 | 42.9 | 0 | 56.3 | 53.4079 | 0 | 0 | 0 | 0 | 0 | 90.1452
3248 | 153.2539 | 0.7 | 43 | 0 | 37.6 | 76.6269 | 0 | 0 | 0 | 0 | 0 | 57.3632
3249 | 228.7079 | 2.1 | 43.2 | 0 | 0 | 114.354 | 0 | 0 | 0 | 0 | 0 | 93.7268
3250 | 267.3813 | 3.5 | 43.4 | 0 | 0 | 133.6906 | 0 | 0 | 0 | 0 | 0 | 209.7245
3251 | 278.6203 | 3.5 | 43.4 | 0 | 0 | 139.3102 | 0 | 0 | 3.4 | 0 | 0 | 166.5761
3252 | 233.3121 | 2.8 | 43.3 | 0 | 0 | 116.6561 | 0 | 1.7 | 25.3 | 0 | 0 | 89.7869
3253 | 214.4738 | 1.4 | 43.1 | 0 | 75.1 | 107.2369 | 0 | 7.7 | 56.6 | 0 | 0 | 185.5447
3254 | 209.9678 | 2.1 | 43.2 | 0 | 37.6 | 104.9839 | 0 | 19.5 | 84.1 | 0 | 0 | 142.3457
3255 | 188.7378 | 3.5 | 43.4 | 0 | 0 | 94.3689 | 0 | 40.2 | 105.2 | 0 | 0 | 224.7642
3256 | 147.1893 | 2.8 | 43.3 | 0 | 0 | 73.5947 | 0 | 51.2 | 129.3 | 0 | 0 | 167.8586
3257 | 106.8445 | 2.1 | 43.2 | 0 | 0 | 53.4223 | 0 | 65.9 | 151.1 | 0 | 0 | 141.2596
3258 | 87.4257 | 0.7 | 43 | 0 | 37.6 | 43.7129 | 26.4 | 61.2 | 158.6 | 0 | 0 | 106.4284
3259 | 58.4244 | 0 | 42.9 | 0 | 75.1 | 29.2122 | 33.7 | 0 | 82.3 | 0 | 0 | 138.1115
3260 | 45.0881 | 0 | 42.9 | 0 | 75.1 | 22.5441 | 7.4 | 0 | 11 | 0 | 0 | 197.2453
3261 | 43.6331 | 0 | 42.9 | 0 | 75.1 | 21.8165 | 0 | 0 | 0.2 | 0 | 0 | 149.3717
3262 | 41.4261 | 0 | 42.9 | 0 | 93.9 | 20.7131 | 0 | 0 | 0 | 0 | 0 | 154.6157
3263 | 43.4471 | 0 | 0 | 0 | 0 | 21.7236 | 0 | 0 | 0 | 0 | 0 | 137.5553
3264 | 41.9365 | 0 | 0 | 0 | 0 | 20.9683 | 0 | 0 | 0 | 0 | 0 | 94.7981
3265 | 41.3864 | 0 | 0 | 0 | 0 | 20.6932 | 0 | 0 | 0 | 0 | 0 | 78.1669
3266 | 39.8328 | 0 | 0 | 0 | 0 | 19.9164 | 0 | 0 | 0 | 0 | 0 | 80.306
3267 | 40.8757 | 0 | 0 | 0 | 0 | 20.4378 | 0 | 0 | 0 | 0 | 0 | 77.9259
3268 | 43.1074 | 0 | 0 | 0 | 0 | 21.5537 | 0 | 0 | 0 | 0 | 0 | 81.7253
3269 | 42.7179 | 0 | 0 | 0 | 0 | 21.3589 | 0 | 0 | 0 | 0 | 0 | 76.4967
3270 | 62.781 | 0 | 0 | 0 | 0 | 31.3905 | 0 | 0 | 0 | 0 | 0 | 72.0867
3271 | 91.6639 | 0 | 42.9 | 0 | 56.3 | 45.832 | 0 | 0 | 0 | 0 | 0 | 60.5865
3272 | 154.6597 | 0.7 | 43 | 0 | 37.6 | 77.3298 | 0 | 0 | 0 | 0 | 0 | 50.8116
3273 | 239.5574 | 2.1 | 43.2 | 0 | 0 | 119.7787 | 0 | 0 | 0 | 0 | 0 | 62.0858
3274 | 298.3943 | 3.5 | 43.4 | 0 | 0 | 149.1972 | 0 | 0 | 2.3 | 0 | 0 | 50.8113
3275 | 266.1311 | 3.5 | 43.4 | 0 | 0 | 133.0655 | 0 | 2.7 | 19.1 | 0 | 0 | 93.0067
3276 | 246.7925 | 2.8 | 43.3 | 0 | 0 | 123.3963 | 0 | 23.7 | 52.4 | 0 | 0 | 66.7927
3277 | 226.5335 | 1.4 | 43.1 | 0 | 75.1 | 113.2668 | 4 | 40.4 | 94.5 | 0 | 0 | 169.0879
3278 | 219.6597 | 2.1 | 43.2 | 0 | 37.6 | 109.8299 | 14 | 52.6 | 122.5 | 0 | 0 | 127.9092
3279 | 196.5618 | 3.5 | 43.4 | 0 | 0 | 98.2809 | 0 | 73.9 | 145.1 | 0 | 0 | 145.9941
3280 | 156.4566 | 2.8 | 43.3 | 0 | 0 | 78.2283 | 0 | 86.8 | 171.3 | 0 | 0 | 96.714
3281 | 107.8171 | 2.1 | 43.2 | 0 | 0 | 53.9085 | 0 | 99.6 | 193.6 | 0 | 0 | 62.2006
3282 | 79.4396 | 0.7 | 43 | 0 | 37.6 | 39.7198 | 143.6 | 90 | 200.7 | 0 | 0 | 71.3955
3283 | 58.4567 | 0 | 42.9 | 0 | 75.1 | 29.2283 | 146.2 | 3.9 | 119.7 | 0 | 0 | 148.9789
3284 | 44.009 | 0 | 42.9 | 0 | 75.1 | 22.0045 | 59.3 | 0 | 32.9 | 0 | 0 | 165.9151
3285 | 40.584 | 0 | 42.9 | 0 | 75.1 | 20.292 | 17.6 | 0 | 10.3 | 0 | 0 | 182.5467
3286 | 43.2664 | 0 | 42.9 | 0 | 93.9 | 21.6332 | 6.6 | 0 | 0.5 | 0 | 0 | 171.0479
3287 | 41.1478 | 0 | 0 | 0 | 0 | 20.5739 | 0 | 0 | 0 | 0 | 0 | 118.6215
3288 | 42.3652 | 0 | 0 | 0 | 0 | 21.1826 | 0 | 0 | 0 | 0 | 0 | 71.5121
3289 | 41.9223 | 0 | 0 | 0 | 0 | 20.9611 | 0 | 0 | 0 | 0 | 0 | 63.9228
3290 | 42.0472 | 0 | 0 | 0 | 0 | 21.0236 | 0 | 0 | 0 | 0 | 0 | 56.5521
3291 | 42.9537 | 0 | 0 | 0 | 0 | 21.4769 | 0 | 0 | 0 | 0 | 0 | 51.4998
3292 | 43.0423 | 0 | 0 | 0 | 0 | 21.5212 | 0 | 0 | 0 | 0 | 0 | 50.4665
3293 | 44.2501 | 0 | 0 | 0 | 0 | 22.1251 | 0 | 0 | 0 | 0 | 0 | 56.3201
3294 | 58.5007 | 0 | 0 | 0 | 0 | 29.2503 | 0 | 0 | 0 | 0 | 0 | 56.7844
3295 | 93.3713 | 0 | 42.9 | 0 | 56.3 | 46.6856 | 0 | 0 | 0 | 0 | 0 | 49.8937
3296 | 145.8083 | 0.7 | 43 | 0 | 37.6 | 72.9042 | 0 | 0 | 0 | 0 | 0 | 55.7487
3297 | 212.6834 | 2.1 | 43.2 | 0 | 0 | 106.3417 | 0 | 0 | 0 | 0 | 0 | 58.1707
3298 | 262.7901 | 3.5 | 43.4 | 0 | 0 | 131.3951 | 0 | 0 | 0 | 0 | 0 | 79.1221
3299 | 260.2738 | 3.5 | 43.4 | 0 | 0 | 130.1369 | 0 | 0.1 | 4 | 0 | 0 | 97.5497
3300 | 214.3343 | 2.8 | 43.3 | 0 | 0 | 107.1672 | 0 | 13.3 | 15.1 | 0 | 0 | 79.4745
3301 | 207.42 | 1.4 | 43.1 | 0 | 75.1 | 103.71 | 0 | 28.4 | 36.5 | 0 | 0 | 109.3277
3302 | 200.2378 | 2.1 | 43.2 | 0 | 37.6 | 100.1189 | 0.3 | 34.6 | 50.7 | 0 | 0 | 191.12
3303 | 186.8312 | 3.5 | 43.4 | 0 | 0 | 93.4156 | 0 | 47.9 | 56.7 | 0 | 0 | 115.6585
3304 | 149.3845 | 2.8 | 43.3 | 0 | 0 | 74.6923 | 0 | 62.4 | 63.6 | 0 | 0 | 113.323
3305 | 108.3678 | 2.1 | 43.2 | 0 | 0 | 54.1839 | 0 | 81.8 | 66.5 | 0 | 0 | 226.1055
3306 | 81.1216 | 0.7 | 43 | 0 | 37.6 | 40.5608 | 10 | 80.7 | 58.1 | 0 | 0 | 124.8046
3307 | 64.3182 | 0 | 42.9 | 0 | 75.1 | 32.1591 | 8.6 | 1.3 | 10.9 | 0 | 0 | 156.7328
3308 | 55.2865 | 0 | 42.9 | 0 | 75.1 | 27.6432 | 0 | 0 | 0 | 0 | 0 | 228.5111
3309 | 41.4475 | 0 | 42.9 | 0 | 75.1 | 20.7237 | 0 | 0 | 0 | 0 | 0 | 239.7107
3310 | 40.6361 | 0 | 42.9 | 0 | 93.9 | 20.3181 | 0 | 0 | 0 | 0 | 0 | 179.3544
3311 | 42.7169 | 0 | 0 | 0 | 0 | 21.3585 | 0 | 0 | 0 | 0 | 0 | 102.8219
3312 | 42.0401 | 0 | 0 | 0 | 0 | 21.02 | 0 | 0 | 0 | 0 | 0 | 93.9639
3313 | 42.4538 | 0 | 0 | 0 | 0 | 21.2269 | 0 | 0 | 0 | 0 | 0 | 76.149
3314 | 43.6365 | 0 | 0 | 0 | 0 | 21.8182 | 0 | 0 | 0 | 0 | 0 | 60.1272
3315 | 41.2185 | 0 | 0 | 0 | 0 | 20.6092 | 0 | 0 | 0 | 0 | 0 | 49.662
3316 | 42.5263 | 0 | 0 | 0 | 0 | 21.2632 | 0 | 0 | 0 | 0 | 0 | 55.0578
3317 | 44.1088 | 0 | 0 | 0 | 0 | 22.0544 | 0 | 0 | 0 | 0 | 0 | 55.6341
3318 | 48.7462 | 0 | 0 | 0 | 0 | 24.3731 | 0 | 0 | 0 | 0 | 0 | 68.2876
3319 | 59.9465 | 0 | 42.9 | 0 | 56.3 | 29.9732 | 0 | 0 | 0 | 0 | 0 | 55.5187
3320 | 62.1404 | 0 | 42.9 | 0 | 37.6 | 31.0702 | 0 | 0 | 0 | 0 | 0 | 58.9788
3321 | 58.2908 | 0 | 42.9 | 0 | 0 | 29.1454 | 0 | 0 | 0 | 0 | 0 | 48.8603
3322 | 56.0603 | 0 | 42.9 | 0 | 0 | 28.0302 | 0 | 0 | 0 | 0 | 0 | 56.3207
3323 | 51.8234 | 0 | 42.9 | 0 | 0 | 25.9117 | 0 | 0 | 4.2 | 0 | 0 | 66.1008
3324 | 55.6475 | 0 | 42.9 | 0 | 0 | 27.8238 | 0 | 1.6 | 21.8 | 0 | 0 | 157.7968
3325 | 53.2809 | 0 | 42.9 | 0 | 75.1 | 26.6405 | 0.8 | 12.3 | 48.3 | 0 | 0 | 133.1965
3326 | 51.2854 | 0 | 42.9 | 0 | 37.6 | 25.6427 | 3.9 | 20.8 | 77 | 0 | 0 | 101.622
3327 | 53.0104 | 0 | 42.9 | 0 | 0 | 26.5052 | 0 | 28.1 | 102.3 | 0 | 0 | 92.8877
3328 | 52.8873 | 0 | 42.9 | 0 | 0 | 26.4437 | 0 | 34.9 | 127.4 | 0 | 0 | 94.7995
3329 | 53.2834 | 0 | 42.9 | 0 | 0 | 26.6417 | 0 | 41.9 | 145.5 | 0 | 0 | 169.4722
3330 | 48.7728 | 0 | 42.9 | 0 | 37.6 | 24.3864 | 89 | 44.4 | 152.3 | 0 | 0 | 114.8952
3331 | 45.7492 | 0 | 42.9 | 0 | 75.1 | 22.8746 | 99.9 | 37.7 | 110 | 0 | 0 | 137.3381
3332 | 44.657 | 0 | 42.9 | 0 | 75.1 | 22.3285 | 37.8 | 3.6 | 27.8 | 0 | 0 | 171.9156
3333 | 43.9386 | 0 | 42.9 | 0 | 75.1 | 21.9693 | 11.9 | 0.5 | 9.5 | 0 | 0 | 183.1466
3334 | 44.746 | 0 | 42.9 | 0 | 93.9 | 22.373 | 4.9 | 0 | 1.2 | 0 | 0 | 139.9443
3335 | 40.558 | 0 | 0 | 0 | 0 | 20.279 | 0 | 0 | 0 | 0 | 0 | 146.5153
3336 | 41.2702 | 0 | 0 | 0 | 0 | 20.6351 | 0 | 0 | 0 | 0 | 0 | 121.2831
3337 | 43.2531 | 0 | 0 | 0 | 0 | 21.6265 | 0 | 0 | 0 | 0 | 0 | 53.6833
3338 | 42.848 | 0 | 0 | 0 | 0 | 21.424 | 0 | 0 | 0 | 0 | 0 | 51.9609
3339 | 43.6591 | 0 | 0 | 0 | 0 | 21.8295 | 0 | 0 | 0 | 0 | 0 | 47.7086
3340 | 40.4275 | 0 | 0 | 0 | 0 | 20.2138 | 0 | 0 | 0 | 0 | 0 | 47.7084
3341 | 39.9149 | 0 | 0 | 0 | 0 | 19.9575 | 0 | 0 | 0 | 0 | 0 | 55.4035
3342 | 51.5305 | 0 | 0 | 0 | 0 | 25.7653 | 0 | 0 | 0 | 0 | 0 | 58.9778
3343 | 71.095 | 0 | 42.9 | 0 | 56.3 | 35.5475 | 0 | 0 | 0 | 0 | 0 | 54.3698
3344 | 71.1099 | 0 | 42.9 | 0 | 37.6 | 35.5549 | 0 | 0 | 0 | 0 | 0 | 55.5172
3345 | 68.2415 | 0 | 42.9 | 0 | 0 | 34.1208 | 0 | 7.1 | 10.5 | 0 | 0 | 61.0479
3346 | 66.9544 | 0 | 42.9 | 0 | 0 | 33.4772 | 0 | 21.6 | 34.8 | 0 | 0 | 88.7215
3347 | 64.1744 | 0 | 42.9 | 0 | 0 | 32.0872 | 0 | 30.9 | 66.6 | 0 | 0 | 242.6852
3348 | 58.0271 | 0 | 42.9 | 0 | 0 | 29.0135 | 0 | 39.4 | 100.6 | 0 | 0 | 104.6152
3349 | 57.7463 | 0 | 42.9 | 0 | 75.1 | 28.8732 | 189.8 | 49.7 | 133.4 | 0 | 0 | 99.5928
3350 | 57.1382 | 0 | 42.9 | 0 | 37.6 | 28.5691 | 200.6 | 56.2 | 155.8 | 0 | 0 | 83.9718
3351 | 55.3528 | 0 | 42.9 | 0 | 0 | 27.6764 | 0 | 63.2 | 171.4 | 0 | 0 | 82.7916
3352 | 56.5423 | 0 | 42.9 | 0 | 0 | 28.2711 | 0 | 70.4 | 188.3 | 0 | 0 | 68.288
3353 | 58.4216 | 0 | 42.9 | 0 | 0 | 29.2108 | 0 | 73.1 | 200.8 | 0 | 0 | 50.5814
3354 | 55.0816 | 0 | 42.9 | 0 | 37.6 | 27.5408 | 391.2 | 70.8 | 210.5 | 0 | 0 | 129.0614
3355 | 49.3437 | 0 | 42.9 | 0 | 75.1 | 24.6718 | 398.2 | 61.4 | 194.4 | 0 | 0 | 175.6185
3356 | 46.1183 | 0 | 42.9 | 0 | 75.1 | 23.0592 | 283.2 | 24.1 | 88.4 | 0 | 0 | 173.5833
3357 | 43.3678 | 0 | 42.9 | 0 | 75.1 | 21.6839 | 194.1 | 18.1 | 62.7 | 0 | 0 | 154.0252
3358 | 41.2529 | 0 | 42.9 | 0 | 93.9 | 20.6264 | 149.9 | 11.7 | 43.5 | 0 | 0 | 150.8864
3359 | 41.9167 | 0 | 0 | 0 | 0 | 20.9584 | 0 | 5 | 0 | 0 | 0 | 153.5263
3360 | 42.2375 | 0 | 0 | 0 | 0 | 21.1187 | 0 | 0.4 | 0 | 0 | 0 | 102.0989
3361 | 42.3156 | 0 | 0 | 0 | 0 | 21.1578 | 0 | 0 | 0 | 0 | 0 | 64.9555
3362 | 42.2669 | 0 | 0 | 0 | 0 | 21.1335 | 0 | 0 | 0 | 0 | 0 | 67.024
3363 | 41.5752 | 0 | 0 | 0 | 0 | 20.7876 | 0 | 0 | 0 | 0 | 0 | 59.0933
3364 | 43.4149 | 0 | 0 | 0 | 0 | 21.7074 | 0 | 0 | 0 | 0 | 0 | 72.0871
3365 | 42.1566 | 0 | 0 | 0 | 0 | 21.0783 | 0 | 0 | 0 | 0 | 0 | 54.3693
3366 | 45.5654 | 0 | 0 | 0 | 0 | 22.7827 | 0 | 0 | 0 | 0 | 0 | 63.5788
3367 | 48.3479 | 0 | 42.9 | 0 | 56.3 | 24.174 | 5.4 | 11.7 | 0 | 0 | 0 | 57.5939
3368 | 56.1192 | 0.7 | 43 | 0 | 37.6 | 28.0596 | 6.2 | 140.2 | 7.7 | 0 | 0 | 99.7152
3369 | 55.7718 | 2.1 | 43.2 | 0 | 0 | 27.8859 | 0 | 145.9 | 28.2 | 0 | 0 | 71.8567
3370 | 56.0219 | 3.5 | 43.4 | 0 | 0 | 28.011 | 0 | 183.7 | 48.6 | 0 | 0 | 52.5341
3371 | 56.9861 | 3.5 | 43.4 | 0 | 0 | 28.493 | 0 | 196.9 | 53.4 | 0 | 0 | 88.0069
3372 | 55.165 | 2.8 | 43.3 | 0 | 0 | 27.5825 | 0 | 180.9 | 104.2 | 0 | 0 | 60.1275
3373 | 53.5047 | 1.4 | 43.1 | 0 | 75.1 | 26.7524 | 231.3 | 149.9 | 170.3 | 0 | 0 | 70.4743
3374 | 53.166 | 2.1 | 43.2 | 0 | 37.6 | 26.583 | 266.5 | 163.7 | 215.6 | 0 | 0 | 156.929
3375 | 58.8865 | 3.5 | 43.4 | 0 | 0 | 29.4433 | 0 | 187.2 | 228.5 | 0 | 0 | 259.3026
3376 | 60.3224 | 2.8 | 43.3 | 0 | 0 | 30.1612 | 0 | 162.2 | 202.5 | 0 | 0 | 96.3481
3377 | 62.971 | 2.1 | 43.2 | 0 | 0 | 31.4855 | 0 | 143 | 183.4 | 0 | 0 | 87.6418
3378 | 56.2791 | 0.7 | 43 | 0 | 37.6 | 28.1396 | 280 | 112.1 | 156.2 | 0 | 0 | 115.1354
3379 | 48.1675 | 0 | 42.9 | 0 | 75.1 | 24.0838 | 269.8 | 9.8 | 75.9 | 0 | 0 | 134.7734
3380 | 43.462 | 0 | 42.9 | 0 | 75.1 | 21.731 | 184.7 | 0 | 27.8 | 0 | 0 | 194.0389
3381 | 43.1229 | 0 | 42.9 | 0 | 75.1 | 21.5615 | 110.2 | 0 | 16.9 | 0 | 0 | 201.7274
3382 | 41.8036 | 0 | 42.9 | 0 | 93.9 | 20.9018 | 69.4 | 0 | 8.9 | 0 | 0 | 137.8428
3383 | 39.1156 | 0 | 0 | 0 | 0 | 19.5578 | 0 | 0 | 0 | 0 | 0 | 112.9659
3384 | 40.3693 | 0 | 0 | 0 | 0 | 20.1846 | 0 | 0 | 0 | 0 | 0 | 134.8316
3385 | 43.2999 | 0 | 0 | 0 | 0 | 21.6499 | 0 | 0 | 0 | 0 | 0 | 70.1287
3386 | 40.4322 | 0 | 0 | 0 | 0 | 20.2161 | 0 | 0 | 0 | 0 | 0 | 57.9386
3387 | 41.8622 | 0 | 0 | 0 | 0 | 20.9311 | 0 | 0 | 0 | 0 | 0 | 55.633
3388 | 42.8985 | 0 | 0 | 0 | 0 | 21.4493 | 0 | 0 | 0 | 0 | 0 | 53.2245
3389 | 40.2503 | 0 | 0 | 0 | 0 | 20.1251 | 0 | 0 | 0 | 0 | 0 | 58.2855
3390 | 62.0691 | 0 | 0 | 0 | 0 | 31.0346 | 0 | 0 | 0 | 0 | 0 | 58.7499
3391 | 88.2542 | 0 | 42.9 | 0 | 56.3 | 44.1271 | 0 | 0 | 0 | 0 | 0 | 52.0752
3392 | 119.7228 | 0.7 | 43 | 0 | 37.6 | 59.8614 | 0 | 30.4 | 0 | 0 | 0 | 76.7324
3393 | 161.2514 | 2.1 | 43.2 | 0 | 0 | 80.6257 | 0 | 22.9 | 0 | 0 | 0 | 59.3219
3394 | 197.9323 | 3.5 | 43.4 | 0 | 0 | 98.9662 | 0 | 32.2 | 4.6 | 0 | 0 | 49.2037
3395 | 208.8524 | 3.5 | 43.4 | 0 | 0 | 104.4262 | 0 | 39 | 15.8 | 0 | 0 | 60.3588
3396 | 212.406 | 2.8 | 43.3 | 0 | 0 | 106.203 | 0 | 54.4 | 33.4 | 0 | 0 | 62.7761
3397 | 223.9816 | 1.4 | 43.1 | 0 | 75.1 | 111.9908 | 34.5 | 47.9 | 64.7 | 0 | 0 | 105.4607
3398 | 228.2018 | 2.1 | 43.2 | 0 | 37.6 | 114.1009 | 50 | 48.9 | 89.5 | 0 | 0 | 166.6854
3399 | 212.384 | 3.5 | 43.4 | 0 | 0 | 106.192 | 0 | 61 | 114.6 | 0 | 0 | 170.2625
3400 | 176.1903 | 2.8 | 43.3 | 0 | 0 | 88.0952 | 0 | 56.9 | 142.7 | 0 | 0 | 177.8452
3401 | 134.41 | 2.1 | 43.2 | 0 | 0 | 67.205 | 0 | 67.7 | 162.6 | 0 | 0 | 122.442
3402 | 86.4129 | 0.7 | 43 | 0 | 37.6 | 43.2065 | 186.6 | 58.5 | 179.2 | 0 | 0 | 111.5086
3403 | 56.617 | 0 | 42.9 | 0 | 75.1 | 28.3085 | 230 | 0 | 119.6 | 0 | 0 | 159.3094
3404 | 44.1199 | 0 | 42.9 | 0 | 75.1 | 22.06 | 169.2 | 0 | 62.4 | 0 | 0 | 183.3055
3405 | 41.8634 | 0 | 42.9 | 0 | 75.1 | 20.9317 | 83.8 | 0 | 34.5 | 0 | 0 | 243.5239
3406 | 41.3303 | 0 | 42.9 | 0 | 93.9 | 20.6652 | 49.2 | 0 | 12.7 | 0 | 0 | 226.9423
3407 | 43.5165 | 0 | 0 | 0 | 0 | 21.7583 | 0 | 0 | 0 | 0 | 0 | 162.4913
3408 | 42.6565 | 0 | 0 | 0 | 0 | 21.3282 | 0 | 0 | 0 | 0 | 0 | 120.5367
3409 | 44.2591 | 0 | 0 | 0 | 0 | 22.1296 | 0 | 0 | 0 | 0 | 0 | 102.5768
3410 | 41.9567 | 0 | 0 | 0 | 0 | 20.9783 | 0 | 0 | 0 | 0 | 0 | 79.5986
3411 | 43.0482 | 0 | 0 | 0 | 0 | 21.5241 | 0 | 0 | 0 | 0 | 0 | 63.3483
3412 | 42.4051 | 0 | 0 | 0 | 0 | 21.2026 | 0 | 0 | 0 | 0 | 0 | 51.0416
3413 | 43.2515 | 0 | 0 | 0 | 0 | 21.6258 | 0 | 0 | 0 | 0 | 0 | 54.0255
3414 | 55.9013 | 0 | 0 | 0 | 0 | 27.9507 | 0 | 0 | 0 | 0 | 0 | 66.1012
3415 | 85.6905 | 0 | 42.9 | 0 | 56.3 | 42.8452 | 0 | 0 | 0 | 0 | 0 | 51.7299
3416 | 155.1673 | 0.7 | 43 | 0 | 37.6 | 77.5837 | 0 | 5.7 | 0 | 0 | 0 | 51.8437
3417 | 240.2448 | 2.1 | 43.2 | 0 | 0 | 120.1224 | 0 | 9.9 | 0.2 | 0 | 0 | 67.2558
3418 | 293.13 | 3.5 | 43.4 | 0 | 0 | 146.565 | 0 | 22.6 | 5.3 | 0 | 0 | 57.9383
3419 | 280.6835 | 3.5 | 43.4 | 0 | 0 | 140.3417 | 0 | 36.4 | 15 | 0 | 0 | 112.3596
3420 | 249.4365 | 2.8 | 43.3 | 0 | 0 | 124.7182 | 0 | 61.1 | 22.5 | 0 | 0 | 239.3975
3421 | 240.2569 | 1.4 | 43.1 | 0 | 75.1 | 120.1284 | 18.4 | 67.3 | 51 | 0 | 0 | 118.6803
3422 | 223.0497 | 2.1 | 43.2 | 0 | 37.6 | 111.5248 | 15.8 | 79.1 | 61 | 0 | 0 | 162.005
3423 | 207.1147 | 3.5 | 43.4 | 0 | 0 | 103.5573 | 0 | 108.4 | 74.2 | 0 | 0 | 57.9377
3424 | 169.2031 | 2.8 | 43.3 | 0 | 0 | 84.6016 | 0 | 120 | 78.1 | 0 | 0 | 61.7418
3425 | 113.1837 | 2.1 | 43.2 | 0 | 0 | 56.5918 | 0 | 125.5 | 87.6 | 0 | 0 | 114.0405
3426 | 76.9606 | 0.7 | 43 | 0 | 37.6 | 38.4803 | 34.2 | 107.8 | 83 | 0 | 0 | 75.3237
3427 | 55.9782 | 0 | 42.9 | 0 | 75.1 | 27.9891 | 44.4 | 18.7 | 15.4 | 0 | 0 | 118.4163
3428 | 43.9089 | 0 | 42.9 | 0 | 75.1 | 21.9544 | 12.2 | 0.5 | 0 | 0 | 0 | 183.2391
3429 | 43.7406 | 0 | 42.9 | 0 | 75.1 | 21.8703 | 0 | 0 | 0 | 0 | 0 | 353.3813
3430 | 39.8384 | 0 | 42.9 | 0 | 93.9 | 19.9192 | 0 | 0 | 0 | 0 | 0 | 164.4393
3431 | 43.5429 | 0 | 0 | 0 | 0 | 21.7714 | 0 | 0 | 0 | 0 | 0 | 110.7787
3432 | 42.3825 | 0 | 0 | 0 | 0 | 21.1913 | 0 | 0 | 0 | 0 | 0 | 76.4981
3433 | 42.1749 | 0 | 0 | 0 | 0 | 21.0874 | 0 | 0 | 0 | 0 | 0 | 49.5479
3434 | 42.045 | 0 | 0 | 0 | 0 | 21.0225 | 0 | 0 | 0 | 0 | 0 | 53.6839
3435 | 42.1089 | 0 | 0 | 0 | 0 | 21.0544 | 0 | 0 | 0 | 0 | 0 | 57.9373
3436 | 43.6204 | 0 | 0 | 0 | 0 | 21.8102 | 0 | 0 | 0 | 0 | 0 | 53.4525
3437 | 46.0368 | 0 | 0 | 0 | 0 | 23.0184 | 0 | 0 | 0 | 0 | 0 | 51.9601
3438 | 59.3378 | 0 | 0 | 0 | 0 | 29.6689 | 0 | 0 | 0 | 0 | 0 | 58.0552
3439 | 102.5406 | 0 | 42.9 | 0 | 56.3 | 51.2703 | 0 | 0 | 0 | 0 | 0 | 55.6347
3440 | 187.6438 | 0.7 | 43 | 0 | 37.6 | 93.8219 | 0 | 19.6 | 0 | 0 | 0 | 76.3809
3441 | 246.7067 | 2.1 | 43.2 | 0 | 0 | 123.3533 | 0 | 21.9 | 0 | 0 | 0 | 146.2785
3442 | 277.9918 | 3.5 | 43.4 | 0 | 0 | 138.9959 | 0 | 30.5 | 0 | 0 | 0 | 89.9024
3443 | 290.7312 | 3.5 | 43.4 | 0 | 0 | 145.3656 | 0 | 43.3 | 0 | 0 | 0 | 62.5461
3444 | 303.0999 | 2.8 | 43.3 | 0 | 0 | 151.5499 | 0 | 68.2 | 0 | 0 | 0 | 70.7053
3445 | 277.6909 | 1.4 | 43.1 | 0 | 75.1 | 138.8454 | 0 | 77.3 | 0 | 0 | 0 | 191.4581
3446 | 260.422 | 2.1 | 43.2 | 0 | 37.6 | 130.211 | 0 | 85.1 | 0.3 | 0 | 0 | 248.2858
3447 | 255.2512 | 3.5 | 43.4 | 0 | 0 | 127.6256 | 0 | 105 | 4.8 | 0 | 0 | 193.5352
3448 | 221.8785 | 2.8 | 43.3 | 0 | 0 | 110.9392 | 0 | 114 | 12.1 | 0 | 0 | 115.2581
3449 | 164.7297 | 2.1 | 43.2 | 0 | 0 | 82.3648 | 0 | 122.3 | 26.1 | 0 | 0 | 89.7825
3450 | 112.9537 | 0.7 | 43 | 0 | 37.6 | 56.4769 | 0 | 108.5 | 36 | 0 | 0 | 121.0759
3451 | 92.6095 | 0 | 42.9 | 0 | 75.1 | 46.3047 | 1.1 | 18.5 | 15 | 0 | 0 | 173.1892
3452 | 71.5044 | 0 | 42.9 | 0 | 75.1 | 35.7522 | 0 | 0.4 | 0 | 0 | 0 | 149.6247
3453 | 64.2882 | 0 | 42.9 | 0 | 75.1 | 32.1441 | 0 | 0 | 0 | 0 | 0 | 147.8065
3454 | 56.4868 | 0 | 42.9 | 0 | 93.9 | 28.2434 | 0 | 0 | 0 | 0 | 0 | 176.9646
3455 | 42.4194 | 0 | 0 | 0 | 0 | 21.2097 | 0 | 0 | 0 | 0 | 0 | 112.3605
3456 | 41.9623 | 0 | 0 | 0 | 0 | 20.9811 | 0 | 0 | 0 | 0 | 0 | 85.0425
3457 | 41.9678 | 0 | 0 | 0 | 0 | 20.9839 | 0 | 0 | 0 | 0 | 0 | 54.3695
3458 | 42.1451 | 0 | 0 | 0 | 0 | 21.0726 | 0 | 0 | 0 | 0 | 0 | 54.7128
3459 | 43.8915 | 0 | 0 | 0 | 0 | 21.9458 | 0 | 0 | 0 | 0 | 0 | 47.9393
3460 | 43.201 | 0 | 0 | 0 | 0 | 21.6005 | 0 | 0 | 0 | 0 | 0 | 48.2843
3461 | 42.7848 | 0 | 0 | 0 | 0 | 21.3924 | 0 | 0 | 0 | 0 | 0 | 54.8284
3462 | 54.8113 | 0 | 0 | 0 | 0 | 27.4057 | 0 | 0 | 0 | 0 | 0 | 48.8596
3463 | 92.7914 | 0 | 42.9 | 0 | 56.3 | 46.3957 | 0 | 0 | 0 | 0 | 0 | 65.9854
3464 | 145.2446 | 0.7 | 43 | 0 | 37.6 | 72.6223 | 0 | 27.6 | 0 | 0 | 0 | 98.1561
3465 | 199.8244 | 2.1 | 43.2 | 0 | 0 | 99.9122 | 0 | 18.4 | 0 | 0 | 0 | 86.1074
3466 | 251.2517 | 3.5 | 43.4 | 0 | 0 | 125.6258 | 0 | 26.1 | 0 | 0 | 0 | 100.7829
3467 | 275.9339 | 3.5 | 43.4 | 0 | 0 | 137.967 | 0 | 31.1 | 0 | 0 | 0 | 61.97
3468 | 274.6245 | 2.8 | 43.3 | 0 | 0 | 137.3122 | 0 | 44.4 | 0 | 0 | 0 | 56.2063
3469 | 246.659 | 1.4 | 43.1 | 0 | 75.1 | 123.3295 | 0 | 43.8 | 8.1 | 0 | 0 | 140.4178
3470 | 256.3648 | 2.1 | 43.2 | 0 | 37.6 | 128.1824 | 0 | 42.5 | 24.6 | 0 | 0 | 148.4714
3471 | 243.989 | 3.5 | 43.4 | 0 | 0 | 121.9945 | 0 | 50.3 | 51.6 | 0 | 0 | 151.7833
3472 | 228.2155 | 2.8 | 43.3 | 0 | 0 | 114.1077 | 0 | 49.1 | 73 | 0 | 0 | 122.9515
3473 | 181.4103 | 2.1 | 43.2 | 0 | 0 | 90.7052 | 0 | 55.4 | 116.6 | 0 | 0 | 84.3285
3474 | 139.2082 | 0.7 | 43 | 0 | 37.6 | 69.6041 | 21.5 | 46.6 | 154.8 | 0 | 0 | 130.9537
3475 | 108.6012 | 0 | 42.9 | 0 | 75.1 | 54.3006 | 51.9 | 0 | 96.7 | 0 | 0 | 207.8889
3476 | 85.8857 | 0 | 42.9 | 0 | 75.1 | 42.9429 | 24 | 0 | 38.2 | 0 | 0 | 192.0044
3477 | 63.2403 | 0 | 42.9 | 0 | 75.1 | 31.6202 | 1.2 | 0 | 16 | 0 | 0 | 167.8953
3478 | 61.6833 | 0 | 42.9 | 0 | 93.9 | 30.8416 | 0 | 0 | 1.3 | 0 | 0 | 150.2231
3479 | 59.89 | 0 | 0 | 0 | 0 | 29.945 | 0 | 0 | 0 | 0 | 0 | 117.8942
3480 | 59.709 | 0 | 0 | 0 | 0 | 29.8545 | 0 | 0 | 0 | 0 | 0 | 88.716
3481 | 59.1794 | 0 | 0 | 0 | 0 | 29.5897 | 0 | 0 | 0 | 0 | 0 | 69.2085
3482 | 60.1222 | 0 | 0 | 0 | 0 | 30.0611 | 0 | 0 | 0 | 0 | 0 | 53.4522
3483 | 58.3547 | 0 | 0 | 0 | 0 | 29.1773 | 0 | 0 | 0 | 0 | 0 | 46.9051
3484 | 45.3792 | 0 | 0 | 0 | 0 | 22.6896 | 0 | 0 | 0 | 0 | 0 | 48.1691
3485 | 43.0637 | 0 | 0 | 0 | 0 | 21.5319 | 0 | 0 | 0 | 0 | 0 | 54.9444
3486 | 40.5301 | 0 | 0 | 0 | 0 | 20.2651 | 0 | 0 | 0 | 0 | 0 | 48.1696
3487 | 45.2366 | 0 | 42.9 | 0 | 56.3 | 22.6183 | 0 | 0 | 0 | 0 | 0 | 61.1643
3488 | 51.8944 | 0 | 42.9 | 0 | 37.6 | 25.9472 | 0 | 0 | 0 | 0 | 0 | 94.081
3489 | 51.4391 | 0 | 42.9 | 0 | 0 | 25.7195 | 0 | 0 | 0.7 | 0 | 0 | 71.0502
3490 | 59.3399 | 0 | 42.9 | 0 | 0 | 29.67 | 0 | 0 | 20.2 | 0 | 0 | 84.0885
3491 | 64.4967 | 0 | 42.9 | 0 | 0 | 32.2484 | 0 | 0 | 59.4 | 0 | 0 | 139.6531
3492 | 75.1677 | 0 | 42.9 | 0 | 0 | 37.5838 | 0 | 0 | 101.3 | 0 | 0 | 160.3812
3493 | 79.6206 | 0 | 42.9 | 0 | 75.1 | 39.8103 | 78.5 | 0 | 135.6 | 0 | 0 | 163.1005
3494 | 84.0922 | 0 | 42.9 | 0 | 37.6 | 42.0461 | 92.7 | 0 | 165.8 | 0 | 0 | 106.4266
3495 | 82.4648 | 0 | 42.9 | 0 | 0 | 41.2324 | 0 | 0 | 197.9 | 0 | 0 | 67.9432
3496 | 81.2725 | 0 | 42.9 | 0 | 0 | 40.6363 | 0 | 0 | 209.4 | 0 | 0 | 55.0587
3497 | 80.4125 | 0 | 42.9 | 0 | 0 | 40.2062 | 0 | 0 | 210.5 | 0 | 0 | 119.9183
3498 | 79.581 | 0 | 42.9 | 0 | 37.6 | 39.7905 | 254.6 | 0 | 211.5 | 0 | 0 | 133.4007
3499 | 73.508 | 0 | 42.9 | 0 | 75.1 | 36.754 | 268.5 | 0 | 148 | 0 | 0 | 263.9437
3500 | 66.2664 | 0 | 42.9 | 0 | 75.1 | 33.1332 | 186.9 | 0 | 69.8 | 0 | 0 | 236.902
3501 | 66.4477 | 0 | 42.9 | 0 | 75.1 | 33.2238 | 91 | 0 | 43.9 | 0 | 0 | 189.5053
3502 | 64.612 | 0 | 42.9 | 0 | 93.9 | 32.306 | 51 | 0 | 21.1 | 0 | 0 | 169.3834
3503 | 65.1463 | 0 | 0 | 0 | 0 | 32.5732 | 0 | 0 | 0 | 0 | 0 | 117.824
3504 | 51.872 | 0 | 0 | 0 | 0 | 25.936 | 0 | 0 | 0 | 0 | 0 | 82.5559
3505 | 44.0555 | 0 | 0 | 0 | 0 | 22.0277 | 0 | 0 | 0 | 0 | 0 | 60.5888
3506 | 43.5079 | 0 | 0 | 0 | 0 | 21.7539 | 0 | 0 | 0 | 0 | 0 | 53.5689
3507 | 43.3492 | 0 | 0 | 0 | 0 | 21.6746 | 0 | 0 | 0 | 0 | 0 | 47.5928
3508 | 43.4951 | 0 | 0 | 0 | 0 | 21.7476 | 0 | 0 | 0 | 0 | 0 | 51.9606
3509 | 46.4772 | 0 | 0 | 0 | 0 | 23.2386 | 0 | 0 | 0 | 0 | 0 | 59.7823
3510 | 53.3442 | 0 | 0 | 0 | 0 | 26.6721 | 0 | 0 | 0 | 0 | 0 | 75.6748
3511 | 58.9875 | 0 | 42.9 | 0 | 56.3 | 29.4938 | 7 | 0 | 0.6 | 0 | 0 | 96.5901
3512 | 53.8122 | 0 | 42.9 | 0 | 37.6 | 26.9061 | 1.8 | 0 | 0.7 | 0 | 0 | 56.9006
3513 | 53.2868 | 0 | 42.9 | 0 | 0 | 26.6434 | 0 | 0 | 15.7 | 0 | 0 | 54.4846
3514 | 59.8315 | 0 | 42.9 | 0 | 0 | 29.9157 | 0 | 0 | 48.3 | 0 | 0 | 72.4347
3515 | 69.1815 | 0 | 42.9 | 0 | 0 | 34.5908 | 0 | 0 | 80.9 | 0 | 0 | 73.5863
3516 | 75.1054 | 0 | 42.9 | 0 | 0 | 37.5527 | 0 | 0 | 128 | 0 | 0 | 110.5359
3517 | 78.31 | 0 | 42.9 | 0 | 75.1 | 39.155 | 356.3 | 0 | 167.7 | 0 | 0 | 159.4216
3518 | 79.8999 | 0 | 42.9 | 0 | 37.6 | 39.9499 | 293.9 | 0 | 164.8 | 0 | 0 | 169.105
3519 | 81.1049 | 0 | 42.9 | 0 | 0 | 40.5524 | 0 | 0 | 171.3 | 0 | 0 | 116.8044
3520 | 84.4818 | 0 | 42.9 | 0 | 0 | 42.2409 | 0 | 0.2 | 194.6 | 0 | 0 | 136.5481
3521 | 81.2499 | 0 | 42.9 | 0 | 0 | 40.625 | 0 | 5.6 | 218 | 0 | 0 | 97.6709
3522 | 81.1275 | 0 | 42.9 | 0 | 37.6 | 40.5637 | 543.3 | 7.3 | 257.4 | 0 | 0 | 103.7748
3523 | 78.1271 | 0 | 42.9 | 0 | 75.1 | 39.0636 | 565.8 | 0.6 | 251.9 | 0 | 0 | 124.736
3524 | 68.9091 | 0 | 42.9 | 0 | 75.1 | 34.4545 | 451.1 | 0 | 155.1 | 0 | 0 | 150.8671
3525 | 65.1274 | 0 | 42.9 | 0 | 75.1 | 32.5637 | 327 | 0 | 106.9 | 0 | 0 | 173.643
3526 | 65.9726 | 0 | 42.9 | 0 | 93.9 | 32.9863 | 277.4 | 0 | 77.1 | 0 | 0 | 160.5883
3527 | 63.5357 | 0 | 0 | 0 | 0 | 31.7678 | 0 | 0 | 0 | 0 | 0 | 134.389
3528 | 58.6832 | 0 | 0 | 0 | 0 | 29.3416 | 0 | 0 | 0 | 0 | 0 | 97.4307
3529 | 42.0624 | 0 | 0 | 0 | 0 | 21.0312 | 0 | 0 | 0 | 0 | 0 | 130.1504
3530 | 42.5806 | 0 | 0 | 0 | 0 | 21.2903 | 0 | 0 | 0 | 0 | 0 | 86.8173
3531 | 41.6102 | 0 | 0 | 0 | 0 | 20.8051 | 0 | 0 | 0 | 0 | 0 | 59.7816
3532 | 40.4895 | 0 | 0 | 0 | 0 | 20.2448 | 0 | 0 | 0 | 0 | 0 | 49.5486
3533 | 42.3661 | 0 | 0 | 0 | 0 | 21.183 | 0 | 0 | 0 | 0 | 0 | 62.8896
3534 | 51.6191 | 0 | 0 | 0 | 0 | 25.8096 | 0 | 0 | 0 | 0 | 0 | 82.0798
3535 | 97.4046 | 0 | 42.9 | 0 | 56.3 | 48.7023 | 100.5 | 0 | 4 | 0 | 0 | 59.3232
3536 | 159.3993 | 0.7 | 43 | 0 | 37.6 | 79.6997 | 95.8 | 31.6 | 42.2 | 0 | 0 | 50.2376
3537 | 256.1819 | 2.1 | 43.2 | 0 | 0 | 128.091 | 0 | 34.4 | 60.6 | 0 | 0 | 79.004
3538 | 275.7675 | 3.5 | 43.4 | 0 | 0 | 137.8837 | 0 | 68.8 | 106.4 | 0 | 0 | 117.0588
3539 | 265.2915 | 3.5 | 43.4 | 0 | 0 | 132.6457 | 0 | 87.1 | 177.2 | 0 | 0 | 341.988
3540 | 231.9621 | 2.8 | 43.3 | 0 | 0 | 115.9811 | 0 | 92.3 | 238.3 | 0 | 0 | 181.5651
3541 | 210.5579 | 1.4 | 43.1 | 0 | 75.1 | 105.279 | 533.7 | 70.7 | 280.7 | 0 | 0 | 131.4176
3542 | 216.9929 | 2.1 | 43.2 | 0 | 37.6 | 108.4964 | 482 | 77.6 | 310.8 | 0 | 0 | 184.9261
3543 | 214.719 | 3.5 | 43.4 | 0 | 0 | 107.3595 | 0.3 | 110.1 | 337.5 | 0 | 0 | 304.3972
3544 | 187.9943 | 2.8 | 43.3 | 0 | 0 | 93.9972 | 6.9 | 114.8 | 341.8 | 0 | 0 | 96.9511
3545 | 143.593 | 2.1 | 43.2 | 0 | 0 | 71.7965 | 17.3 | 102.4 | 338.9 | 0 | 0 | 141.6227
3546 | 110.0922 | 0.7 | 43 | 0 | 37.6 | 55.0461 | 697.5 | 71 | 346.5 | 0 | 0 | 156.8608
3547 | 89.7768 | 0 | 42.9 | 0 | 75.1 | 44.8884 | 698.1 | 0 | 244.6 | 0 | 0 | 259.9922
3548 | 73.4045 | 0 | 42.9 | 0 | 75.1 | 36.7023 | 594.4 | 0 | 163.8 | 0 | 0 | 455.6794
3549 | 69.2107 | 0 | 42.9 | 0 | 75.1 | 34.6053 | 462.9 | 0 | 122.2 | 0 | 0 | 225.4963
3550 | 64.4549 | 0 | 42.9 | 0 | 93.9 | 32.2274 | 401.4 | 0 | 87 | 0 | 0 | 149.2437
3551 | 66.1663 | 0 | 0 | 0 | 0 | 33.0831 | 0 | 0 | 0 | 0 | 0 | 130.0082
3552 | 61.025 | 0 | 0 | 0 | 0 | 30.5125 | 0 | 0 | 0 | 0 | 0 | 78.0442
3553 | 63.1185 | 0 | 0 | 0 | 0 | 31.5593 | 0 | 0 | 0 | 0 | 0 | 56.7847
3554 | 61.2057 | 0 | 0 | 0 | 0 | 30.6028 | 0 | 0 | 0 | 0 | 0 | 61.9693
3555 | 65.7281 | 0 | 0 | 0 | 0 | 32.864 | 0 | 0 | 0 | 0 | 0 | 45.8803
3556 | 60.4761 | 0 | 0 | 0 | 0 | 30.2381 | 0 | 0 | 0 | 0 | 0 | 44.9768
3557 | 63.7638 | 0 | 0 | 0 | 0 | 31.8819 | 0 | 0 | 0 | 0 | 0 | 53.4533
3558 | 75.0831 | 0 | 0 | 0 | 0 | 37.5415 | 0 | 0 | 0 | 0 | 0 | 119.2577
3559 | 109.3546 | 0 | 42.9 | 0 | 56.3 | 54.6773 | 65.1 | 0 | 0 | 0 | 0 | 84.5648
3560 | 161.089 | 0.7 | 43 | 0 | 37.6 | 80.5445 | 26.4 | 27.1 | 3.4 | 0 | 0 | 62.4292
3561 | 251.7903 | 2.1 | 43.2 | 0 | 0 | 125.8952 | 0 | 32.1 | 9.5 | 0 | 0 | 99.3496
3562 | 244.7092 | 3.5 | 43.4 | 0 | 0 | 122.3546 | 0 | 54.7 | 14.6 | 0 | 0 | 73.7022
3563 | 229.8075 | 3.5 | 43.4 | 0 | 0 | 114.9038 | 0 | 61.3 | 22 | 0 | 0 | 107.393
3564 | 210.5846 | 2.8 | 43.3 | 0 | 0 | 105.2923 | 0 | 82.4 | 24.3 | 0 | 0 | 183.7315
3565 | 200.4449 | 1.4 | 43.1 | 0 | 75.1 | 100.2224 | 100.7 | 79.4 | 49.6 | 0 | 0 | 164.8912
3566 | 209.3248 | 2.1 | 43.2 | 0 | 37.6 | 104.6624 | 113.1 | 87.6 | 78.4 | 0 | 0 | 218.4825
3567 | 207.3478 | 3.5 | 43.4 | 0 | 0 | 103.6739 | 0 | 97.2 | 87 | 0 | 0 | 179.5651
3568 | 185.6141 | 2.8 | 43.3 | 0 | 0 | 92.8071 | 0 | 76.5 | 97.3 | 0 | 0 | 170.3227
3569 | 132.2802 | 2.1 | 43.2 | 0 | 0 | 66.1401 | 0 | 67.8 | 115.9 | 0 | 0 | 233.0363
3570 | 98.8008 | 0.7 | 43 | 0 | 37.6 | 49.4004 | 199.1 | 52.8 | 128.2 | 0 | 0 | 132.9389
3571 | 75.521 | 0 | 42.9 | 0 | 75.1 | 37.7605 | 216.5 | 0 | 60 | 0 | 0 | 193.0632
3572 | 57.8774 | 0 | 42.9 | 0 | 75.1 | 28.9387 | 133.8 | 0 | 15.4 | 0 | 0 | 201.967
3573 | 50.3627 | 0 | 42.9 | 0 | 75.1 | 25.1814 | 64.2 | 0 | 7 | 0 | 0 | 214.9087
3574 | 45.787 | 0 | 42.9 | 0 | 93.9 | 22.8935 | 32.1 | 0 | 0.7 | 0 | 0 | 225.4239
3575 | 44.6202 | 0 | 0 | 0 | 0 | 22.3101 | 0 | 0 | 0 | 0 | 0 | 159.2645
3576 | 40.8174 | 0 | 0 | 0 | 0 | 20.4087 | 0 | 0 | 0 | 0 | 0 | 111.9989
3577 | 43.1505 | 0 | 0 | 0 | 0 | 21.5753 | 0 | 0 | 0 | 0 | 0 | 57.131
3578 | 40.5667 | 0 | 0 | 0 | 0 | 20.2833 | 0 | 0 | 0 | 0 | 0 | 57.2484
3579 | 40.1415 | 0 | 0 | 0 | 0 | 20.0707 | 0 | 0 | 0 | 0 | 0 | 57.4776
3580 | 40.3392 | 0 | 0 | 0 | 0 | 20.1696 | 0 | 0 | 0 | 0 | 0 | 58.7503
3581 | 43.8794 | 0 | 0 | 0 | 0 | 21.9397 | 0 | 0 | 0 | 0 | 0 | 52.1909
3582 | 64.0325 | 0 | 0 | 0 | 0 | 32.0162 | 0 | 0 | 0 | 0 | 0 | 49.2056
3583 | 116.4057 | 0 | 42.9 | 0 | 56.3 | 58.2028 | 0 | 0 | 0 | 0 | 0 | 47.5935
3584 | 185.3482 | 0.7 | 43 | 0 | 37.6 | 92.6741 | 0 | 0 | 0 | 0 | 0 | 49.7783
3585 | 282.5622 | 2.1 | 43.2 | 0 | 0 | 141.2811 | 0 | 0 | 0 | 0 | 0 | 80.1852
3586 | 341.6353 | 3.5 | 43.4 | 0 | 0 | 170.8177 | 0 | 0 | 0 | 0 | 0 | 70.8211
3587 | 333.1335 | 3.5 | 43.4 | 0 | 0 | 166.5668 | 0 | 0.6 | 0 | 0 | 0 | 69.3226
3588 | 299.8348 | 2.8 | 43.3 | 0 | 0 | 149.9174 | 0 | 13.9 | 0 | 0 | 0 | 116.0835
3589 | 301.5874 | 1.4 | 43.1 | 0 | 75.1 | 150.7937 | 0 | 24.2 | 0 | 0 | 0 | 179.3069
3590 | 261.8191 | 2.1 | 43.2 | 0 | 37.6 | 130.9096 | 0 | 22.8 | 3.7 | 0 | 0 | 120.9451
3591 | 233.6019 | 3.5 | 43.4 | 0 | 0 | 116.801 | 0 | 25.3 | 18.6 | 0 | 0 | 172.2029
3592 | 197.7907 | 2.8 | 43.3 | 0 | 0 | 98.8953 | 0 | 20.1 | 55.7 | 0 | 0 | 289.6818
3593 | 146.337 | 2.1 | 43.2 | 0 | 0 | 73.1685 | 0 | 28.8 | 98.9 | 0 | 0 | 97.7966
3594 | 118.3396 | 0.7 | 43 | 0 | 37.6 | 59.1698 | 50.4 | 25.2 | 106.6 | 0 | 0 | 107.3921
3595 | 100.1716 | 0 | 42.9 | 0 | 75.1 | 50.0858 | 69.3 | 0 | 44.9 | 0 | 0 | 88.7209
3596 | 81.3757 | 0 | 42.9 | 0 | 75.1 | 40.6879 | 32.5 | 0 | 4.8 | 0 | 0 | 151.2493
3597 | 64.6133 | 0 | 42.9 | 0 | 75.1 | 32.3066 | 6.8 | 0 | 0.1 | 0 | 0 | 245.5118
3598 | 65.5021 | 0 | 42.9 | 0 | 93.9 | 32.7511 | 0.5 | 0 | 0 | 0 | 0 | 156.9651
3599 | 63.4616 | 0 | 0 | 0 | 0 | 31.7308 | 0 | 0 | 0 | 0 | 0 | 122.7959
3600 | 62.6456 | 0 | 0 | 0 | 0 | 31.3228 | 0 | 0 | 0 | 0 | 0 | 76.8542
3601 | 62.5644 | 0 | 0 | 0 | 0 | 31.2822 | 0 | 0 | 0 | 0 | 0 | 51.9583
3602 | 59.7738 | 0 | 0 | 0 | 0 | 29.8869 | 0 | 0 | 0 | 0 | 0 | 47.7107
3603 | 60.5942 | 0 | 0 | 0 | 0 | 30.2971 | 0 | 0 | 0 | 0 | 0 | 47.5956
3604 | 57.8297 | 0 | 0 | 0 | 0 | 28.9148 | 0 | 0 | 0 | 0 | 0 | 47.3634
3605 | 59.3393 | 0 | 0 | 0 | 0 | 29.6697 | 0 | 0 | 0 | 0 | 0 | 54.5991
3606 | 68.1628 | 0 | 0 | 0 | 0 | 34.0814 | 0 | 0 | 0 | 0 | 0 | 53.5677
3607 | 111.4416 | 0 | 42.9 | 0 | 56.3 | 55.7208 | 0 | 0 | 0 | 0 | 0 | 70.8215
3608 | 155.9583 | 0.7 | 43 | 0 | 37.6 | 77.9791 | 0 | 0 | 3.7 | 0 | 0 | 91.6987
3609 | 220.3775 | 2.1 | 43.2 | 0 | 0 | 110.1888 | 0 | 0 | 15.7 | 0 | 0 | 75.0911
3610 | 238.9747 | 3.5 | 43.4 | 0 | 0 | 119.4874 | 0 | 0 | 36.9 | 0 | 0 | 68.746
3611 | 244.893 | 3.5 | 43.4 | 0 | 0 | 122.4465 | 0 | 0.6 | 47.1 | 0 | 0 | 65.7565
3612 | 231.5936 | 2.8 | 43.3 | 0 | 0 | 115.7968 | 0 | 8.8 | 65 | 0 | 0 | 115.9637
3613 | 223.4098 | 1.4 | 43.1 | 0 | 75.1 | 111.7049 | 30.3 | 4 | 72.5 | 0 | 0 | 83.9713
3614 | 217.027 | 2.1 | 43.2 | 0 | 37.6 | 108.5135 | 23.4 | 1.8 | 78.3 | 0 | 0 | 108.6063
3615 | 204.0418 | 3.5 | 43.4 | 0 | 0 | 102.0209 | 0 | 7.3 | 89.2 | 0 | 0 | 76.0314
3616 | 176.0986 | 2.8 | 43.3 | 0 | 0 | 88.0493 | 0 | 7.3 | 75.5 | 0 | 0 | 113.7986
3617 | 127.2725 | 2.1 | 43.2 | 0 | 0 | 63.6362 | 0 | 10.6 | 91.8 | 0 | 0 | 75.7914
3618 | 105.2813 | 0.7 | 43 | 0 | 37.6 | 52.6406 | 42 | 7.2 | 99.3 | 0 | 0 | 168.0823
3619 | 81.1287 | 0 | 42.9 | 0 | 75.1 | 40.5644 | 55 | 0 | 31.8 | 0 | 0 | 168.6963
3620 | 70.1584 | 0 | 42.9 | 0 | 75.1 | 35.0792 | 11.8 | 0 | 0 | 0 | 0 | 141.9543
3621 | 66.2528 | 0 | 42.9 | 0 | 75.1 | 33.1264 | 0 | 0 | 0 | 0 | 0 | 127.586
3622 | 62.2132 | 0 | 42.9 | 0 | 93.9 | 31.1066 | 0 | 0 | 0 | 0 | 0 | 119.738
3623 | 60.0379 | 0 | 0 | 0 | 0 | 30.0189 | 0 | 0 | 0 | 0 | 0 | 91.6974
3624 | 58.7852 | 0 | 0 | 0 | 0 | 29.3926 | 0 | 0 | 0 | 0 | 0 | 73.4716
3625 | 47.892 | 0 | 0 | 0 | 0 | 23.946 | 0 | 0 | 0 | 0 | 0 | 60.7035
3626 | 43.6721 | 0 | 0 | 0 | 0 | 21.8361 | 0 | 0 | 0 | 0 | 0 | 52.5371
3627 | 41.7927 | 0 | 0 | 0 | 0 | 20.8964 | 0 | 0 | 0 | 0 | 0 | 46.6777
3628 | 40.7195 | 0 | 0 | 0 | 0 | 20.3597 | 0 | 0 | 0 | 0 | 0 | 46.5632
3629 | 41.0861 | 0 | 0 | 0 | 0 | 20.5431 | 0 | 0 | 0 | 0 | 0 | 57.8229
3630 | 52.7742 | 0 | 0 | 0 | 0 | 26.3871 | 0 | 0 | 0 | 0 | 0 | 50.352
3631 | 86.9398 | 0 | 42.9 | 0 | 56.3 | 43.4699 | 0 | 0 | 0 | 0 | 0 | 51.1558
3632 | 123.3739 | 0.7 | 43 | 0 | 37.6 | 61.687 | 0 | 0 | 0 | 0 | 0 | 63.1182
3633 | 207.7869 | 2.1 | 43.2 | 0 | 0 | 103.8935 | 0 | 0 | 0 | 0 | 0 | 96.7147
3634 | 272.9549 | 3.5 | 43.4 | 0 | 0 | 136.4775 | 0 | 0 | 0.8 | 0 | 0 | 121.8171
3635 | 270.9913 | 3.5 | 43.4 | 0 | 0 | 135.4956 | 0 | 0.7 | 15 | 0 | 0 | 77.326
3636 | 256.6217 | 2.8 | 43.3 | 0 | 0 | 128.3109 | 0 | 24 | 45.9 | 0 | 0 | 85.511
3637 | 241.2849 | 1.4 | 43.1 | 0 | 75.1 | 120.6424 | 13.5 | 42.6 | 86.9 | 0 | 0 | 97.0715
3638 | 232.7372 | 2.1 | 43.2 | 0 | 37.6 | 116.3686 | 32.6 | 52.1 | 124.2 | 0 | 0 | 85.1582
3639 | 219.5503 | 3.5 | 43.4 | 0 | 0 | 109.7752 | 0 | 71.8 | 161.4 | 0 | 0 | 87.0548
3640 | 197.9413 | 2.8 | 43.3 | 0 | 0 | 98.9707 | 0 | 77.9 | 199.2 | 0 | 0 | 214.6705
3641 | 169.8378 | 2.1 | 43.2 | 0 | 0 | 84.9189 | 0 | 83.4 | 229.6 | 0 | 0 | 74.7416
3642 | 130.151 | 0.7 | 43 | 0 | 37.6 | 65.0755 | 243.1 | 74.4 | 252.7 | 0 | 0 | 77.6878
3643 | 98.4673 | 0 | 42.9 | 0 | 75.1 | 49.2337 | 284.5 | 0 | 177.6 | 0 | 0 | 91.0968
3644 | 73.1172 | 0 | 42.9 | 0 | 75.1 | 36.5586 | 192.9 | 0 | 92.6 | 0 | 0 | 144.3284
3645 | 45.7966 | 0 | 42.9 | 0 | 75.1 | 22.8983 | 91.5 | 0 | 51.2 | 0 | 0 | 171.454
3646 | 46.6003 | 0 | 42.9 | 0 | 93.9 | 23.3001 | 48.8 | 0 | 21 | 0 | 0 | 89.5498
3647 | 45.3665 | 0 | 0 | 0 | 0 | 22.6832 | 0 | 0 | 0 | 0 | 0 | 94.6794
3648 | 42.919 | 0 | 0 | 0 | 0 | 21.4595 | 0 | 0 | 0 | 0 | 0 | 81.7268
3649 | 42.0091 | 0 | 0 | 0 | 0 | 21.0045 | 0 | 0 | 0 | 0 | 0 | 64.8398
3650 | 45.0423 | 0 | 0 | 0 | 0 | 22.5211 | 0 | 0 | 0 | 0 | 0 | 62.4306
3651 | 43.3002 | 0 | 0 | 0 | 0 | 21.6501 | 0 | 0 | 0 | 0 | 0 | 63.3494
3652 | 42.2849 | 0 | 0 | 0 | 0 | 21.1424 | 0 | 0 | 0 | 0 | 0 | 55.2875
3653 | 43.2295 | 0 | 0 | 0 | 0 | 21.6148 | 0 | 0 | 0 | 0 | 0 | 54.8282
3654 | 48.1189 | 0 | 0 | 0 | 0 | 24.0594 | 0 | 0 | 0 | 0 | 0 | 46.4487
3655 | 51.6904 | 0 | 42.9 | 0 | 56.3 | 25.8452 | 0.5 | 0 | 0 | 0 | 0 | 59.667
3656 | 54.7807 | 0 | 42.9 | 0 | 37.6 | 27.3903 | 8.8 | 0 | 14.4 | 0 | 0 | 62.4302
3657 | 54.0706 | 0 | 42.9 | 0 | 0 | 27.0353 | 0 | 0 | 53.2 | 0 | 0 | 92.4096
3658 | 51.8398 | 0 | 42.9 | 0 | 0 | 25.9199 | 0 | 0 | 92.9 | 0 | 0 | 157.1626
3659 | 56.9154 | 0 | 42.9 | 0 | 0 | 28.4577 | 0 | 0 | 134.1 | 0 | 0 | 141.2113
3660 | 63.1879 | 0 | 42.9 | 0 | 0 | 31.594 | 0 | 0 | 133.8 | 0 | 0 | 132.8301
3661 | 70.071 | 0 | 42.9 | 0 | 75.1 | 35.0355 | 228.7 | 3.7 | 126.4 | 0 | 0 | 108.3642
3662 | 77.2491 | 0 | 42.9 | 0 | 37.6 | 38.6246 | 189.3 | 13.6 | 121.5 | 0 | 0 | 96.2278
3663 | 79.3631 | 0 | 42.9 | 0 | 0 | 39.6815 | 0 | 20.8 | 124.1 | 0 | 0 | 109.6909
3664 | 78.3434 | 0 | 42.9 | 0 | 0 | 39.1717 | 0 | 31.1 | 120.8 | 0 | 0 | 84.4458
3665 | 76.9163 | 0 | 42.9 | 0 | 0 | 38.4581 | 0 | 39.4 | 114.2 | 0 | 0 | 110.5387
3666 | 75.8721 | 0 | 42.9 | 0 | 37.6 | 37.9361 | 205.8 | 43.8 | 96.8 | 0 | 0 | 117.8354
3667 | 67.7379 | 0 | 42.9 | 0 | 75.1 | 33.869 | 218 | 42 | 72.8 | 0 | 0 | 232.6005
3668 | 60.6441 | 0 | 42.9 | 0 | 75.1 | 30.322 | 140.5 | 11.2 | 17 | 0 | 0 | 145.3958
3669 | 55.2124 | 0 | 42.9 | 0 | 75.1 | 27.6062 | 56 | 1 | 5.9 | 0 | 0 | 139.4119
3670 | 45.7061 | 0 | 42.9 | 0 | 93.9 | 22.8531 | 22.7 | 0 | 0 | 0 | 0 | 297.5181
3671 | 41.8702 | 0 | 0 | 0 | 0 | 20.9351 | 0 | 0 | 0 | 0 | 0 | 123.1965
3672 | 40.5558 | 0 | 0 | 0 | 0 | 20.2779 | 0 | 0 | 0 | 0 | 0 | 84.3258
3673 | 40.9863 | 0 | 0 | 0 | 0 | 20.4932 | 0 | 0 | 0 | 0 | 0 | 77.5658
3674 | 43.3185 | 0 | 0 | 0 | 0 | 21.6592 | 0 | 0 | 0 | 0 | 0 | 48.6296
3675 | 42.0512 | 0 | 0 | 0 | 0 | 21.0256 | 0 | 0 | 0 | 0 | 0 | 47.0201
3676 | 43.4226 | 0 | 0 | 0 | 0 | 21.7113 | 0 | 0 | 0 | 0 | 0 | 49.2061
3677 | 40.8921 | 0 | 0 | 0 | 0 | 20.4461 | 0 | 0 | 0 | 0 | 0 | 51.1563
3678 | 44.2461 | 0 | 0 | 0 | 0 | 22.123 | 0 | 0 | 0 | 0 | 0 | 61.623
3679 | 57.7851 | 0 | 42.9 | 0 | 56.3 | 28.8925 | 0 | 0 | 0 | 0 | 0 | 58.0537
3680 | 57.2966 | 0 | 42.9 | 0 | 37.6 | 28.6483 | 2.8 | 0 | 1.6 | 0 | 0 | 100.9024
3681 | 54.9192 | 0 | 42.9 | 0 | 0 | 27.4596 | 0 | 0 | 26.3 | 0 | 0 | 57.3623
3682 | 58.2502 | 0 | 42.9 | 0 | 0 | 29.1251 | 0 | 0 | 59 | 0 | 0 | 62.3158
3683 | 64.3244 | 0 | 42.9 | 0 | 0 | 32.1622 | 0 | 0 | 91.5 | 0 | 0 | 56.092
3684 | 72.2414 | 0 | 42.9 | 0 | 0 | 36.1207 | 0 | 0 | 90.8 | 0 | 0 | 97.9186
3685 | 80.5879 | 0 | 42.9 | 0 | 75.1 | 40.294 | 224.1 | 0 | 92.7 | 0 | 0 | 72.3188
3686 | 83.9468 | 0 | 42.9 | 0 | 37.6 | 41.9734 | 191.6 | 1.5 | 98.6 | 0 | 0 | 77.8028
3687 | 83.4804 | 0 | 42.9 | 0 | 0 | 41.7402 | 0 | 4.6 | 93.5 | 0 | 0 | 109.4521
3688 | 84.117 | 0 | 42.9 | 0 | 0 | 42.0585 | 0 | 6.2 | 79.9 | 0 | 0 | 70.0138
3689 | 86.6444 | 0 | 42.9 | 0 | 0 | 43.3222 | 0 | 9.4 | 69.6 | 0 | 0 | 90.6256
3690 | 84.6011 | 0 | 42.9 | 0 | 37.6 | 42.3005 | 178.2 | 15.8 | 58.3 | 0 | 0 | 93.2429
3691 | 83.8356 | 0 | 42.9 | 0 | 75.1 | 41.9178 | 166.2 | 6.5 | 49.8 | 0 | 0 | 119.2382
3692 | 73.7823 | 0 | 42.9 | 0 | 75.1 | 36.8912 | 95.8 | 0 | 7.7 | 0 | 0 | 167.2347
3693 | 67.2994 | 0 | 42.9 | 0 | 75.1 | 33.6497 | 40.3 | 0 | 2.4 | 0 | 0 | 132.8121
3694 | 67.7395 | 0 | 42.9 | 0 | 93.9 | 33.8697 | 18.1 | 0 | 0 | 0 | 0 | 162.023
3695 | 67.6204 | 0 | 0 | 0 | 0 | 33.8102 | 0 | 0 | 0 | 0 | 0 | 124.1259
3696 | 55.8474 | 0 | 0 | 0 | 0 | 27.9237 | 0 | 0 | 0 | 0 | 0 | 85.1599
3697 | 43.6266 | 0 | 0 | 0 | 0 | 21.8133 | 0 | 0 | 0 | 0 | 0 | 67.5989
3698 | 44.9735 | 0 | 0 | 0 | 0 | 22.4867 | 0 | 0 | 0 | 0 | 0 | 53.3381
3699 | 40.7821 | 0 | 0 | 0 | 0 | 20.391 | 0 | 0 | 0 | 0 | 0 | 48.3985
3700 | 43.1877 | 0 | 0 | 0 | 0 | 21.5939 | 0 | 0 | 0 | 0 | 0 | 49.663
3701 | 43.5993 | 0 | 0 | 0 | 0 | 21.7996 | 0 | 0 | 0 | 0 | 0 | 56.4359
3702 | 63.3165 | 0 | 0 | 0 | 0 | 31.6583 | 0 | 0 | 0 | 0 | 0 | 48.1698
3703 | 86.3698 | 0 | 42.9 | 0 | 56.3 | 43.1849 | 0 | 0 | 0 | 0 | 0 | 60.7038
3704 | 133.3404 | 0.7 | 43 | 0 | 37.6 | 66.6702 | 0 | 25.6 | 0 | 0 | 0 | 76.2652
3705 | 217.1246 | 2.1 | 43.2 | 0 | 0 | 108.5623 | 0 | 28.6 | 0 | 0 | 0 | 88.1252
3706 | 251.508 | 3.5 | 43.4 | 0 | 0 | 125.754 | 0 | 32.5 | 0 | 0 | 0 | 77.2111
3707 | 236.557 | 3.5 | 43.4 | 0 | 0 | 118.2785 | 0 | 38.9 | 0 | 0 | 0 | 75.3228
3708 | 227.5386 | 2.8 | 43.3 | 0 | 0 | 113.7693 | 0 | 53.3 | 0 | 0 | 0 | 118.1255
3709 | 223.707 | 1.4 | 43.1 | 0 | 75.1 | 111.8535 | 0 | 56.8 | 0 | 0 | 0 | 139.7808
3710 | 222.3613 | 2.1 | 43.2 | 0 | 37.6 | 111.1807 | 0 | 53 | 0 | 0 | 0 | 102.4579
3711 | 224.559 | 3.5 | 43.4 | 0 | 0 | 112.2795 | 0 | 51.2 | 0 | 0 | 0 | 77.8066
3712 | 195.7009 | 2.8 | 43.3 | 0 | 0 | 97.8504 | 0 | 51.4 | 0 | 0 | 0 | 75.7927
3713 | 144.2565 | 2.1 | 43.2 | 0 | 0 | 72.1283 | 0 | 63.4 | 0 | 0 | 0 | 86.6974
3714 | 109.3521 | 0.7 | 43 | 0 | 37.6 | 54.6761 | 0 | 58.2 | 0 | 0 | 0 | 88.8363
3715 | 81.0525 | 0 | 42.9 | 0 | 75.1 | 40.5262 | 0 | 0 | 0 | 0 | 0 | 186.1987
3716 | 67.657 | 0 | 42.9 | 0 | 75.1 | 33.8285 | 0 | 0 | 0 | 0 | 0 | 117.3027
3717 | 64.2438 | 0 | 42.9 | 0 | 75.1 | 32.1219 | 0 | 0 | 0 | 0 | 0 | 170.5704
3718 | 63.1145 | 0 | 42.9 | 0 | 93.9 | 31.5572 | 0 | 0 | 0 | 0 | 0 | 139.7256
3719 | 62.5154 | 0 | 0 | 0 | 0 | 31.2577 | 0 | 0 | 0 | 0 | 0 | 96.9533
3720 | 60.1795 | 0 | 0 | 0 | 0 | 30.0898 | 0 | 0 | 0 | 0 | 0 | 69.0933
3721 | 58.7849 | 0 | 0 | 0 | 0 | 29.3924 | 0 | 0 | 0 | 0 | 0 | 57.5921
3722 | 59.4816 | 0 | 0 | 0 | 0 | 29.7408 | 0 | 0 | 0 | 0 | 0 | 48.2854
3723 | 61.5066 | 0 | 0 | 0 | 0 | 30.7533 | 0 | 0 | 0 | 0 | 0 | 44.3006
3724 | 57.8157 | 0 | 0 | 0 | 0 | 28.9079 | 0 | 0 | 0 | 0 | 0 | 45.5412
3725 | 45.8834 | 0 | 0 | 0 | 0 | 22.9417 | 0 | 0 | 0 | 0 | 0 | 61.0486
3726 | 60.4848 | 0 | 0 | 0 | 0 | 30.2424 | 0 | 0 | 0 | 0 | 0 | 54.0267
3727 | 95.9588 | 0 | 42.9 | 0 | 56.3 | 47.9794 | 0 | 0 | 0 | 0 | 0 | 52.9927
3728 | 144.3678 | 0.7 | 43 | 0 | 37.6 | 72.1839 | 0 | 0 | 0 | 0 | 0 | 53.9116
3729 | 201.3291 | 2.1 | 43.2 | 0 | 0 | 100.6645 | 0 | 0 | 0 | 0 | 0 | 49.7773
3730 | 259.2241 | 3.5 | 43.4 | 0 | 0 | 129.6121 | 0 | 0.7 | 0 | 0 | 0 | 49.4348
3731 | 276.2761 | 3.5 | 43.4 | 0 | 0 | 138.138 | 0 | 5.8 | 0 | 0 | 0 | 65.4111
3732 | 277.6503 | 2.8 | 43.3 | 0 | 0 | 138.8251 | 0 | 27.1 | 0 | 0 | 0 | 110.058
3733 | 280.3404 | 1.4 | 43.1 | 0 | 75.1 | 140.1702 | 0 | 40 | 0 | 0 | 0 | 175.3333
3734 | 276.0616 | 2.1 | 43.2 | 0 | 37.6 | 138.0308 | 0 | 52.2 | 0 | 0 | 0 | 64.7248
3735 | 272.5065 | 3.5 | 43.4 | 0 | 0 | 136.2532 | 0 | 70.4 | 0 | 0 | 0 | 59.5524
3736 | 235.9868 | 2.8 | 43.3 | 0 | 0 | 117.9934 | 0 | 80.9 | 0 | 0 | 0 | 58.0549
3737 | 174.672 | 2.1 | 43.2 | 0 | 0 | 87.336 | 0 | 91.4 | 1.5 | 0 | 0 | 84.448
3738 | 122.6819 | 0.7 | 43 | 0 | 37.6 | 61.3409 | 0 | 81.3 | 0.2 | 0 | 0 | 147.6562
3739 | 100.052 | 0 | 42.9 | 0 | 75.1 | 50.026 | 0 | 2.8 | 0 | 0 | 0 | 180.5653
3740 | 75.4838 | 0 | 42.9 | 0 | 75.1 | 37.7419 | 0 | 0 | 0 | 0 | 0 | 110.4159
3741 | 66.1474 | 0 | 42.9 | 0 | 75.1 | 33.0737 | 0 | 0 | 0 | 0 | 0 | 97.6746
3742 | 64.2813 | 0 | 42.9 | 0 | 93.9 | 32.1407 | 0 | 0 | 0 | 0 | 0 | 102.8227
3743 | 64.555 | 0 | 0 | 0 | 0 | 32.2775 | 0 | 0 | 0 | 0 | 0 | 89.3108
3744 | 63.2539 | 0 | 0 | 0 | 0 | 31.627 | 0 | 0 | 0 | 0 | 0 | 71.5117
3745 | 63.0206 | 0 | 0 | 0 | 0 | 31.5103 | 0 | 0 | 0 | 0 | 0 | 57.2457
3746 | 62.0682 | 0 | 0 | 0 | 0 | 31.0341 | 0 | 0 | 0 | 0 | 0 | 58.0531
3747 | 60.8028 | 0 | 0 | 0 | 0 | 30.4014 | 0 | 0 | 0 | 0 | 0 | 57.3635
3748 | 59.0291 | 0 | 0 | 0 | 0 | 29.5145 | 0 | 0 | 0 | 0 | 0 | 59.3222
3749 | 61.1874 | 0 | 0 | 0 | 0 | 30.5937 | 0 | 0 | 0 | 0 | 0 | 67.1388
3750 | 72.9353 | 0 | 0 | 0 | 0 | 36.4677 | 0 | 0 | 0 | 0 | 0 | 65.8711
3751 | 90.387 | 0 | 42.9 | 0 | 56.3 | 45.1935 | 0 | 0 | 0 | 0 | 0 | 63.1179
3752 | 123.5577 | 0.7 | 43 | 0 | 37.6 | 61.7789 | 0 | 6.1 | 0 | 0 | 0 | 96.2264
3753 | 191.8219 | 2.1 | 43.2 | 0 | 0 | 95.9109 | 0 | 7.7 | 0 | 0 | 0 | 137.286
3754 | 247.6662 | 3.5 | 43.4 | 0 | 0 | 123.8331 | 0 | 11.3 | 0 | 0 | 0 | 158.6251
3755 | 265.6324 | 3.5 | 43.4 | 0 | 0 | 132.8162 | 0 | 19 | 0 | 0 | 0 | 109.5691
3756 | 262.84 | 2.8 | 43.3 | 0 | 0 | 131.42 | 0 | 45.1 | 0 | 0 | 0 | 138.8928
3757 | 249.7675 | 1.4 | 43.1 | 0 | 75.1 | 124.8837 | 0 | 56.9 | 0 | 0 | 0 | 129.304
3758 | 249.7018 | 2.1 | 43.2 | 0 | 37.6 | 124.8509 | 0 | 64.5 | 0 | 0 | 0 | 87.8874
3759 | 248.1918 | 3.5 | 43.4 | 0 | 0 | 124.0959 | 0 | 77.7 | 0 | 0 | 0 | 71.7425
3760 | 195.7743 | 2.8 | 43.3 | 0 | 0 | 97.8872 | 0 | 86 | 0 | 0 | 0 | 96.5894
3761 | 143.1789 | 2.1 | 43.2 | 0 | 0 | 71.5895 | 0 | 99.1 | 0 | 0 | 0 | 172.2095
3762 | 110.7313 | 0.7 | 43 | 0 | 37.6 | 55.3656 | 0 | 93 | 0 | 0 | 0 | 141.4993
3763 | 91.8083 | 0 | 42.9 | 0 | 75.1 | 45.9042 | 0 | 9.8 | 0 | 0 | 0 | 221.4832
3764 | 72.8485 | 0 | 42.9 | 0 | 75.1 | 36.4243 | 0 | 0 | 0 | 0 | 0 | 209.5974
3765 | 66.9054 | 0 | 42.9 | 0 | 75.1 | 33.4527 | 0 | 0 | 0 | 0 | 0 | 218.7839
3766 | 64.5882 | 0 | 42.9 | 0 | 93.9 | 32.2941 | 0 | 0 | 0 | 0 | 0 | 269.8682
3767 | 62.8402 | 0 | 0 | 0 | 0 | 31.4201 | 0 | 0 | 0 | 0 | 0 | 178.1708
3768 | 64.0498 | 0 | 0 | 0 | 0 | 32.0249 | 0 | 0 | 0 | 0 | 0 | 112.2384
3769 | 61.8745 | 0 | 0 | 0 | 0 | 30.9372 | 0 | 0 | 0 | 0 | 0 | 85.3964
3770 | 57.7568 | 0 | 0 | 0 | 0 | 28.8784 | 0 | 0 | 0 | 0 | 0 | 66.9097
3771 | 44.2179 | 0 | 0 | 0 | 0 | 22.1089 | 0 | 0 | 0 | 0 | 0 | 61.5079
3772 | 41.4679 | 0 | 0 | 0 | 0 | 20.734 | 0 | 0 | 0 | 0 | 0 | 58.749
3773 | 45.2239 | 0 | 0 | 0 | 0 | 22.6119 | 0 | 0 | 0 | 0 | 0 | 55.2869
3774 | 67.5101 | 0 | 0 | 0 | 0 | 33.7551 | 0 | 0 | 0 | 0 | 0 | 66.7935
3775 | 115.9597 | 0 | 42.9 | 0 | 56.3 | 57.9798 | 0 | 0 | 0 | 0 | 18.5 | 58.4016
3776 | 172.497 | 0.7 | 43 | 0.1 | 37.6 | 86.2485 | 0 | 10.6 | 0 | 0 | 13 | 49.2034
3777 | 254.027 | 2.1 | 43.2 | 0 | 0 | 127.0135 | 0 | 7.8 | 0 | 0 | 0 | 48.5137
3778 | 320.2962 | 3.5 | 43.4 | 0 | 0 | 160.1481 | 0 | 13.9 | 0 | 0 | 0 | 63.2335
3779 | 298.4693 | 3.5 | 43.4 | 0 | 0 | 149.2347 | 0 | 22.9 | 0 | 0 | 0 | 142.0804
3780 | 252.1613 | 2.8 | 43.3 | 0 | 0 | 126.0807 | 0 | 47.5 | 0 | 0 | 0 | 192.9201
3781 | 242.7951 | 1.4 | 43.1 | 0 | 75.1 | 121.3976 | 0 | 57.3 | 0 | 0 | 0 | 93.9625
3782 | 243.7395 | 2.1 | 43.2 | 0 | 37.6 | 121.8697 | 0 | 64 | 0 | 0 | 0 | 128.1771
3783 | 244.0274 | 3.5 | 43.4 | 0 | 0 | 122.0137 | 0 | 79.4 | 0 | 0 | 0 | 159.7523
3784 | 224.2488 | 2.8 | 43.3 | 0 | 0 | 112.1244 | 0 | 86.5 | 0 | 0 | 0 | 232.677
3785 | 174.9271 | 2.1 | 43.2 | 0 | 0 | 87.4635 | 0 | 98.9 | 0 | 0 | 0 | 117.2889
3786 | 144.1353 | 0.7 | 43 | 0 | 37.6 | 72.0677 | 0 | 92.9 | 0 | 0 | 0 | 175.8978
3787 | 111.1543 | 0 | 42.9 | 0 | 75.1 | 55.5772 | 0 | 10.7 | 0 | 0 | 0 | 198.8461
3788 | 89.103 | 0 | 42.9 | 0 | 75.1 | 44.5515 | 0 | 0 | 0 | 0 | 0 | 180.2475
3789 | 65.6515 | 0 | 42.9 | 0 | 75.1 | 32.8258 | 0 | 0 | 0 | 0 | 0 | 316.1446
3790 | 63.7579 | 0 | 42.9 | 0 | 93.9 | 31.8789 | 0 | 0 | 0 | 0 | 0 | 252.38
3791 | 61.9544 | 0 | 0 | 0 | 0 | 30.9772 | 0 | 0 | 0 | 0 | 0 | 106.1818
3792 | 60.4845 | 0 | 0 | 0 | 0 | 30.2422 | 0 | 0 | 0 | 0 | 0 | 92.7693
3793 | 44.8312 | 0 | 0 | 0 | 0 | 22.4156 | 0 | 0 | 0 | 0 | 0 | 64.6095
3794 | 43.1871 | 0 | 0 | 0 | 0 | 21.5935 | 0 | 0 | 0 | 0 | 0 | 66.2174
3795 | 41.1586 | 0 | 0 | 0 | 0 | 20.5793 | 0 | 0 | 0 | 0 | 0 | 67.0244
3796 | 43.6166 | 0 | 0 | 0 | 0 | 21.8083 | 0 | 0 | 0 | 0 | 0 | 52.3063
3797 | 41.3809 | 0 | 0 | 0 | 0 | 20.6904 | 0 | 0 | 0 | 0 | 0 | 75.5595
3798 | 63.9131 | 0 | 0 | 0 | 0 | 31.9566 | 0 | 0 | 0 | 0 | 0 | 69.5543
3799 | 89.4793 | 0 | 42.9 | 0 | 56.3 | 44.7396 | 0 | 0 | 0 | 0 | 29.5 | 65.9858
3800 | 126.0201 | 0.7 | 43 | 5.4 | 37.6 | 63.01 | 0 | 0 | 0 | 0 | 28 | 87.8814
3801 | 201.4121 | 2.1 | 43.2 | 0.1 | 0 | 100.7061 | 0 | 0 | 0 | 0 | 0 | 84.8067
3802 | 283.8599 | 3.5 | 43.4 | 0 | 0 | 141.9299 | 0 | 0 | 0 | 0 | 0 | 90.9787
3803 | 289.4577 | 3.5 | 43.4 | 0 | 0 | 144.7288 | 0 | 0 | 0 | 0 | 0 | 111.7547
3804 | 273.9318 | 2.8 | 43.3 | 0 | 0 | 136.9659 | 0 | 10.3 | 0 | 0 | 0 | 146.4057
3805 | 274.1745 | 1.4 | 43.1 | 0 | 75.1 | 137.0872 | 0 | 15.6 | 0 | 0 | 0.9 | 147.4248
3806 | 268.6653 | 2.1 | 43.2 | 0 | 37.6 | 134.3327 | 0 | 13.2 | 0 | 0 | 0 | 104.0112
3807 | 253.6028 | 3.5 | 43.4 | 0 | 0 | 126.8014 | 0 | 4.6 | 0 | 0 | 0 | 99.5966
3808 | 213.2341 | 2.8 | 43.3 | 0 | 0 | 106.6171 | 0 | 0.4 | 0 | 0 | 0 | 221.523
3809 | 162.2928 | 2.1 | 43.2 | 0 | 0 | 81.1464 | 0 | 4.3 | 0 | 0 | 0 | 119.0952
3810 | 134.1565 | 0.7 | 43 | 0 | 37.6 | 67.0782 | 0 | 6.6 | 0 | 0 | 0 | 155.7053
3811 | 113.5649 | 0 | 42.9 | 0 | 75.1 | 56.7825 | 0 | 0 | 0 | 0 | 0 | 100.0671
3812 | 74.5466 | 0 | 42.9 | 0 | 75.1 | 37.2733 | 0 | 0 | 0 | 0 | 0 | 144.6933
3813 | 44.3053 | 0 | 42.9 | 0 | 75.1 | 22.1526 | 0 | 0 | 0 | 0 | 0 | 138.1875
3814 | 43.6718 | 0 | 42.9 | 0 | 93.9 | 21.8359 | 0 | 0 | 0 | 0 | 0 | 142.5263
3815 | 40.5106 | 0 | 0 | 0 | 0 | 20.2553 | 0 | 0 | 0 | 0 | 0 | 122.991
3816 | 39.5415 | 0 | 0 | 0 | 0 | 19.7707 | 0 | 0 | 0 | 0 | 0 | 104.982
3817 | 41.0573 | 0 | 0 | 0 | 0 | 20.5286 | 0 | 0 | 0 | 0 | 0 | 74.1636
3818 | 42.0425 | 0 | 0 | 0 | 0 | 21.0213 | 0 | 0 | 0 | 0 | 0 | 62.0851
3819 | 40.9321 | 0 | 0 | 0 | 0 | 20.466 | 0 | 0 | 0 | 0 | 0 | 58.2861
3820 | 41.8377 | 0 | 0 | 0 | 0 | 20.9188 | 0 | 0 | 0 | 0 | 0 | 55.8642
3821 | 43.2367 | 0 | 0 | 0 | 0 | 21.6183 | 0 | 0 | 0 | 0 | 0 | 60.9339
3822 | 54.6806 | 0 | 0 | 0 | 0 | 27.3403 | 0 | 0 | 0 | 0 | 0 | 85.8633
3823 | 69.3938 | 0 | 42.9 | 0 | 56.3 | 34.6969 | 0 | 0 | 0 | 0 | 73.4 | 52.0747
3824 | 70.7386 | 0 | 42.9 | 0 | 37.6 | 35.3693 | 0 | 0 | 0 | 0 | 28.1 | 55.4015
3825 | 65.6357 | 0 | 42.9 | 0 | 0 | 32.8178 | 0 | 0 | 0 | 0 | 0 | 75.9125
3826 | 67.3468 | 0 | 42.9 | 0 | 0 | 33.6734 | 0 | 0 | 0 | 0 | 0 | 191.7884
3827 | 72.8278 | 0 | 42.9 | 0 | 0 | 36.4139 | 0 | 0 | 0 | 0 | 0 | 245.5794
3828 | 81.5679 | 0 | 42.9 | 0 | 0 | 40.7839 | 0 | 0 | 0 | 0 | 0 | 136.6932
3829 | 86.8827 | 0 | 42.9 | 0 | 75.1 | 43.4414 | 0 | 0 | 0 | 0 | 0 | 161.6076
3830 | 94.2093 | 0 | 42.9 | 0 | 37.6 | 47.1047 | 0 | 0 | 0 | 0 | 0 | 112.3615
3831 | 93.0177 | 0 | 42.9 | 0 | 0 | 46.5088 | 0 | 0 | 5.5 | 0 | 0 | 103.297
3832 | 90.8287 | 0 | 42.9 | 0 | 0 | 45.4143 | 0 | 0 | 25.8 | 0 | 0 | 137.6613
3833 | 86.7885 | 0 | 42.9 | 0 | 0 | 43.3943 | 0 | 0 | 50.5 | 0 | 0 | 221.4404
3834 | 85.8805 | 0 | 42.9 | 0 | 37.6 | 42.9402 | 0 | 0 | 72.7 | 0 | 0 | 115.5025
3835 | 80.0734 | 0 | 42.9 | 0 | 75.1 | 40.0367 | 0 | 0 | 59.1 | 0 | 0 | 121.3109
3836 | 74.3374 | 0 | 42.9 | 0 | 75.1 | 37.1687 | 0 | 0 | 7.8 | 0 | 0 | 132.4157
3837 | 61.0488 | 0 | 42.9 | 0 | 75.1 | 30.5244 | 0 | 0 | 0 | 0 | 0 | 166.9779
3838 | 47.768 | 0 | 42.9 | 0 | 93.9 | 23.884 | 0 | 0 | 0 | 0 | 0 | 134.2481
3839 | 45.5118 | 0 | 0 | 0 | 0 | 22.7559 | 0 | 0 | 0 | 0 | 0 | 124.9231
3840 | 43.6281 | 0 | 0 | 0 | 0 | 21.8141 | 0 | 0 | 0 | 0 | 0 | 148.0866
3841 | 42.91 | 0 | 0 | 0 | 0 | 21.455 | 0 | 0 | 0 | 0 | 0 | 93.4851
3842 | 43.952 | 0 | 0 | 0 | 0 | 21.976 | 0 | 0 | 0 | 0 | 0 | 46.7924
3843 | 41.1419 | 0 | 0 | 0 | 0 | 20.571 | 0 | 0 | 0 | 0 | 0 | 47.5942
3844 | 44.9846 | 0 | 0 | 0 | 0 | 22.4923 | 0 | 0 | 0 | 0 | 0 | 48.2847
3845 | 45.3637 | 0 | 0 | 0 | 0 | 22.6818 | 0 | 0 | 0 | 0 | 0 | 53.1087
3846 | 47.8889 | 0 | 0 | 0 | 0 | 23.9445 | 0 | 0 | 0 | 0 | 0 | 56.4383
3847 | 58.7684 | 0 | 42.9 | 0 | 56.3 | 29.3842 | 0 | 0 | 0 | 0 | 0 | 86.1068
3848 | 61.704 | 0 | 42.9 | 0 | 37.6 | 30.852 | 0 | 0 | 0 | 0 | 0 | 133.092
3849 | 61.6396 | 0 | 42.9 | 0 | 0 | 30.8198 | 0 | 0 | 0 | 0 | 0 | 108.3669
3850 | 68.3134 | 0 | 42.9 | 0 | 0 | 34.1567 | 0 | 0 | 0 | 0 | 0 | 72.3176
3851 | 77.6892 | 0 | 42.9 | 0 | 0 | 38.8446 | 0 | 0 | 0 | 0 | 0 | 52.9935
3852 | 82.1319 | 0 | 42.9 | 0 | 0 | 41.066 | 0 | 0 | 5.2 | 0 | 0 | 130.8956
3853 | 86.2115 | 0 | 42.9 | 0 | 75.1 | 43.1057 | 0 | 0 | 24.8 | 0 | 0 | 273.8507
3854 | 84.7381 | 0 | 42.9 | 0 | 37.6 | 42.369 | 0 | 0 | 45.9 | 0 | 0 | 112.4847
3855 | 85.1968 | 0 | 42.9 | 0 | 0 | 42.5984 | 0 | 0 | 69.5 | 0 | 0 | 264.4866
3856 | 83.7355 | 0 | 42.9 | 0 | 0 | 41.8677 | 0 | 0 | 96.6 | 0 | 0 | 194.1118
3857 | 83.6462 | 0 | 42.9 | 0 | 0 | 41.8231 | 0 | 0 | 121.1 | 0 | 0 | 146.0135
3858 | 82.873 | 0 | 42.9 | 0 | 37.6 | 41.4365 | 61.2 | 0 | 137.4 | 0 | 0 | 124.4076
3859 | 75.8349 | 0 | 42.9 | 0 | 75.1 | 37.9175 | 95 | 0 | 141.6 | 0 | 0 | 167.5852
3860 | 70.9506 | 0 | 42.9 | 0 | 75.1 | 35.4753 | 42.9 | 0 | 65.8 | 0 | 0 | 198.1478
3861 | 69.1502 | 0 | 42.9 | 0 | 75.1 | 34.5751 | 7.5 | 0 | 28.2 | 0 | 0 | 174.6516
3862 | 62.41 | 0 | 42.9 | 0 | 93.9 | 31.205 | 0.5 | 0 | 5 | 0 | 0 | 195.8686
3863 | 63.6534 | 0 | 0 | 0 | 0 | 31.8267 | 0 | 0 | 0 | 0 | 0 | 170.2807
3864 | 61.5246 | 0 | 0 | 0 | 0 | 30.7623 | 0 | 0 | 0 | 0 | 0 | 75.3242
3865 | 59.8587 | 0 | 0 | 0 | 0 | 29.9294 | 0 | 0 | 0 | 0 | 0 | 59.2079
3866 | 51.9752 | 0 | 0 | 0 | 0 | 25.9876 | 0 | 0 | 0 | 0 | 0 | 48.7434
3867 | 42.7529 | 0 | 0 | 0 | 0 | 21.3764 | 0 | 0 | 0 | 0 | 0 | 48.9741
3868 | 40.563 | 0 | 0 | 0 | 0 | 20.2815 | 0 | 0 | 0 | 0 | 0 | 49.7778
3869 | 44.3645 | 0 | 0 | 0 | 0 | 22.1822 | 0 | 0 | 0 | 0 | 0 | 52.1911
3870 | 58.9981 | 0 | 0 | 0 | 0 | 29.499 | 0 | 0 | 0 | 0 | 0 | 48.6284
3871 | 92.3622 | 0 | 42.9 | 0 | 56.3 | 46.1811 | 0 | 0 | 0 | 0 | 0 | 73.8165
3872 | 133.4904 | 0.7 | 43 | 0 | 37.6 | 66.7452 | 0 | 0 | 10.7 | 0 | 0 | 55.8628
3873 | 178.0604 | 2.1 | 43.2 | 0 | 0 | 89.0302 | 0 | 0 | 52.8 | 0 | 0 | 59.2073
3874 | 238.4841 | 3.5 | 43.4 | 0 | 0 | 119.2421 | 0 | 0 | 106.1 | 0 | 0 | 94.2023
3875 | 255.223 | 3.5 | 43.4 | 0 | 0 | 127.6115 | 0 | 0 | 160.3 | 0 | 0 | 116.2776
3876 | 260.9901 | 2.8 | 43.3 | 0 | 0 | 130.495 | 0 | 4.9 | 175.7 | 0 | 0 | 75.7963
3877 | 250.0514 | 1.4 | 43.1 | 0 | 75.1 | 125.0257 | 201.7 | 7.3 | 189.7 | 0 | 0 | 91.0987
3878 | 246.9627 | 2.1 | 43.2 | 0 | 37.6 | 123.4813 | 194.4 | 14.4 | 202 | 0 | 0 | 128.0329
3879 | 246.9974 | 3.5 | 43.4 | 0 | 0 | 123.4987 | 0 | 34.3 | 210.3 | 0 | 0 | 126.8577
3880 | 215.4612 | 2.8 | 43.3 | 0 | 0 | 107.7306 | 0 | 45.2 | 207.6 | 0 | 0 | 92.1724
3881 | 153.9618 | 2.1 | 43.2 | 0 | 0 | 76.9809 | 0 | 56.2 | 216.3 | 0 | 0 | 99.1073
3882 | 114.9909 | 0.7 | 43 | 0 | 37.6 | 57.4954 | 266.4 | 39.9 | 183.8 | 0 | 0 | 79.1181
3883 | 90.4515 | 0 | 42.9 | 0 | 75.1 | 45.2258 | 230.8 | 0 | 82.7 | 0 | 0 | 97.3109
3884 | 64.4351 | 0 | 42.9 | 0 | 75.1 | 32.2175 | 147 | 0 | 29.2 | 0 | 0 | 111.5077
3885 | 46.087 | 0 | 42.9 | 0 | 75.1 | 23.0435 | 74 | 0 | 16.4 | 0 | 0 | 174.14
3886 | 44.8414 | 0 | 42.9 | 0 | 93.9 | 22.4207 | 34.5 | 0 | 5.4 | 0 | 0 | 168.9499
3887 | 41.6511 | 0 | 0 | 0 | 0 | 20.8256 | 0 | 0 | 0 | 0 | 0 | 123.5186
3888 | 42.8964 | 0 | 0 | 0 | 0 | 21.4482 | 0 | 0 | 0 | 0 | 0 | 102.339
3889 | 43.3836 | 0 | 0 | 0 | 0 | 21.6918 | 0 | 0 | 0 | 0 | 0 | 60.1268
3890 | 42.7668 | 0 | 0 | 0 | 0 | 21.3834 | 0 | 0 | 0 | 0 | 0 | 49.0891
3891 | 42.1504 | 0 | 0 | 0 | 0 | 21.0752 | 0 | 0 | 0 | 0 | 0 | 50.2379
3892 | 40.7189 | 0 | 0 | 0 | 0 | 20.3594 | 0 | 0 | 0 | 0 | 0 | 46.1083
3893 | 45.2403 | 0 | 0 | 0 | 0 | 22.6202 | 0 | 0 | 0 | 0 | 0 | 56.3219
3894 | 56.4809 | 0 | 0 | 0 | 0 | 28.2404 | 0 | 0 | 0 | 0 | 0 | 105.223
3895 | 90.3449 | 0 | 42.9 | 0 | 56.3 | 45.1724 | 0 | 0 | 0 | 0 | 0 | 54.4849
3896 | 168.3133 | 0.7 | 43 | 0 | 37.6 | 84.1567 | 0 | 0 | 1 | 0 | 0 | 55.2866
3897 | 269.4578 | 2.1 | 43.2 | 0 | 0 | 134.7289 | 0 | 0 | 17.7 | 0 | 0 | 82.0814
3898 | 272.7089 | 3.5 | 43.4 | 0 | 0 | 136.3544 | 0 | 1.6 | 41.8 | 0 | 0 | 119.3397
3899 | 282.6812 | 3.5 | 43.4 | 0 | 0 | 141.3406 | 0 | 15.2 | 73.2 | 0 | 0 | 144.6599
3900 | 245.9294 | 2.8 | 43.3 | 0 | 0 | 122.9647 | 0 | 39.9 | 120.3 | 0 | 0 | 106.6716
3901 | 211.475 | 1.4 | 43.1 | 0 | 75.1 | 105.7375 | 172.7 | 46.8 | 152 | 0 | 0 | 89.4294
3902 | 209.8773 | 2.1 | 43.2 | 0 | 37.6 | 104.9387 | 180.3 | 58.1 | 173.5 | 0 | 0 | 133.306
3903 | 229.1629 | 3.5 | 43.4 | 0 | 0 | 114.5814 | 0 | 78.1 | 205 | 0 | 0 | 183.4361
3904 | 172.9076 | 2.8 | 43.3 | 0 | 0 | 86.4538 | 0 | 80.9 | 236.5 | 0 | 0 | 95.7484
3905 | 111.0096 | 2.1 | 43.2 | 0 | 0 | 55.5048 | 0 | 83.7 | 259.5 | 0 | 0 | 136.5617
3906 | 88.6657 | 0.7 | 43 | 0 | 37.6 | 44.3329 | 415.6 | 65.3 | 272.9 | 0 | 0 | 160.4391
3907 | 70.9375 | 0 | 42.9 | 0 | 75.1 | 35.4688 | 443.8 | 0 | 194.3 | 0 | 0 | 199.0484
3908 | 52.508 | 0 | 42.9 | 0 | 75.1 | 26.254 | 353.6 | 0 | 113 | 0 | 0 | 236.3976
3909 | 43.2246 | 0 | 42.9 | 0 | 75.1 | 21.6123 | 245.6 | 0 | 77.9 | 0 | 0 | 263.7161
3910 | 42.4597 | 0 | 42.9 | 0 | 93.9 | 21.2298 | 197 | 0 | 53.4 | 0 | 0 | 255.42
3911 | 44.2966 | 0 | 0 | 0 | 0 | 22.1483 | 0 | 0 | 0 | 0 | 0 | 157.2859
3912 | 42.7011 | 0 | 0 | 0 | 0 | 21.3506 | 0 | 0 | 0 | 0 | 0 | 121.7719
3913 | 43.5094 | 0 | 0 | 0 | 0 | 21.7547 | 0 | 0 | 0 | 0 | 0 | 77.0891
3914 | 41.3167 | 0 | 0 | 0 | 0 | 20.6583 | 0 | 0 | 0 | 0 | 0 | 72.4343
3915 | 40.7743 | 0 | 0 | 0 | 0 | 20.3872 | 0 | 0 | 0 | 0 | 0 | 60.5875
3916 | 42.8604 | 0 | 0 | 0 | 0 | 21.4302 | 0 | 0 | 0 | 0 | 0 | 56.6679
3917 | 42.4925 | 0 | 0 | 0 | 0 | 21.2463 | 0 | 0 | 0 | 0 | 0 | 56.7835
3918 | 63.1061 | 0 | 0 | 0 | 0 | 31.5531 | 0 | 0 | 0 | 0 | 0 | 60.3578
3919 | 108.07 | 0 | 42.9 | 0 | 56.3 | 54.035 | 158.8 | 0 | 23.4 | 0 | 0 | 83.4992
3920 | 215.6819 | 0.7 | 43 | 0 | 37.6 | 107.8409 | 111.9 | 70.7 | 57.4 | 0 | 0 | 104.7377
3921 | 323.1379 | 2.1 | 43.2 | 0 | 0 | 161.569 | 0 | 88.4 | 58.8 | 0 | 0 | 101.7448
3922 | 391.7802 | 3.5 | 43.4 | 0 | 0 | 195.8901 | 0 | 125.9 | 58.4 | 0 | 0 | 220.5695
3923 | 368.0385 | 3.5 | 43.4 | 0 | 0 | 184.0193 | 0 | 141.2 | 60.7 | 0 | 0 | 108.7297
3924 | 339.1088 | 2.8 | 43.3 | 0 | 0 | 169.5544 | 0 | 148 | 63.3 | 0 | 0 | 144.2802
3925 | 291.8302 | 1.4 | 43.1 | 0 | 75.1 | 145.9151 | 172.4 | 119.4 | 80.2 | 0 | 0 | 89.7832
3926 | 295.1135 | 2.1 | 43.2 | 0 | 37.6 | 147.5567 | 161 | 124.9 | 100.6 | 0 | 0 | 249.9305
3927 | 268.497 | 3.5 | 43.4 | 0 | 0 | 134.2485 | 0 | 156.2 | 124.1 | 0 | 0 | 194.2336
3928 | 211.7902 | 2.8 | 43.3 | 0 | 0 | 105.8951 | 0 | 144.7 | 149.9 | 0 | 0 | 99.5913
3929 | 173.7236 | 2.1 | 43.2 | 0 | 0 | 86.8618 | 0 | 123.8 | 177.7 | 0 | 0 | 123.8118
3930 | 151.9835 | 0.7 | 43 | 0 | 37.6 | 75.9918 | 281.1 | 87.1 | 175.2 | 0 | 0 | 225.4104
3931 | 114.8582 | 0 | 42.9 | 0 | 75.1 | 57.4291 | 312.3 | 0 | 85.5 | 0 | 0 | 266.1051
3932 | 66.3423 | 0 | 42.9 | 0 | 75.1 | 33.1712 | 222.5 | 0 | 24.2 | 0 | 0 | 524.5687
3933 | 39.5579 | 0 | 42.9 | 0 | 75.1 | 19.7789 | 141.6 | 0 | 19.1 | 0 | 0 | 337.0576
3934 | 40.3643 | 0 | 42.9 | 0 | 93.9 | 20.1822 | 84.3 | 0 | 5.7 | 0 | 0 | 195.0117
3935 | 43.3675 | 0 | 0 | 0 | 0 | 21.6837 | 0 | 0 | 0 | 0 | 0 | 124.7929
3936 | 40.0634 | 0 | 0 | 0 | 0 | 20.0317 | 0 | 0 | 0 | 0 | 0 | 110.6587
3937 | 41.0347 | 0 | 0 | 0 | 0 | 20.5173 | 0 | 0 | 0 | 0 | 0 | 65.6407
3938 | 45.1929 | 0 | 0 | 0 | 0 | 22.5964 | 0 | 0 | 0 | 0 | 0 | 47.4794
3939 | 39.5213 | 0 | 0 | 0 | 0 | 19.7607 | 0 | 0 | 0 | 0 | 0 | 47.9405
3940 | 41.4531 | 0 | 0 | 0 | 0 | 20.7265 | 0 | 0 | 0 | 0 | 0 | 51.1566
3941 | 42.4588 | 0 | 0 | 0 | 0 | 21.2294 | 0 | 0 | 0 | 0 | 0 | 60.1262
3942 | 57.7153 | 0 | 0 | 0 | 0 | 28.8577 | 0 | 0 | 0 | 0 | 0 | 49.0884
3943 | 94.1709 | 0 | 42.9 | 0 | 56.3 | 47.0854 | 0.6 | 0 | 0 | 0 | 0 | 54.2562
3944 | 167.9675 | 0.7 | 43 | 0 | 37.6 | 83.9837 | 0 | 39.1 | 1.5 | 0 | 0 | 135.5112
3945 | 254.7907 | 2.1 | 43.2 | 0 | 0 | 127.3953 | 0 | 44 | 6.4 | 0 | 0 | 162.4603
3946 | 287.2972 | 3.5 | 43.4 | 0 | 0 | 143.6486 | 0 | 53.2 | 7.9 | 0 | 0 | 90.6237
3947 | 289.1462 | 3.5 | 43.4 | 0 | 0 | 144.5731 | 0 | 62.2 | 13.7 | 0 | 0 | 113.0872
3948 | 272.0605 | 2.8 | 43.3 | 0 | 0 | 136.0303 | 0 | 83.1 | 19 | 0 | 0 | 160.6924
3949 | 230.9558 | 1.4 | 43.1 | 0 | 75.1 | 115.4779 | 15.9 | 86.1 | 26.2 | 0 | 0 | 176.1457
3950 | 208.9705 | 2.1 | 43.2 | 0 | 37.6 | 104.4853 | 10.2 | 92.5 | 35.7 | 0 | 0 | 164.2581
3951 | 213.2552 | 3.5 | 43.4 | 0 | 0 | 106.6276 | 0 | 116.9 | 42.8 | 0 | 0 | 145.6171
3952 | 176.3434 | 2.8 | 43.3 | 0 | 0 | 88.1717 | 0 | 127.4 | 42.9 | 0 | 0 | 84.4497
3953 | 137.9381 | 2.1 | 43.2 | 0 | 0 | 68.9691 | 0 | 133.1 | 41.7 | 0 | 0 | 123.8746
3954 | 93.1175 | 0.7 | 43 | 0 | 37.6 | 46.5587 | 10.4 | 121.5 | 37.9 | 0 | 0 | 114.8932
3955 | 71.2816 | 0 | 42.9 | 0 | 75.1 | 35.6408 | 21.2 | 31.5 | 2.2 | 0 | 0 | 153.5044
3956 | 51.2265 | 0 | 42.9 | 0 | 75.1 | 25.6132 | 3.2 | 9.1 | 0 | 0 | 0 | 189.3397
3957 | 45.7015 | 0 | 42.9 | 0 | 75.1 | 22.8507 | 0 | 0.9 | 0 | 0 | 0 | 180.8004
3958 | 42.7994 | 0 | 42.9 | 0 | 93.9 | 21.3997 | 0 | 0 | 0 | 0 | 0 | 175.4452
3959 | 42.9407 | 0 | 0 | 0 | 0 | 21.4703 | 0 | 0 | 0 | 0 | 0 | 163.4716
3960 | 40.0138 | 0 | 0 | 0 | 0 | 20.0069 | 0 | 0 | 0 | 0 | 0 | 149.2821
3961 | 40.9947 | 0 | 0 | 0 | 0 | 20.4973 | 0 | 0 | 0 | 0 | 0 | 61.9703
3962 | 41.4636 | 0 | 0 | 0 | 0 | 20.7318 | 0 | 0 | 0 | 0 | 0 | 47.7102
3963 | 41.5011 | 0 | 0 | 0 | 0 | 20.7506 | 0 | 0 | 0 | 0 | 0 | 47.9409
3964 | 40.4089 | 0 | 0 | 0 | 0 | 20.2045 | 0 | 0 | 0 | 0 | 0 | 49.2049
3965 | 41.0595 | 0 | 0 | 0 | 0 | 20.5297 | 0 | 0 | 0 | 0 | 0 | 55.9777
3966 | 60.2418 | 0 | 0 | 0 | 0 | 30.1209 | 0 | 0 | 0 | 0 | 0 | 56.206
3967 | 111.1298 | 0 | 42.9 | 0 | 56.3 | 55.5649 | 0 | 0 | 0 | 0 | 0 | 60.9329
3968 | 164.0172 | 0.7 | 43 | 0 | 37.6 | 82.0086 | 0 | 18.1 | 0 | 0 | 0 | 120.3066
3969 | 253.3254 | 2.1 | 43.2 | 0 | 0 | 126.6627 | 0 | 12.3 | 0 | 0 | 0 | 109.2115
3970 | 333.4769 | 3.5 | 43.4 | 0 | 0 | 166.7385 | 0 | 39.6 | 0 | 0 | 0 | 185.8428
3971 | 310.7646 | 3.5 | 43.4 | 0 | 0 | 155.3823 | 0 | 63.2 | 1.7 | 0 | 0 | 134.6739
3972 | 271.1512 | 2.8 | 43.3 | 0 | 0 | 135.5756 | 0 | 85.9 | 8.8 | 0 | 0 | 120.1737
3973 | 262.2006 | 1.4 | 43.1 | 0 | 75.1 | 131.1003 | 0 | 92.6 | 25.4 | 0 | 0 | 226.4979
3974 | 265.5469 | 2.1 | 43.2 | 0 | 37.6 | 132.7734 | 0 | 94.7 | 42.8 | 0 | 0 | 129.5525
3975 | 246.1318 | 3.5 | 43.4 | 0 | 0 | 123.0659 | 0 | 89.6 | 47.1 | 0 | 0 | 121.3433
3976 | 225.49 | 2.8 | 43.3 | 0 | 0 | 112.745 | 0 | 75 | 60.4 | 0 | 0 | 108.9701
3977 | 185.6699 | 2.1 | 43.2 | 0 | 0 | 92.835 | 0 | 70.9 | 58.7 | 0 | 0 | 66.6787
3978 | 143.7916 | 0.7 | 43 | 0 | 37.6 | 71.8958 | 1 | 59.3 | 52.2 | 0 | 0 | 126.7364
3979 | 111.6276 | 0 | 42.9 | 0 | 75.1 | 55.8138 | 5.9 | 0 | 2.5 | 0 | 0 | 120.0466
3980 | 77.4298 | 0 | 42.9 | 0 | 75.1 | 38.7149 | 0 | 0 | 0 | 0 | 0 | 146.9986
3981 | 46.9985 | 0 | 42.9 | 0 | 75.1 | 23.4993 | 0 | 0 | 0 | 0 | 0 | 173.1295
3982 | 47.415 | 0 | 42.9 | 0 | 93.9 | 23.7075 | 0 | 0 | 0 | 0 | 0 | 157.8274
3983 | 41.7404 | 0 | 0 | 0 | 0 | 20.8702 | 0 | 0 | 0 | 0 | 0 | 131.3589
3984 | 40.9051 | 0 | 0 | 0 | 0 | 20.4526 | 0 | 0 | 0 | 0 | 0 | 90.978
3985 | 40.5862 | 0 | 0 | 0 | 0 | 20.2931 | 0 | 0 | 0 | 0 | 0 | 58.7506
3986 | 40.8245 | 0 | 0 | 0 | 0 | 20.4123 | 0 | 0 | 0 | 0 | 0 | 50.5819
3987 | 44.142 | 0 | 0 | 0 | 0 | 22.071 | 0 | 0 | 0 | 0 | 0 | 49.6625
3988 | 41.8619 | 0 | 0 | 0 | 0 | 20.9309 | 0 | 0 | 0 | 0 | 0 | 49.7771
3989 | 42.676 | 0 | 0 | 0 | 0 | 21.338 | 0 | 0 | 0 | 0 | 0 | 55.6324
3990 | 47.1234 | 0 | 0 | 0 | 0 | 23.5617 | 0 | 0 | 0 | 0 | 0 | 46.3355
3991 | 58.4037 | 0 | 42.9 | 0 | 56.3 | 29.2018 | 0 | 0 | 0 | 0 | 0 | 51.0421
3992 | 61.1849 | 0 | 42.9 | 0 | 37.6 | 30.5925 | 0 | 0 | 0 | 0 | 0 | 74.2779
3993 | 59.5256 | 0 | 42.9 | 0 | 0 | 29.7628 | 0 | 0 | 0 | 0 | 0 | 139.7324
3994 | 57.4193 | 0 | 42.9 | 0 | 0 | 28.7097 | 0 | 0 | 0 | 0 | 0 | 245.9407
3995 | 61.8987 | 0 | 42.9 | 0 | 0 | 30.9493 | 0 | 0 | 0 | 0 | 0 | 150.9941
3996 | 72.3557 | 0 | 42.9 | 0 | 0 | 36.1779 | 0 | 0 | 0 | 0 | 0 | 129.1424
3997 | 73.9553 | 0 | 42.9 | 0 | 75.1 | 36.9776 | 0 | 0 | 0 | 0 | 0 | 110.2978
3998 | 78.1367 | 0 | 42.9 | 0 | 37.6 | 39.0684 | 0 | 0.3 | 0 | 0 | 0 | 131.9555
3999 | 81.3903 | 0 | 42.9 | 0 | 0 | 40.6951 | 0 | 2.7 | 0 | 0 | 0 | 116.8089
4000 | 84.8602 | 0 | 42.9 | 0 | 0 | 42.4301 | 0 | 4.5 | 0 | 0 | 0 | 74.9737
4001 | 84.638 | 0 | 42.9 | 0 | 0 | 42.319 | 0 | 6.1 | 0 | 0 | 0 | 115.9936
4002 | 80.2293 | 0 | 42.9 | 0 | 37.6 | 40.1147 | 0 | 4.3 | 0 | 0 | 0 | 171.5104
4003 | 76.1424 | 0 | 42.9 | 0 | 75.1 | 38.0712 | 0 | 1.1 | 0 | 0 | 0 | 185.4878
4004 | 70.5883 | 0 | 42.9 | 0 | 75.1 | 35.2941 | 0 | 0 | 0 | 0 | 0 | 143.6758
4005 | 56.5853 | 0 | 42.9 | 0 | 75.1 | 28.2927 | 0 | 0 | 0 | 0 | 0 | 208.938
4006 | 49.2656 | 0 | 42.9 | 0 | 93.9 | 24.6328 | 0 | 0 | 0 | 0 | 0 | 289.5153
4007 | 44.7038 | 0 | 0 | 0 | 0 | 22.3519 | 0 | 0 | 0 | 0 | 0 | 154.8597
4008 | 42.8313 | 0 | 0 | 0 | 0 | 21.4156 | 0 | 0 | 0 | 0 | 0 | 75.3224
4009 | 41.8804 | 0 | 0 | 0 | 0 | 20.9402 | 0 | 0 | 0 | 0 | 0 | 60.3581
4010 | 42.5025 | 0 | 0 | 0 | 0 | 21.2512 | 0 | 0 | 0 | 0 | 0 | 45.9934
4011 | 41.9883 | 0 | 0 | 0 | 0 | 20.9942 | 0 | 0 | 0 | 0 | 0 | 46.1079
4012 | 43.7251 | 0 | 0 | 0 | 0 | 21.8626 | 0 | 0 | 0 | 0 | 0 | 53.4536
4013 | 43.9548 | 0 | 0 | 0 | 0 | 21.9774 | 0 | 0 | 0 | 0 | 0 | 76.2634
4014 | 47.1135 | 0 | 0 | 0 | 0 | 23.5567 | 0 | 0 | 0 | 0 | 0 | 85.0403
4015 | 56.9833 | 0 | 42.9 | 0 | 56.3 | 28.4916 | 0 | 0 | 0 | 0 | 0 | 76.8515
4016 | 62.0201 | 0 | 42.9 | 0 | 37.6 | 31.0101 | 0 | 0 | 0 | 0 | 0 | 56.4374
4017 | 60.0775 | 0 | 42.9 | 0 | 0 | 30.0388 | 0 | 0 | 0 | 0 | 0 | 110.6615
4018 | 56.4865 | 0 | 42.9 | 0 | 0 | 28.2432 | 0 | 0 | 0 | 0 | 0 | 101.9768
4019 | 56.3182 | 0 | 42.9 | 0 | 0 | 28.1591 | 0 | 0 | 0.8 | 0 | 0 | 104.3777
4020 | 56.656 | 0 | 42.9 | 0 | 0 | 28.328 | 0 | 0 | 15.5 | 0 | 0 | 110.7815
4021 | 53.5236 | 0 | 42.9 | 0 | 75.1 | 26.7618 | 8.2 | 0 | 44.9 | 0 | 0 | 97.1956
4022 | 57.0859 | 0 | 42.9 | 0 | 37.6 | 28.5429 | 13.9 | 0 | 70.4 | 0 | 0 | 199.4662
4023 | 64.4611 | 0 | 42.9 | 0 | 0 | 32.2305 | 0 | 0 | 97.6 | 0 | 0 | 84.4447
4024 | 66.3783 | 0 | 42.9 | 0 | 0 | 33.1891 | 0 | 0.5 | 133.6 | 0 | 0 | 106.553
4025 | 63.7638 | 0 | 42.9 | 0 | 0 | 31.8819 | 0 | 9.9 | 162.1 | 0 | 0 | 99.3504
4026 | 55.698 | 0 | 42.9 | 0 | 37.6 | 27.849 | 196.9 | 22.4 | 180.8 | 0 | 0 | 173.0139
4027 | 54.5414 | 0 | 42.9 | 0 | 75.1 | 27.2707 | 257.1 | 30.1 | 176.7 | 0 | 0 | 110.9035
4028 | 50.482 | 0 | 42.9 | 0 | 75.1 | 25.241 | 178.1 | 3.6 | 89.6 | 0 | 0 | 128.7344
4029 | 41.7918 | 0 | 42.9 | 0 | 75.1 | 20.8959 | 78.2 | 0 | 49.1 | 0 | 0 | 172.8412
4030 | 42.8945 | 0 | 42.9 | 0 | 93.9 | 21.4473 | 38.7 | 0 | 20.8 | 0 | 0 | 146.4614
4031 | 43.298 | 0 | 0 | 0 | 0 | 21.649 | 0 | 0 | 0 | 0 | 0 | 148.1202
4032 | 42.7622 | 0 | 0 | 0 | 0 | 21.3811 | 0 | 0 | 0 | 0 | 0 | 103.8938
4033 | 40.8803 | 0 | 0 | 0 | 0 | 20.4402 | 0 | 0 | 0 | 0 | 0 | 71.5096
4034 | 41.0421 | 0 | 0 | 0 | 0 | 20.5211 | 0 | 0 | 0 | 0 | 0 | 66.5633
4035 | 41.3914 | 0 | 0 | 0 | 0 | 20.6957 | 0 | 0 | 0 | 0 | 0 | 64.6085
4036 | 43.4161 | 0 | 0 | 0 | 0 | 21.7081 | 0 | 0 | 0 | 0 | 0 | 58.4038
4037 | 40.404 | 0 | 0 | 0 | 0 | 20.202 | 0 | 0 | 0 | 0 | 0 | 63.349
4038 | 53.6714 | 0 | 0 | 0 | 0 | 26.8357 | 0 | 0 | 0 | 0 | 0 | 53.2234
4039 | 85.9018 | 0 | 42.9 | 0 | 56.3 | 42.9509 | 0 | 0 | 0 | 0 | 0 | 54.7139
4040 | 179.0258 | 0.7 | 43 | 0 | 37.6 | 89.5129 | 1.9 | 108.6 | 21.1 | 0 | 0 | 55.5169
4041 | 302.7717 | 2.1 | 43.2 | 0 | 0 | 151.3858 | 0 | 125.6 | 62 | 0 | 0 | 76.499
4042 | 334.1767 | 3.5 | 43.4 | 0 | 0 | 167.0884 | 0 | 151 | 118.8 | 0 | 0 | 91.8176
4043 | 302.6086 | 3.5 | 43.4 | 0 | 0 | 151.3043 | 0 | 155.7 | 186.2 | 0 | 0 | 98.3966
4044 | 292.4159 | 2.8 | 43.3 | 0 | 0 | 146.208 | 0 | 149.8 | 242.9 | 0 | 0 | 181.2363
4045 | 267.3379 | 1.4 | 43.1 | 0 | 75.1 | 133.669 | 425 | 114.9 | 279 | 0 | 0 | 165.9014
4046 | 250.8634 | 2.1 | 43.2 | 0 | 37.6 | 125.4317 | 399 | 122.7 | 306.3 | 0 | 0 | 130.4012
4047 | 253.2138 | 3.5 | 43.4 | 0 | 0 | 126.6069 | 0 | 139.7 | 344.5 | 0 | 0 | 130.9289
4048 | 211.801 | 2.8 | 43.3 | 0 | 0 | 105.9005 | 3.5 | 124.5 | 354.4 | 0 | 0 | 199.8768
4049 | 160.1844 | 2.1 | 43.2 | 0 | 0 | 80.0922 | 16.4 | 111.8 | 364.4 | 0 | 0 | 165.9618
4050 | 130.2412 | 0.7 | 43 | 0 | 37.6 | 65.1206 | 690.7 | 87.8 | 369.4 | 0 | 0 | 228.9668
4051 | 95.4915 | 0 | 42.9 | 0 | 75.1 | 47.7457 | 687.3 | 0 | 270.2 | 0 | 0 | 188.5228
4052 | 74.3439 | 0 | 42.9 | 0 | 75.1 | 37.1719 | 580.4 | 0 | 185 | 0 | 0 | 180.5129
4053 | 54.0734 | 0 | 42.9 | 0 | 75.1 | 27.0367 | 462.4 | 0 | 139.1 | 0 | 0 | 172.7707
4054 | 42.6432 | 0 | 42.9 | 0 | 93.9 | 21.3216 | 412.9 | 0 | 100.4 | 0 | 0 | 156.7857
4055 | 42.7222 | 0 | 0 | 0 | 0 | 21.3611 | 0 | 0 | 0 | 0 | 0 | 144.3266
4056 | 42.6088 | 0 | 0 | 0 | 0 | 21.3044 | 0 | 0 | 0 | 0 | 0 | 90.7418
4057 | 42.1011 | 0 | 0 | 0 | 0 | 21.0506 | 0 | 0 | 0 | 0 | 0 | 67.4853
4058 | 40.9476 | 0 | 0 | 0 | 0 | 20.4738 | 0 | 0 | 0 | 0 | 0 | 51.5006
4059 | 42.292 | 0 | 0 | 0 | 0 | 21.146 | 0 | 0 | 0 | 0 | 0 | 46.1075
4060 | 41.4382 | 0 | 0 | 0 | 0 | 20.7191 | 0 | 0 | 0 | 0 | 0 | 47.9386
4061 | 43.1976 | 0 | 0 | 0 | 0 | 21.5988 | 0 | 0 | 0 | 0 | 0 | 55.0575
4062 | 58.5351 | 0 | 0 | 0 | 0 | 29.2675 | 0 | 0 | 0 | 0 | 0 | 86.1005
4063 | 86.9109 | 0 | 42.9 | 0 | 56.3 | 43.4555 | 374.4 | 0 | 68.2 | 0 | 0 | 73.01
4064 | 134.0684 | 0.7 | 43 | 0 | 37.6 | 67.0342 | 406.6 | 90.7 | 177.7 | 0 | 0 | 60.9322
4065 | 228.1826 | 2.1 | 43.2 | 0 | 0 | 114.0913 | 0 | 106.4 | 256.7 | 0 | 0 | 72.318
4066 | 257.3677 | 3.5 | 43.4 | 0 | 0 | 128.6839 | 4.3 | 149.3 | 327.7 | 0 | 0 | 51.2695
4067 | 270.642 | 3.5 | 43.4 | 0 | 0 | 135.321 | 43.5 | 178.1 | 370.4 | 0 | 0 | 68.8636
4068 | 264.0754 | 2.8 | 43.3 | 0 | 0 | 132.0377 | 96.9 | 190.2 | 401.9 | 0 | 0 | 270.1994
4069 | 255.8881 | 1.4 | 43.1 | 0 | 75.1 | 127.9441 | 968.8 | 160.1 | 420.5 | 0 | 0 | 135.23
4070 | 251.9583 | 2.1 | 43.2 | 0 | 37.6 | 125.9792 | 840.4 | 178.7 | 446.3 | 0 | 0 | 91.8182
4071 | 253.6279 | 3.5 | 43.4 | 0 | 0 | 126.8139 | 194.2 | 236.7 | 496.1 | 0 | 0 | 71.8579
4072 | 227.2429 | 2.8 | 43.3 | 0 | 0 | 113.6215 | 307.8 | 246.1 | 507.8 | 0 | 0 | 101.6204
4073 | 180.2987 | 2.1 | 43.2 | 0 | 0 | 90.1493 | 361.5 | 221.7 | 505.8 | 0 | 0 | 96.5886
4074 | 135.4665 | 0.7 | 43 | 0 | 37.6 | 67.7333 | 1140.3 | 168.6 | 502.8 | 0 | 0 | 168.6229
4075 | 101.2697 | 0 | 42.9 | 0 | 75.1 | 50.6348 | 1123 | 49.5 | 397.5 | 0 | 0 | 240.8638
4076 | 84.7839 | 0 | 42.9 | 0 | 75.1 | 42.392 | 998.2 | 26.5 | 310.9 | 0 | 0 | 206.5072
4077 | 65.2176 | 0 | 42.9 | 0 | 75.1 | 32.6088 | 856.2 | 19.8 | 256.1 | 0 | 0 | 224.674
4078 | 63.3478 | 0 | 42.9 | 0 | 93.9 | 31.6739 | 809.4 | 14.3 | 221.2 | 0 | 0 | 197.7419
4079 | 64.8764 | 0 | 0 | 0 | 0 | 32.4382 | 109.1 | 9.7 | 51.5 | 0 | 0 | 117.4834
4080 | 61.0132 | 0 | 0 | 0 | 0 | 30.5066 | 107.1 | 6.5 | 47.4 | 0 | 0 | 75.4407
4081 | 59.7001 | 0 | 0 | 0 | 0 | 29.85 | 76.7 | 4 | 32.2 | 0 | 0 | 58.9781
4082 | 62.0369 | 0 | 0 | 0 | 0 | 31.0184 | 47 | 1.6 | 17.5 | 0 | 0 | 49.3195
4083 | 60.817 | 0 | 0 | 0 | 0 | 30.4085 | 28.9 | 0.6 | 10 | 0 | 0 | 47.1342
4084 | 58.4706 | 0 | 0 | 0 | 0 | 29.2353 | 18.3 | 0 | 4.3 | 0 | 0 | 50.3526
4085 | 62.5163 | 0 | 0 | 0 | 0 | 31.2582 | 12.4 | 0 | 0.4 | 0 | 0 | 58.8642
4086 | 75.0375 | 0 | 0 | 0 | 0 | 37.5188 | 12 | 0 | 0.6 | 0 | 0 | 63.4636
4087 | 98.2216 | 0 | 42.9 | 0 | 56.3 | 49.1108 | 863.9 | 13.3 | 161.2 | 0 | 0 | 102.58
4088 | 179.4445 | 0.7 | 43 | 0 | 37.6 | 89.7223 | 752.8 | 139.2 | 255.6 | 0 | 0 | 82.7884
4089 | 250.9873 | 2.1 | 43.2 | 0 | 0 | 125.4937 | 29.2 | 131.6 | 299.7 | 0 | 0 | 62.4309
4090 | 263.5562 | 3.5 | 43.4 | 0 | 0 | 131.7781 | 73.8 | 174.3 | 325.5 | 0 | 0 | 99.8345
4091 | 275.1424 | 3.5 | 43.4 | 0 | 0 | 137.5712 | 111 | 189.1 | 352.1 | 0 | 0 | 193.8286
4092 | 262.6011 | 2.8 | 43.3 | 0 | 0 | 131.3005 | 151.2 | 174.2 | 383.1 | 0 | 0 | 111.6307
4093 | 251.3874 | 1.4 | 43.1 | 0 | 75.1 | 125.6937 | 1112.5 | 134.4 | 400.1 | 0 | 0 | 225.0517
4094 | 248.5901 | 2.1 | 43.2 | 0 | 37.6 | 124.295 | 924.1 | 147.1 | 413.7 | 0 | 0 | 144.4556
4095 | 249.4489 | 3.5 | 43.4 | 0 | 0 | 124.7244 | 155.6 | 197.8 | 446.3 | 0 | 0 | 254.1003
4096 | 225.6214 | 2.8 | 43.3 | 0 | 0 | 112.8107 | 222.2 | 196.3 | 442.7 | 0 | 0 | 246.6647
4097 | 177.5397 | 2.1 | 43.2 | 0 | 0 | 88.7699 | 229.9 | 167.9 | 419.8 | 0 | 0 | 218.8198
4098 | 140.4175 | 0.7 | 43 | 0 | 37.6 | 70.2088 | 1070.8 | 126.9 | 386.6 | 0 | 0 | 222.7258
4099 | 114.1029 | 0 | 42.9 | 0 | 75.1 | 57.0515 | 975.4 | 8.6 | 251.9 | 0 | 0 | 201.3191
4100 | 93.7336 | 0 | 42.9 | 0 | 75.1 | 46.8668 | 838.2 | 0 | 164.9 | 0 | 0 | 188.6969
4101 | 72.3973 | 0 | 42.9 | 0 | 75.1 | 36.1986 | 746.5 | 0 | 146.5 | 0 | 0 | 280.3894
4102 | 65.9369 | 0 | 42.9 | 0 | 93.9 | 32.9685 | 696.6 | 0 | 120.9 | 0 | 0 | 286.5908
4103 | 67.3366 | 0 | 0 | 0 | 0 | 33.6683 | 14.6 | 0 | 3.1 | 0 | 0 | 210.2545
4104 | 67.1187 | 0 | 0 | 0 | 0 | 33.5593 | 14.9 | 0 | 0.8 | 0 | 0 | 117.6239
4105 | 65.0168 | 0 | 0 | 0 | 0 | 32.5084 | 6.6 | 0 | 0 | 0 | 0 | 64.2654
4106 | 63.9259 | 0 | 0 | 0 | 0 | 31.9629 | 0.7 | 0 | 0 | 0 | 0 | 55.8631
4107 | 62.9828 | 0 | 0 | 0 | 0 | 31.4914 | 0 | 0 | 0 | 0 | 0 | 48.5142
4108 | 59.1772 | 0 | 0 | 0 | 0 | 29.5886 | 0 | 0 | 0 | 0 | 0 | 46.5634
4109 | 60.9484 | 0 | 0 | 0 | 0 | 30.4742 | 0 | 0 | 0 | 0 | 0 | 72.3197
4110 | 82.7022 | 0 | 0 | 0 | 0 | 41.3511 | 0 | 0 | 0 | 0 | 0 | 51.3845
4111 | 120.4997 | 0 | 42.9 | 0 | 56.3 | 60.2499 | 637.7 | 0 | 89.5 | 0 | 0 | 53.2231
4112 | 147.7934 | 0.7 | 43 | 0 | 37.6 | 73.8967 | 491 | 97.7 | 163.6 | 0 | 0 | 52.7647
4113 | 202.6769 | 2.1 | 43.2 | 0 | 0 | 101.3385 | 0 | 92.9 | 196.5 | 0 | 0 | 60.2431
4114 | 254.0258 | 3.5 | 43.4 | 0 | 0 | 127.0129 | 3.1 | 127.2 | 239.5 | 0 | 0 | 62.6613
4115 | 259.2161 | 3.5 | 43.4 | 0 | 0 | 129.608 | 8.1 | 148.5 | 241.3 | 0 | 0 | 121.765
4116 | 269.2591 | 2.8 | 43.3 | 0 | 0 | 134.6296 | 16.3 | 147.9 | 261.1 | 0 | 0 | 180.4009
4117 | 261.22 | 1.4 | 43.1 | 0 | 75.1 | 130.61 | 814.3 | 114.8 | 297.9 | 0 | 0 | 132.3774
4118 | 265.2744 | 2.1 | 43.2 | 0 | 37.6 | 132.6372 | 697.2 | 128.4 | 314.9 | 0 | 0 | 133.7597
4119 | 249.6553 | 3.5 | 43.4 | 0 | 0 | 124.8276 | 33.6 | 179.6 | 342.3 | 0 | 0 | 217.4025
4120 | 213.439 | 2.8 | 43.3 | 0 | 0 | 106.7195 | 60.9 | 175.8 | 336.1 | 0 | 0 | 71.1643
4121 | 174.2267 | 2.1 | 43.2 | 0 | 0 | 87.1133 | 57.1 | 147.3 | 301.9 | 0 | 0 | 180.0008
4122 | 142.0666 | 0.7 | 43 | 0 | 37.6 | 71.0333 | 768.8 | 110.4 | 267.7 | 0 | 0 | 119.2024
4123 | 107.4718 | 0 | 42.9 | 0 | 75.1 | 53.7359 | 739.8 | 3.1 | 156 | 0 | 0 | 114.4059
4124 | 81.3475 | 0 | 42.9 | 0 | 75.1 | 40.6738 | 622.5 | 0 | 85 | 0 | 0 | 104.2552
4125 | 68.4851 | 0 | 42.9 | 0 | 75.1 | 34.2426 | 517.4 | 0 | 77.2 | 0 | 0 | 208.4202
4126 | 64.9625 | 0 | 42.9 | 0 | 93.9 | 32.4813 | 449.5 | 0 | 60.8 | 0 | 0 | 160.5066
4127 | 66.4272 | 0 | 0 | 0 | 0 | 33.2136 | 0 | 0 | 0 | 0 | 0 | 111.6287
4128 | 61.5924 | 0 | 0 | 0 | 0 | 30.7962 | 0 | 0 | 0 | 0 | 0 | 80.8987
4129 | 62.1481 | 0 | 0 | 0 | 0 | 31.0741 | 0 | 0 | 0 | 0 | 0 | 69.4382
4130 | 59.5842 | 0 | 0 | 0 | 0 | 29.7921 | 0 | 0 | 0 | 0 | 0 | 67.9424
4131 | 58.7536 | 0 | 0 | 0 | 0 | 29.3768 | 0 | 0 | 0 | 0 | 0 | 58.6338
4132 | 56.0966 | 0 | 0 | 0 | 0 | 28.0483 | 0 | 0 | 0 | 0 | 0 | 47.4791
4133 | 54.8259 | 0 | 0 | 0 | 0 | 27.413 | 0 | 0 | 0 | 0 | 0 | 51.9593
4134 | 76.1737 | 0 | 0 | 0 | 0 | 38.0868 | 0 | 0 | 0 | 0 | 0 | 50.467
4135 | 104.98 | 0 | 42.9 | 0 | 56.3 | 52.49 | 235.5 | 0 | 17.3 | 0 | 0 | 52.7642
4136 | 137.2703 | 0.7 | 43 | 0 | 37.6 | 68.6351 | 259.2 | 61.7 | 85.2 | 0 | 0 | 60.2435
4137 | 215.9726 | 2.1 | 43.2 | 0 | 0 | 107.9863 | 0 | 68.8 | 139 | 0 | 0 | 75.2067
4138 | 279.8864 | 3.5 | 43.4 | 0 | 0 | 139.9432 | 0 | 108.1 | 205.9 | 0 | 0 | 79.4799
4139 | 293.9311 | 3.5 | 43.4 | 0 | 0 | 146.9656 | 0 | 127.7 | 269.7 | 0 | 0 | 107.2734
4140 | 280.7284 | 2.8 | 43.3 | 0 | 0 | 140.3642 | 9.1 | 136.3 | 310.3 | 0 | 0 | 70.1291
4141 | 251.9602 | 1.4 | 43.1 | 0 | 75.1 | 125.9801 | 790.8 | 125.9 | 337.5 | 0 | 0 | 76.7366
4142 | 248.525 | 2.1 | 43.2 | 0 | 37.6 | 124.2625 | 676.1 | 134 | 363.6 | 0 | 0 | 74.5103
4143 | 232.4831 | 3.5 | 43.4 | 0 | 0 | 116.2415 | 72.3 | 171.6 | 395.5 | 0 | 0 | 114.6531
4144 | 191.3954 | 2.8 | 43.3 | 0 | 0 | 95.6977 | 140.9 | 178 | 404.3 | 0 | 0 | 92.411
4145 | 150.1857 | 2.1 | 43.2 | 0 | 0 | 75.0928 | 182 | 172.1 | 407.6 | 0 | 0 | 91.8202
4146 | 115.4514 | 0.7 | 43 | 0 | 37.6 | 57.7257 | 923.8 | 120.9 | 403.2 | 0 | 0 | 128.8334
4147 | 91.6211 | 0 | 42.9 | 0 | 75.1 | 45.8106 | 883.1 | 15.4 | 298 | 0 | 0 | 112.3625
4148 | 78.6689 | 0 | 42.9 | 0 | 75.1 | 39.3344 | 754.3 | 0.8 | 209.8 | 0 | 0 | 166.8178
4149 | 62.6973 | 0 | 42.9 | 0 | 75.1 | 31.3487 | 633.4 | 0.1 | 168.2 | 0 | 0 | 179.7328
4150 | 58.0624 | 0 | 42.9 | 0 | 93.9 | 29.0312 | 590.2 | 0 | 135.4 | 0 | 0 | 120.7114
4151 | 59.0371 | 0 | 0 | 0 | 0 | 29.5186 | 9.5 | 0 | 1.1 | 0 | 0 | 146.9127
4152 | 58.4632 | 0 | 0 | 0 | 0 | 29.2316 | 2.6 | 0 | 0 | 0 | 0 | 99.1088
4153 | 56.0693 | 0 | 0 | 0 | 0 | 28.0347 | 0 | 0 | 0 | 0 | 0 | 67.2535
4154 | 58.7632 | 0 | 0 | 0 | 0 | 29.3816 | 0 | 0 | 0 | 0 | 0 | 56.553
4155 | 55.019 | 0 | 0 | 0 | 0 | 27.5095 | 0 | 0 | 0 | 0 | 0 | 50.8118
4156 | 56.3541 | 0 | 0 | 0 | 0 | 28.1771 | 0 | 0 | 0 | 0 | 0 | 60.5881
4157 | 55.3165 | 0 | 0 | 0 | 0 | 27.6583 | 0 | 0 | 0 | 0 | 0 | 55.7493
4158 | 64.917 | 0 | 0 | 0 | 0 | 32.4585 | 0 | 0 | 0 | 0 | 0 | 90.1402
4159 | 88.8715 | 0 | 42.9 | 0 | 56.3 | 44.4358 | 402.6 | 0.4 | 54.8 | 0 | 0 | 113.0853
4160 | 87.5432 | 0 | 42.9 | 0 | 37.6 | 43.7716 | 397 | 9.2 | 109.7 | 0 | 0 | 95.8707
4161 | 84.4588 | 0 | 42.9 | 0 | 0 | 42.2294 | 1 | 26.4 | 169.7 | 0 | 0 | 54.0269
4162 | 85.8938 | 0 | 42.9 | 0 | 0 | 42.9469 | 16.1 | 39 | 220.4 | 0 | 0 | 79.2421
4163 | 85.3424 | 0 | 42.9 | 0 | 0 | 42.6712 | 50.9 | 45.3 | 259.3 | 0 | 0 | 89.5485
4164 | 73.3955 | 0 | 42.9 | 0 | 0 | 36.6978 | 93.4 | 52.3 | 295.7 | 0 | 0 | 152.2386
4165 | 65.5012 | 0 | 42.9 | 0 | 75.1 | 32.7506 | 857 | 62.8 | 319.6 | 0 | 0 | 196.5917
4166 | 67.8727 | 0 | 42.9 | 0 | 37.6 | 33.9364 | 771.7 | 71.1 | 335.9 | 0 | 0 | 209.9796
4167 | 73.9965 | 0 | 42.9 | 0 | 0 | 36.9982 | 169.7 | 79.4 | 367 | 0 | 0 | 177.1185
4168 | 77.1276 | 0 | 42.9 | 0 | 0 | 38.5638 | 256.6 | 90.8 | 379.8 | 0 | 0 | 83.0312
4169 | 77.144 | 0 | 42.9 | 0 | 0 | 38.572 | 295.8 | 100.1 | 384.6 | 0 | 0 | 99.2303
4170 | 68.7377 | 0 | 42.9 | 0 | 37.6 | 34.3689 | 988.7 | 104.9 | 389.8 | 0 | 0 | 149.5605
4171 | 66.0718 | 0 | 42.9 | 0 | 75.1 | 33.0359 | 999.5 | 99.4 | 346 | 0 | 0 | 140.7182
4172 | 56.8277 | 0 | 42.9 | 0 | 75.1 | 28.4138 | 892.7 | 62.6 | 264.6 | 0 | 0 | 179.8376
4173 | 44.0025 | 0 | 42.9 | 0 | 75.1 | 22.0012 | 763.2 | 47.4 | 215.1 | 0 | 0 | 156.0714
4174 | 40.3773 | 0 | 42.9 | 0 | 93.9 | 20.1887 | 713 | 37.3 | 179.7 | 0 | 0 | 200.3441
4175 | 41.8634 | 0 | 0 | 0 | 0 | 20.9317 | 35.3 | 28.6 | 19.5 | 0 | 0 | 132.7868
4176 | 41.3917 | 0 | 0 | 0 | 0 | 20.6958 | 25.2 | 18.7 | 10.2 | 0 | 0 | 79.1211
4177 | 41.4481 | 0 | 0 | 0 | 0 | 20.7241 | 15.1 | 9.7 | 0.8 | 0 | 0 | 61.7421
4178 | 43.5627 | 0 | 0 | 0 | 0 | 21.7814 | 5.1 | 2.4 | 0 | 0 | 0 | 57.8216
4179 | 40.2465 | 0 | 0 | 0 | 0 | 20.1233 | 0 | 0 | 0 | 0 | 0 | 49.0904
4180 | 42.2254 | 0 | 0 | 0 | 0 | 21.1127 | 0 | 0 | 0 | 0 | 0 | 47.3636
4181 | 42.7024 | 0 | 0 | 0 | 0 | 21.3512 | 0 | 0 | 0 | 0 | 0 | 57.937
4182 | 49.1488 | 0 | 0 | 0 | 0 | 24.5744 | 0 | 0.1 | 0 | 0 | 0 | 50.0073
4183 | 63.5552 | 0 | 42.9 | 0 | 56.3 | 31.7776 | 528.5 | 26.6 | 82.3 | 0 | 0 | 53.2242
4184 | 67.7385 | 0 | 42.9 | 0 | 37.6 | 33.8693 | 486 | 40.8 | 102.8 | 0 | 0 | 52.5368
4185 | 67.5256 | 0 | 42.9 | 0 | 0 | 33.7628 | 9 | 56 | 149.7 | 0 | 0 | 81.4893
4186 | 62.657 | 0 | 42.9 | 0 | 0 | 31.3285 | 35.4 | 67 | 194.9 | 0 | 0 | 63.6933
4187 | 65.1429 | 0 | 42.9 | 0 | 0 | 32.5715 | 73.8 | 71.6 | 227.2 | 0 | 0 | 128.6655
4188 | 62.2107 | 0 | 42.9 | 0 | 0 | 31.1054 | 115.1 | 76.5 | 258.7 | 0 | 0 | 148.8913
4189 | 65.1559 | 0 | 42.9 | 0 | 75.1 | 32.578 | 918.1 | 83.2 | 285.8 | 0 | 0 | 99.589
4190 | 63.4117 | 0 | 42.9 | 0 | 37.6 | 31.7058 | 814.4 | 91.6 | 299.5 | 0 | 0 | 136.0044
4191 | 66.7403 | 0 | 42.9 | 0 | 0 | 33.3701 | 167.6 | 95.7 | 311.1 | 0 | 0 | 111.996
4192 | 66.9913 | 0 | 42.9 | 0 | 0 | 33.4956 | 247.8 | 102.2 | 326 | 0 | 0 | 215.0039
4193 | 65.2836 | 0 | 42.9 | 0 | 0 | 32.6418 | 289.3 | 105.6 | 342.9 | 0 | 0 | 92.1737
4194 | 53.6352 | 0 | 42.9 | 0 | 37.6 | 26.8176 | 1032.4 | 104.8 | 357.7 | 0 | 0 | 212.9292
4195 | 46.6325 | 0 | 42.9 | 0 | 75.1 | 23.3162 | 1018.9 | 96.8 | 344.1 | 0 | 0 | 141.3804
4196 | 44.4122 | 0 | 42.9 | 0 | 75.1 | 22.2061 | 895.3 | 56.6 | 255.3 | 0 | 0 | 190.1382
4197 | 43.0392 | 0 | 42.9 | 0 | 75.1 | 21.5196 | 763.2 | 45 | 207.4 | 0 | 0 | 177.3484
4198 | 44.4627 | 0 | 42.9 | 0 | 93.9 | 22.2314 | 696.7 | 37.3 | 165.3 | 0 | 0 | 182.4928
4199 | 39.4764 | 0 | 0 | 0 | 0 | 19.7382 | 27.1 | 31.1 | 14.2 | 0 | 0 | 142.24
4200 | 44.08 | 0 | 0 | 0 | 0 | 22.04 | 23.1 | 24.2 | 6.8 | 0 | 0 | 155.0602
4201 | 43.1939 | 0 | 0 | 0 | 0 | 21.5969 | 12.9 | 18.8 | 0 | 0 | 0 | 71.0498
4202 | 41.2966 | 0 | 0 | 0 | 0 | 20.6483 | 3.1 | 14.6 | 0 | 0 | 0 | 54.8293
4203 | 40.6256 | 0 | 0 | 0 | 0 | 20.3128 | 0 | 11.2 | 0 | 0 | 0 | 47.5937
4204 | 42.151 | 0 | 0 | 0 | 0 | 21.0755 | 0 | 9 | 0 | 0 | 0 | 48.1672
4205 | 44.5978 | 0 | 0 | 0 | 0 | 22.2989 | 0 | 7.2 | 0 | 0 | 0 | 48.8608
4206 | 62.9781 | 0 | 0 | 0 | 0 | 31.4891 | 0 | 7 | 0 | 0 | 0 | 91.5811
4207 | 86.0054 | 0 | 42.9 | 0 | 56.3 | 43.0027 | 632.6 | 33.8 | 107.8 | 0 | 0 | 89.4287
4208 | 127.6022 | 0.7 | 43 | 0 | 37.6 | 63.8011 | 631.2 | 162.6 | 218.8 | 0 | 0 | 96.8351
4209 | 184.4919 | 2.1 | 43.2 | 0 | 0 | 92.246 | 29.7 | 152.3 | 299.5 | 0 | 0 | 140.6634
4210 | 217.4078 | 3.5 | 43.4 | 0 | 0 | 108.7039 | 99.6 | 193.8 | 368 | 0 | 0 | 286.5525
4211 | 204.3304 | 3.5 | 43.4 | 0 | 0 | 102.1652 | 163.5 | 213.3 | 404.4 | 0 | 0 | 148.1303
4212 | 189.1342 | 2.8 | 43.3 | 0 | 0 | 94.5671 | 214.5 | 195.7 | 425.3 | 0 | 0 | 170.2163
4213 | 188.8144 | 1.4 | 43.1 | 0 | 75.1 | 94.4072 | 1099 | 153.4 | 436.1 | 0 | 0 | 351.0933
4214 | 198.6024 | 2.1 | 43.2 | 0 | 37.6 | 99.3012 | 949.4 | 164.7 | 447.2 | 0 | 0 | 109.5701
4215 | 196.1252 | 3.5 | 43.4 | 0 | 0 | 98.0626 | 274.6 | 213.3 | 477.5 | 0 | 0 | 97.3124
4216 | 168.0115 | 2.8 | 43.3 | 0 | 0 | 84.0057 | 377.5 | 206.3 | 494 | 0 | 0 | 113.4404
4217 | 119.7441 | 2.1 | 43.2 | 0 | 0 | 59.8721 | 432.5 | 177.7 | 500.7 | 0 | 0 | 138.3765
4218 | 79.643 | 0.7 | 43 | 0 | 37.6 | 39.8215 | 1214 | 144.9 | 511.6 | 0 | 0 | 115.1395
4219 | 63.1476 | 0 | 42.9 | 0 | 75.1 | 31.5738 | 1221.8 | 20.3 | 414.6 | 0 | 0 | 146.6639
4220 | 52.6651 | 0 | 42.9 | 0 | 75.1 | 26.3326 | 1076.9 | 3.9 | 321.9 | 0 | 0 | 175.9257
4221 | 45.6727 | 0 | 42.9 | 0 | 75.1 | 22.8363 | 928.1 | 3.7 | 266.1 | 0 | 0 | 237.5128
4222 | 42.2207 | 0 | 42.9 | 0 | 93.9 | 21.1104 | 882.2 | 2.5 | 231 | 0 | 0 | 227.6293
4223 | 43.2218 | 0 | 0 | 0 | 0 | 21.6109 | 115.5 | 0.8 | 48.7 | 0 | 0 | 233.6619
4224 | 43.9191 | 0 | 0 | 0 | 0 | 21.9596 | 86.3 | 0 | 33.7 | 0 | 0 | 163.079
4225 | 43.1381 | 0 | 0 | 0 | 0 | 21.5691 | 51.4 | 0 | 17.1 | 0 | 0 | 103.5391
4226 | 41.1645 | 0 | 0 | 0 | 0 | 20.5823 | 31.2 | 0 | 4.7 | 0 | 0 | 50.0068
4227 | 43.709 | 0 | 0 | 0 | 0 | 21.8545 | 18.6 | 0 | 0 | 0 | 0 | 47.25
4228 | 42.6029 | 0 | 0 | 0 | 0 | 21.3014 | 8.3 | 0 | 0 | 0 | 0 | 49.2059
4229 | 41.2724 | 0 | 0 | 0 | 0 | 20.6362 | 1 | 0 | 0 | 0 | 0 | 50.6959
4230 | 57.9341 | 0 | 0 | 0 | 0 | 28.9671 | 0 | 0 | 0 | 0 | 0 | 74.9759
4231 | 92.2212 | 0 | 42.9 | 0 | 56.3 | 46.1106 | 612.5 | 0 | 83.4 | 0 | 0 | 55.2881
4232 | 146.3612 | 0.7 | 43 | 0 | 37.6 | 73.1806 | 482.3 | 66.3 | 135.2 | 0 | 0 | 60.0102
4233 | 222.0316 | 2.1 | 43.2 | 0 | 0 | 111.0158 | 6.3 | 70.2 | 155.7 | 0 | 0 | 47.71
4234 | 260.8302 | 3.5 | 43.4 | 0 | 0 | 130.4151 | 13.4 | 88.2 | 176.9 | 0 | 0 | 54.0272
4235 | 274.5263 | 3.5 | 43.4 | 0 | 0 | 137.2631 | 20.8 | 91.3 | 201.1 | 0 | 0 | 104.2586
4236 | 254.2229 | 2.8 | 43.3 | 0 | 0 | 127.1115 | 30.8 | 110.2 | 213.6 | 0 | 0 | 82.2042
4237 | 226.1176 | 1.4 | 43.1 | 0 | 75.1 | 113.0588 | 677.5 | 95.6 | 226.5 | 0 | 0 | 96.5872
4238 | 231.4411 | 2.1 | 43.2 | 0 | 37.6 | 115.7206 | 580.5 | 102 | 237.9 | 0 | 0 | 89.309
4239 | 219.899 | 3.5 | 43.4 | 0 | 0 | 109.9495 | 34.2 | 120 | 247.6 | 0 | 0 | 151.044
4240 | 177.4347 | 2.8 | 43.3 | 0 | 0 | 88.7173 | 55.3 | 117.5 | 247.8 | 0 | 0 | 99.3527
4241 | 138.8939 | 2.1 | 43.2 | 0 | 0 | 69.447 | 63.2 | 108.4 | 241.1 | 0 | 0 | 78.4095
4242 | 109.6552 | 0.7 | 43 | 0 | 37.6 | 54.8276 | 662.5 | 84.7 | 250.9 | 0 | 0 | 138.0401
4243 | 82.2888 | 0 | 42.9 | 0 | 75.1 | 41.1444 | 726.2 | 2.1 | 182.3 | 0 | 0 | 138.9072
4244 | 74.9352 | 0 | 42.9 | 0 | 75.1 | 37.4676 | 616.8 | 0 | 100 | 0 | 0 | 187.5286
4245 | 64.8113 | 0 | 42.9 | 0 | 75.1 | 32.4057 | 426.5 | 0 | 69.2 | 0 | 0 | 232.8561
4246 | 64.2714 | 0 | 42.9 | 0 | 93.9 | 32.1357 | 291.3 | 0 | 37.4 | 0 | 0 | 145.394
4247 | 63.6779 | 0 | 0 | 0 | 0 | 31.839 | 0 | 0 | 0 | 0 | 0 | 121.3514
4248 | 63.4154 | 0 | 0 | 0 | 0 | 31.7077 | 0 | 0 | 0 | 0 | 0 | 83.9707
4249 | 50.6404 | 0 | 0 | 0 | 0 | 25.3202 | 0 | 0 | 0 | 0 | 0 | 51.6149
4250 | 41.0186 | 0 | 0 | 0 | 0 | 20.5093 | 0 | 0 | 0 | 0 | 0 | 47.7095
4251 | 43.7651 | 0 | 0 | 0 | 0 | 21.8825 | 0 | 0 | 0 | 0 | 0 | 71.7421
4252 | 43.2088 | 0 | 0 | 0 | 0 | 21.6044 | 0 | 0 | 0 | 0 | 0 | 49.434
4253 | 42.9593 | 0 | 0 | 0 | 0 | 21.4796 | 0 | 0 | 0 | 0 | 0 | 54.7131
4254 | 59.4078 | 0 | 0 | 0 | 0 | 29.7039 | 0 | 0 | 0 | 0 | 0 | 51.384
4255 | 89.8521 | 0 | 42.9 | 0 | 56.3 | 44.9261 | 53.5 | 0 | 0 | 0 | 0 | 70.5888
4256 | 149.5367 | 0.7 | 43 | 0 | 37.6 | 74.7683 | 82 | 63.9 | 24.6 | 0 | 0 | 115.0158
4257 | 214.392 | 2.1 | 43.2 | 0 | 0 | 107.196 | 0 | 86.9 | 52.8 | 0 | 0 | 69.4394
4258 | 235.0623 | 3.5 | 43.4 | 0 | 0 | 117.5311 | 0 | 118 | 91.3 | 0 | 0 | 91.4597
4259 | 248.8259 | 3.5 | 43.4 | 0 | 0 | 124.413 | 0 | 126.1 | 140.3 | 0 | 0 | 87.0566
4260 | 244.6097 | 2.8 | 43.3 | 0 | 0 | 122.3049 | 0 | 116.5 | 182.4 | 0 | 0 | 64.1498
4261 | 245.3594 | 1.4 | 43.1 | 0 | 75.1 | 122.6797 | 456.7 | 93.5 | 217.6 | 0 | 0 | 101.2633
4262 | 238.6952 | 2.1 | 43.2 | 0 | 37.6 | 119.3476 | 443.5 | 85.1 | 241.8 | 0 | 0 | 80.7793
4263 | 230.7119 | 3.5 | 43.4 | 0 | 0 | 115.3559 | 19.5 | 111.6 | 269.7 | 0 | 0 | 86.5804
4264 | 199.0471 | 2.8 | 43.3 | 0 | 0 | 99.5236 | 55.8 | 130.6 | 295.1 | 0 | 0 | 107.641
4265 | 151.474 | 2.1 | 43.2 | 0 | 0 | 75.737 | 90.2 | 117.4 | 316.3 | 0 | 0 | 167.6373
4266 | 118.8261 | 0.7 | 43 | 0 | 37.6 | 59.4131 | 699 | 94.2 | 328 | 0 | 0 | 163.2005
4267 | 99.1433 | 0 | 42.9 | 0 | 75.1 | 49.5716 | 706.5 | 3 | 253.8 | 0 | 0 | 131.1106
4268 | 83.9252 | 0 | 42.9 | 0 | 75.1 | 41.9626 | 599 | 0 | 176.9 | 0 | 0 | 121.9435
4269 | 65.8604 | 0 | 42.9 | 0 | 75.1 | 32.9302 | 467 | 0 | 123.9 | 0 | 0 | 143.7795
4270 | 65.4404 | 0 | 42.9 | 0 | 93.9 | 32.7202 | 374.2 | 0 | 80.1 | 0 | 0 | 125.1977
4271 | 64.2305 | 0 | 0 | 0 | 0 | 32.1153 | 0 | 0 | 0 | 0 | 0 | 109.5682
4272 | 61.9631 | 0 | 0 | 0 | 0 | 30.9816 | 0 | 0 | 0 | 0 | 0 | 114.8922
4273 | 59.1317 | 0 | 0 | 0 | 0 | 29.5658 | 0 | 0 | 0 | 0 | 0 | 190.0389
4274 | 58.1275 | 0 | 0 | 0 | 0 | 29.0638 | 0 | 0 | 0 | 0 | 0 | 68.8616
4275 | 57.5309 | 0 | 0 | 0 | 0 | 28.7655 | 0 | 0 | 0 | 0 | 0 | 53.6836
4276 | 49.4013 | 0 | 0 | 0 | 0 | 24.7007 | 0 | 0 | 0 | 0 | 0 | 50.466
4277 | 42.2313 | 0 | 0 | 0 | 0 | 21.1156 | 0 | 0 | 0 | 0 | 0 | 46.2215
4278 | 54.8414 | 0 | 0 | 0 | 0 | 27.4207 | 0 | 0 | 0 | 0 | 0 | 47.2495
4279 | 92.9944 | 0 | 42.9 | 0 | 56.3 | 46.4972 | 108.5 | 0 | 4.6 | 0 | 0 | 59.3216
4280 | 144.524 | 0.7 | 43 | 0 | 37.6 | 72.262 | 142.6 | 39.6 | 44.3 | 0 | 0 | 122.7216
4281 | 222.1692 | 2.1 | 43.2 | 0 | 0 | 111.0846 | 0 | 44.2 | 85.3 | 0 | 0 | 84.6849
4282 | 293.9528 | 3.5 | 43.4 | 0 | 0 | 146.9764 | 0 | 58 | 122.8 | 0 | 0 | 68.5168
4283 | 307.025 | 3.5 | 43.4 | 0 | 0 | 153.5125 | 0 | 71.5 | 162.1 | 0 | 0 | 114.5335
4284 | 297.6939 | 2.8 | 43.3 | 0 | 0 | 148.8469 | 0.7 | 89.6 | 201.5 | 0 | 0 | 108.4848
4285 | 295.3868 | 1.4 | 43.1 | 0 | 75.1 | 147.6934 | 507.3 | 90.1 | 231.4 | 0 | 0 | 180.4986
4286 | 265.3947 | 2.1 | 43.2 | 0 | 37.6 | 132.6973 | 489 | 100.3 | 252.5 | 0 | 0 | 143.6564
4287 | 259.1498 | 3.5 | 43.4 | 0 | 0 | 129.5749 | 29.5 | 120 | 277.1 | 0 | 0 | 127.2649
4288 | 248.8389 | 2.8 | 43.3 | 0 | 0 | 124.4195 | 71.5 | 123.9 | 299.8 | 0 | 0 | 93.9632
4289 | 207.6521 | 2.1 | 43.2 | 0 | 0 | 103.8261 | 106.9 | 126.9 | 321.9 | 0 | 0 | 87.8796
4290 | 166.5942 | 0.7 | 43 | 0 | 37.6 | 83.2971 | 735.4 | 109.9 | 337.6 | 0 | 0 | 140.0163
4291 | 117.5524 | 0 | 42.9 | 0 | 75.1 | 58.7762 | 733.1 | 19.2 | 255.6 | 0 | 0 | 193.9493
4292 | 82.6892 | 0 | 42.9 | 0 | 75.1 | 41.3446 | 616.7 | 1.4 | 175 | 0 | 0 | 315.4032
4293 | 51.167 | 0 | 42.9 | 0 | 75.1 | 25.5835 | 480.3 | 0 | 121.3 | 0 | 0 | 266.7758
4294 | 49.6449 | 0 | 42.9 | 0 | 93.9 | 24.8225 | 392.9 | 0 | 81.9 | 0 | 0 | 151.4256
4295 | 44.4506 | 0 | 0 | 0 | 0 | 22.2253 | 0 | 0 | 0 | 0 | 0 | 146.3298
4296 | 40.6783 | 0 | 0 | 0 | 0 | 20.3391 | 0 | 0 | 0 | 0 | 0 | 126.8602
4297 | 43.1276 | 0 | 0 | 0 | 0 | 21.5638 | 0 | 0 | 0 | 0 | 0 | 89.3102
4298 | 41.1063 | 0 | 0 | 0 | 0 | 20.5531 | 0 | 0 | 0 | 0 | 0 | 65.7561
4299 | 42.3332 | 0 | 0 | 0 | 0 | 21.1666 | 0 | 0 | 0 | 0 | 0 | 58.4025
4300 | 42.5508 | 0 | 0 | 0 | 0 | 21.2754 | 0 | 0 | 0 | 0 | 0 | 57.4789
4301 | 46.6694 | 0 | 0 | 0 | 0 | 23.3347 | 0 | 0 | 0 | 0 | 0 | 60.1255
4302 | 69.3458 | 0 | 0 | 0 | 0 | 34.6729 | 0 | 0 | 0 | 0 | 0 | 94.5594
4303 | 118.8633 | 0 | 42.9 | 0 | 56.3 | 59.4317 | 134.3 | 0 | 8.4 | 0 | 0 | 67.1384
4304 | 207.4352 | 0.7 | 43 | 0 | 37.6 | 103.7176 | 167 | 47.1 | 51.8 | 0 | 0 | 79.4769
4305 | 302.5649 | 2.1 | 43.2 | 0 | 0 | 151.2825 | 0 | 52.1 | 93.8 | 0 | 0 | 147.8514
4306 | 377.4335 | 3.5 | 43.4 | 0 | 0 | 188.7168 | 0 | 61.8 | 133.1 | 0 | 0 | 171.9447
4307 | 373.5979 | 3.5 | 43.4 | 0 | 0 | 186.799 | 0 | 70.7 | 172.1 | 0 | 0 | 111.6278
4308 | 333.8457 | 2.8 | 43.3 | 0 | 0 | 166.9229 | 3.2 | 89 | 206.8 | 0 | 0 | 180.3308
4309 | 293.2254 | 1.4 | 43.1 | 0 | 75.1 | 146.6127 | 532.4 | 88.3 | 238.3 | 0 | 0 | 132.3522
4310 | 293.3466 | 2.1 | 43.2 | 0 | 37.6 | 146.6733 | 511.5 | 101.5 | 259.8 | 0 | 0 | 162.9216
4311 | 261.7094 | 3.5 | 43.4 | 0 | 0 | 130.8547 | 39.1 | 133.8 | 286 | 0 | 0 | 127.212
4312 | 212.5452 | 2.8 | 43.3 | 0 | 0 | 106.2726 | 86.2 | 146.1 | 308.9 | 0 | 0 | 72.6635
4313 | 163.6304 | 2.1 | 43.2 | 0 | 0 | 81.8152 | 123.8 | 150.5 | 328.1 | 0 | 0 | 101.143
4314 | 115.0191 | 0.7 | 43 | 0 | 37.6 | 57.5095 | 757.8 | 130.1 | 339.3 | 0 | 0 | 229.8488
4315 | 88.2669 | 0 | 42.9 | 0 | 75.1 | 44.1334 | 761 | 32.4 | 264.4 | 0 | 0 | 262.6036
4316 | 77.2658 | 0 | 42.9 | 0 | 75.1 | 38.6329 | 647.7 | 11.7 | 187.1 | 0 | 0 | 164.4987
4317 | 66.4248 | 0 | 42.9 | 0 | 75.1 | 33.2124 | 510 | 2.3 | 132.2 | 0 | 0 | 129.4869
4318 | 63.7774 | 0 | 42.9 | 0 | 93.9 | 31.8887 | 424.4 | 0 | 90.7 | 0 | 0 | 154.632
4319 | 62.5238 | 0 | 0 | 0 | 0 | 31.2619 | 3.3 | 0 | 0 | 0 | 0 | 133.1736
4320 | 61.7629 | 0 | 0 | 0 | 0 | 30.8815 | 0.1 | 0 | 0 | 0 | 0 | 110.9054
4321 | 46.6641 | 0 | 0 | 0 | 0 | 23.3321 | 0 | 0 | 0 | 0 | 0 | 50.9268
4322 | 41.4019 | 0 | 0 | 0 | 0 | 20.701 | 0 | 0 | 0 | 0 | 0 | 47.249
4323 | 43.2686 | 0 | 0 | 0 | 0 | 21.6343 | 0 | 0 | 0 | 0 | 0 | 47.7105
4324 | 39.7792 | 0 | 0 | 0 | 0 | 19.8896 | 0 | 0 | 0 | 0 | 0 | 46.2222
4325 | 42.8257 | 0 | 0 | 0 | 0 | 21.4129 | 0 | 0 | 0 | 0 | 0 | 53.1076
4326 | 46.2987 | 0 | 0 | 0 | 0 | 23.1494 | 0 | 0 | 0 | 0 | 0 | 45.7672
4327 | 58.4322 | 0 | 42.9 | 0 | 56.3 | 29.2161 | 230.1 | 0 | 25.1 | 0 | 0 | 49.2039
4328 | 66.2621 | 0 | 42.9 | 0 | 37.6 | 33.131 | 251.2 | 0 | 60.8 | 0 | 0 | 55.5166
4329 | 70.685 | 0 | 42.9 | 0 | 0 | 35.3425 | 0 | 0 | 100 | 0 | 0 | 74.3939
4330 | 77.0647 | 0 | 42.9 | 0 | 0 | 38.5324 | 1.3 | 0 | 151.3 | 0 | 0 | 90.625
4331 | 87.555 | 0 | 42.9 | 0 | 0 | 43.7775 | 11.8 | 0 | 197.9 | 0 | 0 | 180.313
4332 | 88.9034 | 0 | 42.9 | 0 | 0 | 44.4517 | 32.1 | 0 | 231.6 | 0 | 0 | 76.4958
4333 | 89.5577 | 0 | 42.9 | 0 | 75.1 | 44.7788 | 665.5 | 0 | 259 | 0 | 0 | 111.7537
4334 | 90.7193 | 0 | 42.9 | 0 | 37.6 | 45.3596 | 632.1 | 0 | 280.2 | 0 | 0 | 155.0952
4335 | 91.6993 | 0 | 42.9 | 0 | 0 | 45.8496 | 99.9 | 0 | 307.2 | 0 | 0 | 155.7287
4336 | 94.5133 | 0 | 42.9 | 0 | 0 | 47.2567 | 171.8 | 0 | 328.8 | 0 | 0 | 144.0603
4337 | 90.4335 | 0 | 42.9 | 0 | 0 | 45.2168 | 218.5 | 0 | 348.2 | 0 | 0 | 126.235
4338 | 87.8234 | 0 | 42.9 | 0 | 37.6 | 43.9117 | 884.2 | 0 | 360 | 0 | 0 | 110.1788
4339 | 79.7511 | 0 | 42.9 | 0 | 75.1 | 39.8756 | 895.5 | 0 | 317.2 | 0 | 0 | 173.2334
4340 | 73.5049 | 0 | 42.9 | 0 | 75.1 | 36.7525 | 779 | 0 | 234 | 0 | 0 | 224.3723
4341 | 68.7833 | 0 | 42.9 | 0 | 75.1 | 34.3916 | 641.4 | 0 | 179.9 | 0 | 0 | 210.8179
4342 | 68.0695 | 0 | 42.9 | 0 | 93.9 | 34.0348 | 546.3 | 0 | 130.4 | 0 | 0 | 179.9973
4343 | 65.1968 | 0 | 0 | 0 | 0 | 32.5984 | 14.6 | 0 | 6.7 | 0 | 0 | 144.5372
4344 | 65.7051 | 0 | 0 | 0 | 0 | 32.8526 | 9.2 | 0 | 1.4 | 0 | 0 | 149.7419
4345 | 64.5156 | 0 | 0 | 0 | 0 | 32.2578 | 1.1 | 0 | 0 | 0 | 0 | 69.4402
4346 | 63.4898 | 0 | 0 | 0 | 0 | 31.7449 | 0 | 0 | 0 | 0 | 0 | 50.1222
4347 | 63.1898 | 0 | 0 | 0 | 0 | 31.5949 | 0 | 0 | 0 | 0 | 0 | 46.7922
4348 | 61.4982 | 0 | 0 | 0 | 0 | 30.7491 | 0 | 0 | 0 | 0 | 0 | 47.9398
4349 | 61.4508 | 0 | 0 | 0 | 0 | 30.7254 | 0 | 0 | 0 | 0 | 0 | 51.8453
4350 | 69.5069 | 0 | 0 | 0 | 0 | 34.7535 | 0 | 0 | 0 | 0 | 0 | 58.6332
4351 | 86.1767 | 0 | 42.9 | 0 | 56.3 | 43.0884 | 223.3 | 0 | 20.1 | 0 | 0 | 53.1068
4352 | 87.0715 | 0 | 42.9 | 0 | 37.6 | 43.5357 | 241.6 | 0 | 31.6 | 0 | 0 | 56.3204
4353 | 85.4026 | 0 | 42.9 | 0 | 0 | 42.7013 | 0 | 0 | 66.4 | 0 | 0 | 97.0737
4354 | 82.0591 | 0 | 42.9 | 0 | 0 | 41.0296 | 0 | 0 | 100.5 | 0 | 0 | 130.0068
4355 | 90.0777 | 0 | 42.9 | 0 | 0 | 45.0389 | 2.9 | 0 | 136 | 0 | 0 | 90.8606
4356 | 91.8685 | 0 | 42.9 | 0 | 0 | 45.9342 | 14.1 | 0 | 166.2 | 0 | 0 | 181.8784
4357 | 89.0153 | 0 | 42.9 | 0 | 75.1 | 44.5077 | 611.4 | 0 | 192.7 | 0 | 0 | 108.3678
4358 | 92.2187 | 0 | 42.9 | 0 | 37.6 | 46.1093 | 580.3 | 0 | 210 | 0 | 0 | 84.2052
4359 | 90.0737 | 0 | 42.9 | 0 | 0 | 45.0369 | 61.6 | 0 | 225.6 | 0 | 0 | 88.0051
4360 | 92.091 | 0 | 42.9 | 0 | 0 | 46.0455 | 116.2 | 0.2 | 246.3 | 0 | 0 | 104.7427
4361 | 89.7269 | 0 | 42.9 | 0 | 0 | 44.8635 | 152.4 | 0.3 | 265.5 | 0 | 0 | 171.8044
4362 | 88.2762 | 0 | 42.9 | 0 | 37.6 | 44.1381 | 800.3 | 0 | 279.7 | 0 | 0 | 148.8005
4363 | 83.9893 | 0 | 42.9 | 0 | 75.1 | 41.9947 | 795.3 | 0 | 275.1 | 0 | 0 | 116.2263
4364 | 79.0594 | 0 | 42.9 | 0 | 75.1 | 39.5297 | 675.1 | 0 | 190.6 | 0 | 0 | 136.0596
4365 | 69.8395 | 0 | 42.9 | 0 | 75.1 | 34.9197 | 535.8 | 0 | 136.7 | 0 | 0 | 195.026
4366 | 67.3046 | 0 | 42.9 | 0 | 93.9 | 33.6523 | 439.7 | 0 | 91.9 | 0 | 0 | 149.5491
4367 | 68.279 | 0 | 0 | 0 | 0 | 34.1395 | 2.4 | 0 | 0 | 0 | 0 | 117.8274
4368 | 64.0061 | 0 | 0 | 0 | 0 | 32.0031 | 0 | 0 | 0 | 0 | 0 | 79.8345
4369 | 63.2078 | 0 | 0 | 0 | 0 | 31.6039 | 0 | 0 | 0 | 0 | 0 | 73.0096
4370 | 62.6989 | 0 | 0 | 0 | 0 | 31.3494 | 0 | 0 | 0 | 0 | 0 | 61.6267
4371 | 61.5735 | 0 | 0 | 0 | 0 | 30.7868 | 0 | 0 | 0 | 0 | 0 | 50.3518
4372 | 60.0382 | 0 | 0 | 0 | 0 | 30.0191 | 0 | 0 | 0 | 0 | 0 | 47.7112
4373 | 62.8114 | 0 | 0 | 0 | 0 | 31.4057 | 0 | 0 | 0 | 0 | 0 | 54.4838
4374 | 82.5172 | 0 | 0 | 0 | 0 | 41.2586 | 0 | 0 | 0 | 0 | 0 | 64.3796
4375 | 117.8964 | 0 | 42.9 | 0 | 56.3 | 58.9482 | 206.9 | 0 | 21.1 | 0 | 0 | 67.3702
4376 | 160.3719 | 0.7 | 43 | 0 | 37.6 | 80.1859 | 234.3 | 98 | 74 | 0 | 0 | 74.8567
4377 | 234.9668 | 2.1 | 43.2 | 0 | 0 | 117.4834 | 0 | 119 | 117 | 0 | 0 | 77.4466
4378 | 263.021 | 3.5 | 43.4 | 0 | 0 | 131.5105 | 0.1 | 157.1 | 166.9 | 0 | 0 | 96.5879
4379 | 283.2602 | 3.5 | 43.4 | 0 | 0 | 141.6301 | 7.7 | 178.4 | 215.8 | 0 | 0 | 130.8779
4380 | 272.2068 | 2.8 | 43.3 | 0 | 0 | 136.1034 | 25.7 | 173.2 | 253.9 | 0 | 0 | 157.9733
4381 | 268.6988 | 1.4 | 43.1 | 0 | 75.1 | 134.3494 | 652.9 | 143.5 | 283.4 | 0 | 0 | 84.2063
4382 | 267.9767 | 2.1 | 43.2 | 0 | 37.6 | 133.9883 | 620.6 | 145.3 | 305.2 | 0 | 0 | 145.4581
4383 | 278.1071 | 3.5 | 43.4 | 0 | 0 | 139.0535 | 91 | 171.4 | 336 | 0 | 0 | 137.5203
4384 | 249.8233 | 2.8 | 43.3 | 0 | 0 | 124.9116 | 157.5 | 165.5 | 363.1 | 0 | 0 | 80.8956
4385 | 179.6571 | 2.1 | 43.2 | 0 | 0 | 89.8286 | 203.2 | 147.6 | 378.7 | 0 | 0 | 176.4275
4386 | 141.294 | 0.7 | 43 | 0 | 37.6 | 70.647 | 879.2 | 113.4 | 386.4 | 0 | 0 | 100.0741
4387 | 109.031 | 0 | 42.9 | 0 | 75.1 | 54.5155 | 882.8 | 8.7 | 300.7 | 0 | 0 | 116.6134
4388 | 92.6513 | 0 | 42.9 | 0 | 75.1 | 46.3257 | 772.1 | 0 | 222.5 | 0 | 0 | 182.3428
4389 | 73.1637 | 0 | 42.9 | 0 | 75.1 | 36.5819 | 644.9 | 0 | 172.9 | 0 | 0 | 292.3905
4390 | 71.9907 | 0 | 42.9 | 0 | 93.9 | 35.9953 | 570.8 | 0 | 131.1 | 0 | 0 | 235.5674
4391 | 68.4256 | 0 | 0 | 0 | 0 | 34.2128 | 14.8 | 0 | 4.7 | 0 | 0 | 171.2087
4392 | 67.9995 | 0 | 0 | 0 | 0 | 33.9997 | 8.9 | 0 | 0.1 | 0 | 0 | 87.1718
4393 | 65.9143 | 0 | 0 | 0 | 0 | 32.9572 | 0.4 | 0 | 0 | 0 | 0 | 68.8628
4394 | 63.8431 | 0 | 0 | 0 | 0 | 31.9216 | 0 | 0 | 0 | 0 | 0 | 55.5181
4395 | 62.9908 | 0 | 0 | 0 | 0 | 31.4954 | 0 | 0 | 0 | 0 | 0 | 47.2502
4396 | 62.5176 | 0 | 0 | 0 | 0 | 31.2588 | 0 | 0 | 0 | 0 | 0 | 49.6627
4397 | 60.83 | 0 | 0 | 0 | 0 | 30.415 | 0 | 0 | 0 | 0 | 0 | 61.5086
4398 | 78.0813 | 0 | 0 | 0 | 0 | 39.0406 | 0 | 0 | 0 | 0 | 0 | 60.8182
4399 | 115.9873 | 0 | 42.9 | 0 | 56.3 | 57.9936 | 333.3 | 0 | 39.8 | 0 | 0 | 55.5192
4400 | 169.694 | 0.7 | 43 | 0 | 37.6 | 84.847 | 329.8 | 94.3 | 107.7 | 0 | 0 | 129.8775
4401 | 258.2463 | 2.1 | 43.2 | 0 | 0 | 129.1232 | 0.1 | 105.4 | 157.9 | 0 | 0 | 123.6675
4402 | 265.7021 | 3.5 | 43.4 | 0 | 0 | 132.8511 | 8.6 | 143.5 | 203 | 0 | 0 | 109.8172
4403 | 262.5589 | 3.5 | 43.4 | 0 | 0 | 131.2795 | 26.8 | 160.6 | 238.7 | 0 | 0 | 141.9333
4404 | 256.1503 | 2.8 | 43.3 | 0 | 0 | 128.0752 | 56 | 168.8 | 273.6 | 0 | 0 | 90.8612
4405 | 244.3494 | 1.4 | 43.1 | 0 | 75.1 | 122.1747 | 721.2 | 150.5 | 301.8 | 0 | 0 | 123.7781
4406 | 233.9202 | 2.1 | 43.2 | 0 | 37.6 | 116.9601 | 684.3 | 165.4 | 323.2 | 0 | 0 | 205.429
4407 | 225.1069 | 3.5 | 43.4 | 0 | 0 | 112.5535 | 128.4 | 212.3 | 351.6 | 0 | 0 | 129.5978
4408 | 201.7955 | 2.8 | 43.3 | 0 | 0 | 100.8977 | 204.1 | 219.6 | 371.1 | 0 | 0 | 231.3462
4409 | 139.5398 | 2.1 | 43.2 | 0 | 0 | 69.7699 | 249.8 | 208.8 | 387.2 | 0 | 0 | 141.3856
4410 | 106.9034 | 0.7 | 43 | 0 | 37.6 | 53.4517 | 931.7 | 173.5 | 396.5 | 0 | 0 | 98.5165
4411 | 81.2322 | 0 | 42.9 | 0 | 75.1 | 40.6161 | 937.8 | 64.9 | 315.5 | 0 | 0 | 203.9836
4412 | 68.9314 | 0 | 42.9 | 0 | 75.1 | 34.4657 | 818 | 40.4 | 236 | 0 | 0 | 176.1883
4413 | 66.5546 | 0 | 42.9 | 0 | 75.1 | 33.2773 | 674.9 | 28.5 | 181.2 | 0 | 0 | 226.1166
4414 | 63.6984 | 0 | 42.9 | 0 | 93.9 | 31.8492 | 576.5 | 21.1 | 133.2 | 0 | 0 | 132.5015
4415 | 62.9626 | 0 | 0 | 0 | 0 | 31.4813 | 18.7 | 12.6 | 7.3 | 0 | 0 | 101.9776
4416 | 63.7108 | 0 | 0 | 0 | 0 | 31.8554 | 10.7 | 4.3 | 0.7 | 0 | 0 | 107.0318
4417 | 60.7857 | 0 | 0 | 0 | 0 | 30.3929 | 0.8 | 0.1 | 0 | 0 | 0 | 62.5454
4418 | 63.2322 | 0 | 0 | 0 | 0 | 31.6161 | 0 | 0 | 0 | 0 | 0 | 58.1704
4419 | 61.3674 | 0 | 0 | 0 | 0 | 30.6837 | 0 | 0 | 0 | 0 | 0 | 58.1701
4420 | 62.1147 | 0 | 0 | 0 | 0 | 31.0573 | 0 | 0 | 0 | 0 | 0 | 53.5686
4421 | 62.7038 | 0 | 0 | 0 | 0 | 31.3519 | 0 | 0 | 0 | 0 | 0 | 62.3154
4422 | 83.7336 | 0 | 0 | 0 | 0 | 41.8668 | 0 | 0 | 0 | 0 | 0 | 96.7104
4423 | 131.4859 | 0 | 42.9 | 0 | 56.3 | 65.7429 | 186.7 | 24.8 | 11.4 | 0 | 0 | 62.5468
4424 | 184.1876 | 0.7 | 43 | 0 | 37.6 | 92.0938 | 197.8 | 153.1 | 42.6 | 0 | 0 | 87.8826
4425 | 266.2197 | 2.1 | 43.2 | 0 | 0 | 133.1099 | 0 | 151.3 | 71.2 | 0 | 0 | 110.6559
4426 | 302.7081 | 3.5 | 43.4 | 0 | 0 | 151.3541 | 0 | 177.7 | 99.1 | 0 | 0 | 167.872
4427 | 326.1941 | 3.5 | 43.4 | 0 | 0 | 163.097 | 0 | 189.3 | 137.8 | 0 | 0 | 165.0659
4428 | 333.7264 | 2.8 | 43.3 | 0 | 0 | 166.8632 | 1.7 | 178.9 | 183.8 | 0 | 0 | 207.5453
4429 | 287.4671 | 1.4 | 43.1 | 0 | 75.1 | 143.7335 | 528.3 | 149.3 | 223.5 | 0 | 0 | 273.9475
4430 | 287.0945 | 2.1 | 43.2 | 0 | 37.6 | 143.5473 | 501.3 | 143.7 | 240.4 | 0 | 0 | 127.0977
4431 | 258.7751 | 3.5 | 43.4 | 0 | 0 | 129.3875 | 20.3 | 155.4 | 258.7 | 0 | 0 | 134.7028
4432 | 237.9548 | 2.8 | 43.3 | 0 | 0 | 118.9774 | 46.9 | 144.2 | 279.1 | 0 | 0 | 228.6977
4433 | 196.3468 | 2.1 | 43.2 | 0 | 0 | 98.1734 | 69.6 | 133.2 | 292.9 | 0 | 0 | 185.1209
4434 | 152.7047 | 0.7 | 43 | 0 | 37.6 | 76.3524 | 695 | 108.3 | 291.2 | 0 | 0 | 118.7955
4435 | 117.1395 | 0 | 42.9 | 0 | 75.1 | 58.5698 | 662.9 | 11.9 | 207.5 | 0 | 0 | 119.4539
4436 | 91.4662 | 0 | 42.9 | 0 | 75.1 | 45.7331 | 544.7 | 0.1 | 126.4 | 0 | 0 | 190.7039
4437 | 67.2392 | 0 | 42.9 | 0 | 75.1 | 33.6196 | 424.1 | 0 | 89.3 | 0 | 0 | 180.3677
4438 | 64.6734 | 0 | 42.9 | 0 | 93.9 | 32.3367 | 365.2 | 0 | 70.5 | 0 | 0 | 178.8556
4439 | 66.1728 | 0 | 0 | 0 | 0 | 33.0864 | 0 | 0 | 0 | 0 | 0 | 159.0992
4440 | 61.5683 | 0 | 0 | 0 | 0 | 30.7841 | 0 | 0 | 0 | 0 | 0 | 206.8145
4441 | 62.4543 | 0 | 0 | 0 | 0 | 31.2272 | 0 | 0 | 0 | 0 | 0 | 117.946
4442 | 63.7225 | 0 | 0 | 0 | 0 | 31.8613 | 0 | 0 | 0 | 0 | 0 | 64.1505
4443 | 63.3699 | 0 | 0 | 0 | 0 | 31.6849 | 0 | 0 | 0 | 0 | 0 | 55.5184
4444 | 61.6901 | 0 | 0 | 0 | 0 | 30.845 | 0 | 0 | 0 | 0 | 0 | 65.9869
4445 | 63.0125 | 0 | 0 | 0 | 0 | 31.5063 | 0 | 0 | 0 | 0 | 0 | 60.2408
4446 | 77.6061 | 0 | 0 | 0 | 0 | 38.8031 | 0 | 0 | 0 | 0 | 0 | 52.5366
4447 | 116.7146 | 0 | 42.9 | 0 | 56.3 | 58.3573 | 197.2 | 0 | 15.7 | 0 | 0 | 89.7838
4448 | 165.8439 | 0.7 | 43 | 0 | 37.6 | 82.9219 | 152.6 | 41.1 | 42.6 | 0 | 0 | 73.1238
4449 | 261.5145 | 2.1 | 43.2 | 0 | 0 | 130.7572 | 0 | 32.8 | 43 | 0 | 0 | 85.275
4450 | 309.8075 | 3.5 | 43.4 | 0 | 0 | 154.9038 | 0 | 33.5 | 42.1 | 0 | 0 | 134.7183
4451 | 297.5566 | 3.5 | 43.4 | 0 | 0 | 148.7783 | 0 | 57 | 42.6 | 0 | 0 | 192.8137
4452 | 247.1951 | 2.8 | 43.3 | 0 | 0 | 123.5976 | 0 | 77.2 | 49.2 | 0 | 0 | 138.9523
4453 | 235.5653 | 1.4 | 43.1 | 0 | 75.1 | 117.7826 | 196.7 | 75.6 | 62.8 | 0 | 0 | 136.5384
4454 | 232.6957 | 2.1 | 43.2 | 0 | 37.6 | 116.3479 | 171.5 | 79.9 | 74.5 | 0 | 0 | 177.8072
4455 | 202.7485 | 3.5 | 43.4 | 0 | 0 | 101.3743 | 0 | 89.5 | 76.7 | 0 | 0 | 127.2084
4456 | 168.8817 | 2.8 | 43.3 | 0 | 0 | 84.4409 | 0 | 86.6 | 96.5 | 0 | 0 | 133.7536
4457 | 127.4284 | 2.1 | 43.2 | 0 | 0 | 63.7142 | 0 | 93.3 | 116.7 | 0 | 0 | 137.6687
4458 | 86.9193 | 0.7 | 43 | 0 | 37.6 | 43.4597 | 212.5 | 78.6 | 113 | 0 | 0 | 92.0547
4459 | 60.2626 | 0 | 42.9 | 0 | 75.1 | 30.1313 | 221.3 | 1.5 | 44 | 0 | 0 | 216.4721
4460 | 51.4183 | 0 | 42.9 | 0 | 75.1 | 25.7092 | 139.6 | 0 | 6.3 | 0 | 0 | 278.8514
4461 | 43.5323 | 0 | 42.9 | 0 | 75.1 | 21.7662 | 65.5 | 0 | 1.8 | 0 | 0 | 208.9685
4462 | 42.937 | 0 | 42.9 | 0 | 93.9 | 21.4685 | 36 | 0 | 0 | 0 | 0 | 147.4548
4463 | 41.4648 | 0 | 0 | 0 | 0 | 20.7324 | 0 | 0 | 0 | 0 | 0 | 151.5375
4464 | 41.1466 | 0 | 0 | 0 | 0 | 20.5733 | 0 | 0 | 0 | 0 | 0 | 82.9092
4465 | 42.9416 | 0 | 0 | 0 | 0 | 21.4708 | 0 | 0 | 0 | 0 | 0 | 66.7931
4466 | 41.3623 | 0 | 0 | 0 | 0 | 20.6811 | 0 | 0 | 0 | 0 | 0 | 52.6504
4467 | 43.687 | 0 | 0 | 0 | 0 | 21.8435 | 0 | 0 | 0 | 0 | 0 | 50.6966
4468 | 44.3577 | 0 | 0 | 0 | 0 | 22.1788 | 0 | 0 | 0 | 0 | 0 | 52.076
4469 | 41.5092 | 0 | 0 | 0 | 0 | 20.7546 | 0 | 0 | 0 | 0 | 0 | 58.5183
4470 | 59.2206 | 0 | 0 | 0 | 0 | 29.6103 | 0 | 0 | 0 | 0 | 0 | 78.4023
4471 | 94.8527 | 0 | 42.9 | 0 | 56.3 | 47.4264 | 0 | 0 | 0 | 0 | 0 | 72.2038
4472 | 159.9439 | 0.7 | 43 | 0 | 37.6 | 79.9719 | 0 | 26.2 | 0 | 0 | 0 | 108.7261
4473 | 223.2307 | 2.1 | 43.2 | 0 | 0 | 111.6153 | 0 | 21.4 | 0 | 0 | 0 | 73.0091
4474 | 252.4437 | 3.5 | 43.4 | 0 | 0 | 126.2218 | 0 | 34.2 | 0 | 0 | 0 | 70.7058
4475 | 222.5138 | 3.5 | 43.4 | 0 | 0 | 111.2569 | 0 | 48.5 | 0 | 0 | 0 | 129.2618
4476 | 215.407 | 2.8 | 43.3 | 0 | 0 | 107.7035 | 0 | 66.6 | 0.2 | 0 | 0 | 169.5841
4477 | 207.3651 | 1.4 | 43.1 | 0 | 75.1 | 103.6826 | 0 | 68 | 4 | 0 | 0 | 159.9958
4478 | 207.204 | 2.1 | 43.2 | 0 | 37.6 | 103.602 | 0 | 71.9 | 8.7 | 0 | 0 | 156.2098
4479 | 208.3882 | 3.5 | 43.4 | 0 | 0 | 104.1941 | 0 | 64 | 21.1 | 0 | 0 | 92.8883
4480 | 181.0952 | 2.8 | 43.3 | 0 | 0 | 90.5476 | 0 | 54.4 | 43.3 | 0 | 0 | 79.832
4481 | 130.43 | 2.1 | 43.2 | 0 | 0 | 65.215 | 0 | 54.4 | 60.2 | 0 | 0 | 121.0528
4482 | 92.3089 | 0.7 | 43 | 0 | 37.6 | 46.1544 | 33.5 | 47.8 | 75.8 | 0 | 0 | 98.5135
4483 | 71.946 | 0 | 42.9 | 0 | 75.1 | 35.973 | 59.1 | 0 | 43.6 | 0 | 0 | 126.1566
4484 | 58.6817 | 0 | 42.9 | 0 | 75.1 | 29.3408 | 37 | 0 | 14.5 | 0 | 0 | 230.5775
4485 | 41.8268 | 0 | 42.9 | 0 | 75.1 | 20.9134 | 10.3 | 0 | 2.8 | 0 | 0 | 154.4995
4486 | 43.1121 | 0 | 42.9 | 0 | 93.9 | 21.556 | 2.3 | 0 | 0 | 0 | 0 | 126.8721
4487 | 43.0216 | 0 | 0 | 0 | 0 | 21.5108 | 0 | 0 | 0 | 0 | 0 | 113.6802
4488 | 41.2318 | 0 | 0 | 0 | 0 | 20.6159 | 0 | 0 | 0 | 0 | 0 | 88.3584
4489 | 41.4983 | 0 | 0 | 0 | 0 | 20.7492 | 0 | 0 | 0 | 0 | 0 | 60.5895
4490 | 44.3477 | 0 | 0 | 0 | 0 | 22.1739 | 0 | 0 | 0 | 0 | 0 | 53.1079
4491 | 43.466 | 0 | 0 | 0 | 0 | 21.733 | 0 | 0 | 0 | 0 | 0 | 51.4996
4492 | 41.4369 | 0 | 0 | 0 | 0 | 20.7185 | 0 | 0 | 0 | 0 | 0 | 55.1729
4493 | 40.2205 | 0 | 0 | 0 | 0 | 20.1103 | 0 | 0 | 0 | 0 | 0 | 51.0426
4494 | 41.7543 | 0 | 0 | 0 | 0 | 20.8772 | 0 | 0 | 0 | 0 | 0 | 68.5164
4495 | 56.8798 | 0 | 42.9 | 0 | 56.3 | 28.4399 | 0 | 0 | 0 | 0 | 0 | 49.3192
4496 | 64.0607 | 0 | 42.9 | 0 | 37.6 | 32.0303 | 0 | 0 | 0 | 0 | 0 | 93.2422
4497 | 59.4441 | 0 | 42.9 | 0 | 0 | 29.722 | 0 | 0 | 0.3 | 0 | 0 | 58.6341
4498 | 57.5179 | 0 | 42.9 | 0 | 0 | 28.7589 | 0 | 0 | 10.2 | 0 | 0 | 86.2249
4499 | 62.9099 | 0 | 42.9 | 0 | 0 | 31.455 | 0 | 0 | 36.7 | 0 | 0 | 77.5648
4500 | 68.1644 | 0 | 42.9 | 0 | 0 | 34.0822 | 0 | 0 | 72.7 | 0 | 0 | 105.2222
4501 | 73.2573 | 0 | 42.9 | 0 | 75.1 | 36.6287 | 90.6 | 0.2 | 107.9 | 0 | 0 | 106.7946
4502 | 78.5068 | 0 | 42.9 | 0 | 37.6 | 39.2534 | 114.9 | 5.2 | 135.7 | 0 | 0 | 52.5349
4503 | 84.4536 | 0 | 42.9 | 0 | 0 | 42.2268 | 0 | 11.7 | 162.6 | 0 | 0 | 93.1265
4504 | 90.4001 | 0 | 42.9 | 0 | 0 | 45.2 | 0 | 16.8 | 189.8 | 0 | 0 | 153.754
4505 | 89.3826 | 0 | 42.9 | 0 | 0 | 44.6913 | 0 | 20.7 | 213.2 | 0 | 0 | 155.8224
4506 | 84.8766 | 0 | 42.9 | 0 | 37.6 | 42.4383 | 337.4 | 22.8 | 226.9 | 0 | 0 | 290.2904
4507 | 76.5003 | 0 | 42.9 | 0 | 75.1 | 38.2502 | 369.1 | 18.7 | 198.1 | 0 | 0 | 217.5954
4508 | 65.3329 | 0 | 42.9 | 0 | 75.1 | 32.6665 | 311.9 | 0 | 133.6 | 0 | 0 | 166.2978
4509 | 50.504 | 0 | 42.9 | 0 | 75.1 | 25.252 | 205 | 0 | 84.8 | 0 | 0 | 185.53
4510 | 44.6574 | 0 | 42.9 | 0 | 93.9 | 22.3287 | 162.9 | 0 | 57.6 | 0 | 0 | 177.8991
4511 | 44.3924 | 0 | 0 | 0 | 0 | 22.1962 | 0 | 0 | 0 | 0 | 0 | 112.4857
4512 | 43.683 | 0 | 0 | 0 | 0 | 21.8415 | 0 | 0 | 0 | 0 | 0 | 96.2271
4513 | 42.5868 | 0 | 0 | 0 | 0 | 21.2934 | 0 | 0 | 0 | 0 | 0 | 81.2565
4514 | 41.0846 | 0 | 0 | 0 | 0 | 20.5423 | 0 | 0 | 0 | 0 | 0 | 62.0841
4515 | 42.8056 | 0 | 0 | 0 | 0 | 21.4028 | 0 | 0 | 0 | 0 | 0 | 60.2421
4516 | 40.9934 | 0 | 0 | 0 | 0 | 20.4967 | 0 | 0 | 0 | 0 | 0 | 58.4019
4517 | 42.0741 | 0 | 0 | 0 | 0 | 21.0371 | 0 | 0 | 0 | 0 | 0 | 57.8219
4518 | 52.8923 | 0 | 0 | 0 | 0 | 26.4462 | 0 | 0 | 0 | 0 | 0 | 50.5809
4519 | 68.2871 | 0 | 42.9 | 0 | 56.3 | 34.1435 | 67.3 | 0 | 3.3 | 0 | 0 | 73.3544
4520 | 61.6011 | 0 | 42.9 | 0 | 37.6 | 30.8006 | 66.5 | 0.4 | 10 | 0 | 0 | 77.9273
4521 | 64.2231 | 0 | 42.9 | 0 | 0 | 32.1115 | 0 | 11 | 27.2 | 0 | 0 | 61.3931
4522 | 66.4217 | 0 | 42.9 | 0 | 0 | 33.2108 | 0 | 24.7 | 53 | 0 | 0 | 63.4639
4523 | 73.7141 | 0 | 42.9 | 0 | 0 | 36.8571 | 0 | 31 | 76.8 | 0 | 0 | 172.0429
4524 | 77.7121 | 0 | 42.9 | 0 | 0 | 38.8561 | 0 | 35.8 | 108.7 | 0 | 0 | 135.4693
4525 | 80.2876 | 0 | 42.9 | 0 | 75.1 | 40.1438 | 353.4 | 45.8 | 136.5 | 0 | 0 | 222.9088
4526 | 86.0931 | 0 | 42.9 | 0 | 37.6 | 43.0465 | 317.4 | 55 | 154.1 | 0 | 0 | 233.3847
4527 | 88.0877 | 0 | 42.9 | 0 | 0 | 44.0439 | 0 | 64.1 | 174.1 | 0 | 0 | 113.921
4528 | 88.0958 | 0 | 42.9 | 0 | 0 | 44.0479 | 0 | 71.9 | 191.8 | 0 | 0 | 117.0944
4529 | 85.7029 | 0 | 42.9 | 0 | 0 | 42.8514 | 1.9 | 81.4 | 198.2 | 0 | 0 | 197.0022
4530 | 85.7574 | 0 | 42.9 | 0 | 37.6 | 42.8787 | 493.2 | 87.9 | 198 | 0 | 0 | 153.9378
4531 | 78.4358 | 0 | 42.9 | 0 | 75.1 | 39.2179 | 490.4 | 86.3 | 171.9 | 0 | 0 | 155.6643
4532 | 71.9497 | 0 | 42.9 | 0 | 75.1 | 35.9749 | 395.5 | 50.8 | 89.8 | 0 | 0 | 192.5201
4533 | 69.3312 | 0 | 42.9 | 0 | 75.1 | 34.6656 | 306 | 34.5 | 74.2 | 0 | 0 | 333.382
4534 | 66.5751 | 0 | 42.9 | 0 | 93.9 | 33.2875 | 277.1 | 25.5 | 59.7 | 0 | 0 | 150.9418
4535 | 51.5128 | 0 | 0 | 0 | 0 | 25.7564 | 0 | 18.3 | 0 | 0 | 0 | 116.9781
4536 | 44.9295 | 0 | 0 | 0 | 0 | 22.4647 | 0 | 10.4 | 0 | 0 | 0 | 91.5759
4537 | 41.2064 | 0 | 0 | 0 | 0 | 20.6032 | 0 | 4.3 | 0 | 0 | 0 | 59.7819
4538 | 43.1772 | 0 | 0 | 0 | 0 | 21.5886 | 0 | 0.6 | 0 | 0 | 0 | 48.3987
4539 | 42.3193 | 0 | 0 | 0 | 0 | 21.1596 | 0 | 0 | 0 | 0 | 0 | 48.3997
4540 | 42.8775 | 0 | 0 | 0 | 0 | 21.4387 | 0 | 0 | 0 | 0 | 0 | 52.5347
4541 | 40.9519 | 0 | 0 | 0 | 0 | 20.476 | 0 | 0 | 0 | 0 | 0 | 65.2968
4542 | 62.9059 | 0 | 0 | 0 | 0 | 31.4529 | 0 | 1.9 | 0 | 0 | 0 | 48.8606
4543 | 98.4574 | 0 | 42.9 | 0 | 56.3 | 49.2287 | 231.4 | 42.8 | 32.7 | 0 | 0 | 58.8639
4544 | 179.116 | 0.7 | 43 | 0 | 37.6 | 89.558 | 286.5 | 183.1 | 150.6 | 0 | 0 | 53.1082
4545 | 293.1188 | 2.1 | 43.2 | 0 | 0 | 146.5594 | 0 | 194.5 | 245.6 | 0 | 0 | 72.5498
4546 | 329.535 | 3.5 | 43.4 | 0 | 0 | 164.7675 | 0.2 | 238.7 | 300.3 | 0 | 0 | 76.2643
4547 | 303.7268 | 3.5 | 43.4 | 0 | 0 | 151.8634 | 22.5 | 259.7 | 346.7 | 0 | 0 | 89.9042
4548 | 280.6581 | 2.8 | 43.3 | 0 | 0 | 140.329 | 71.5 | 248.8 | 379.7 | 0 | 0 | 272.3686
4549 | 272.4132 | 1.4 | 43.1 | 0 | 75.1 | 136.2066 | 821.9 | 212.2 | 377.5 | 0 | 0 | 120.8838
4550 | 273.1548 | 2.1 | 43.2 | 0 | 37.6 | 136.5774 | 659.7 | 234.6 | 359.4 | 0 | 0 | 172.5959
4551 | 272.6862 | 3.5 | 43.4 | 0 | 0 | 136.3431 | 37.9 | 301.6 | 338.8 | 0 | 0 | 86.1051
4552 | 222.9595 | 2.8 | 43.3 | 0 | 0 | 111.4797 | 64.9 | 308.9 | 328.5 | 0 | 0 | 178.2453
4553 | 162.6092 | 2.1 | 43.2 | 0 | 0 | 81.3046 | 70.9 | 275.7 | 319.8 | 0 | 0 | 153.3292
4554 | 123.2742 | 0.7 | 43 | 0 | 37.6 | 61.6371 | 747.6 | 217.5 | 310.8 | 0 | 0 | 200.5688
4555 | 101.4367 | 0 | 42.9 | 0 | 75.1 | 50.7184 | 729.4 | 93.1 | 214.6 | 0 | 0 | 205.1328
4556 | 89.5592 | 0 | 42.9 | 0 | 75.1 | 44.7796 | 636.4 | 69.5 | 139.1 | 0 | 0 | 140.1365
4557 | 70.1999 | 0 | 42.9 | 0 | 75.1 | 35.1 | 550.2 | 56.6 | 122 | 0 | 0 | 175.2218
4558 | 67.0164 | 0 | 42.9 | 0 | 93.9 | 33.5082 | 500.3 | 48.5 | 90.3 | 0 | 0 | 226.7121
4559 | 63.9612 | 0 | 0 | 0 | 0 | 31.9806 | 0 | 41.5 | 0 | 0 | 0 | 198.4038
4560 | 63.7461 | 0 | 0 | 0 | 0 | 31.873 | 0 | 32.5 | 0 | 0 | 0 | 165.2212
4561 | 61.673 | 0 | 0 | 0 | 0 | 30.8365 | 0 | 23.9 | 0 | 0 | 0 | 51.8442
4562 | 61.5918 | 0 | 0 | 0 | 0 | 30.7959 | 0 | 15.4 | 0 | 0 | 0 | 46.9065
4563 | 59.4097 | 0 | 0 | 0 | 0 | 29.7048 | 0 | 9.1 | 0 | 0 | 0 | 45.541
4564 | 59.4205 | 0 | 0 | 0 | 0 | 29.7103 | 0 | 4.8 | 0 | 0 | 0 | 52.8791
4565 | 61.5035 | 0 | 0 | 0 | 0 | 30.7518 | 0 | 2.2 | 0 | 0 | 0 | 55.9786
4566 | 81.2666 | 0 | 0 | 0 | 0 | 40.6333 | 0 | 1.3 | 0 | 0 | 0 | 118.7852
4567 | 121.1428 | 0 | 42.9 | 0 | 56.3 | 60.5714 | 239 | 16.7 | 21.6 | 0 | 0 | 62.5471
4568 | 198.2872 | 0.7 | 43 | 0 | 37.6 | 99.1436 | 287.4 | 131.7 | 96 | 0 | 0 | 70.1283
4569 | 275.9801 | 2.1 | 43.2 | 0 | 0 | 137.99 | 0 | 119 | 160.5 | 0 | 0 | 101.7424
4570 | 304.1713 | 3.5 | 43.4 | 0 | 0 | 152.0856 | 0 | 146.2 | 242.7 | 0 | 0 | 75.2076
4571 | 287.5892 | 3.5 | 43.4 | 0 | 0 | 143.7946 | 0.9 | 136.9 | 314.9 | 0 | 0 | 67.0233
4572 | 249.7284 | 2.8 | 43.3 | 0 | 0 | 124.8642 | 23.5 | 143.8 | 357.1 | 0 | 0 | 106.4293
4573 | 236.2437 | 1.4 | 43.1 | 0 | 75.1 | 118.1218 | 890.7 | 135.5 | 377.7 | 0 | 0 | 90.0235
4574 | 243.4345 | 2.1 | 43.2 | 0 | 37.6 | 121.7173 | 752 | 139.8 | 393.7 | 0 | 0 | 97.9171
4575 | 241.4532 | 3.5 | 43.4 | 0 | 0 | 120.7266 | 109 | 188 | 426.7 | 0 | 0 | 74.3952
4576 | 205.4399 | 2.8 | 43.3 | 0 | 0 | 102.7199 | 203.9 | 187.5 | 446.6 | 0 | 0 | 104.1353
4577 | 138.6135 | 2.1 | 43.2 | 0 | 0 | 69.3067 | 264.8 | 178.7 | 465.7 | 0 | 0 | 75.3246
4578 | 108.3536 | 0.7 | 43 | 0 | 37.6 | 54.1768 | 1081.7 | 164.5 | 468.3 | 0 | 0 | 173.2897
4579 | 76.8431 | 0 | 42.9 | 0 | 75.1 | 38.4216 | 1020.3 | 44.1 | 352.9 | 0 | 0 | 312.4333
4580 | 68.9224 | 0 | 42.9 | 0 | 75.1 | 34.4612 | 870.9 | 20.8 | 258.9 | 0 | 0 | 218.7927
4581 | 62.6592 | 0 | 42.9 | 0 | 75.1 | 31.3296 | 720.6 | 11.2 | 200.2 | 0 | 0 | 198.8961
4582 | 61.7251 | 0 | 42.9 | 0 | 93.9 | 30.8625 | 647.7 | 6.8 | 154 | 0 | 0 | 258.057
4583 | 60.9993 | 0 | 0 | 0 | 0 | 30.4996 | 14.2 | 3 | 3.6 | 0 | 0 | 106.3072
4584 | 60.4764 | 0 | 0 | 0 | 0 | 30.2382 | 4.8 | 0.7 | 0 | 0 | 0 | 87.0554
4585 | 59.8922 | 0 | 0 | 0 | 0 | 29.9461 | 0 | 0 | 0 | 0 | 0 | 161.1702
4586 | 60.3122 | 0 | 0 | 0 | 0 | 30.1561 | 0 | 0 | 0 | 0 | 0 | 53.6827
4587 | 58.2769 | 0 | 0 | 0 | 0 | 29.1384 | 0 | 0 | 0 | 0 | 0 | 49.2032
4588 | 57.6478 | 0 | 0 | 0 | 0 | 28.8239 | 0 | 0 | 0 | 0 | 0 | 48.8598
4589 | 52.6658 | 0 | 0 | 0 | 0 | 26.3329 | 0 | 0 | 0 | 0 | 0 | 50.6956
4590 | 64.9824 | 0 | 0 | 0 | 0 | 32.4912 | 0 | 0 | 0 | 0 | 0 | 57.1313
4591 | 91.4615 | 0 | 42.9 | 0 | 56.3 | 45.7308 | 325.5 | 0 | 30.5 | 0 | 0 | 46.3357
4592 | 139.8333 | 0.7 | 43 | 0 | 37.6 | 69.9167 | 325.8 | 89.9 | 101.5 | 0 | 0 | 53.7977
4593 | 254.1144 | 2.1 | 43.2 | 0 | 0 | 127.0572 | 0 | 78.3 | 144.7 | 0 | 0 | 58.5174
4594 | 293.8667 | 3.5 | 43.4 | 0 | 0 | 146.9333 | 0.7 | 106.1 | 186.4 | 0 | 0 | 62.2003
4595 | 288.8261 | 3.5 | 43.4 | 0 | 0 | 144.413 | 10.6 | 120.1 | 216.7 | 0 | 0 | 118.9741
4596 | 291.8618 | 2.8 | 43.3 | 0 | 0 | 145.9309 | 32.1 | 113.1 | 251.9 | 0 | 0 | 131.0775
4597 | 293.3627 | 1.4 | 43.1 | 0 | 75.1 | 146.6814 | 690 | 93.3 | 282.7 | 0 | 0 | 240.0468
4598 | 286.4499 | 2.1 | 43.2 | 0 | 37.6 | 143.225 | 657.2 | 93.8 | 313 | 0 | 0 | 145.718
4599 | 274.1246 | 3.5 | 43.4 | 0 | 0 | 137.0623 | 101.1 | 114.1 | 352.4 | 0 | 0 | 91.7013
4600 | 232.3504 | 2.8 | 43.3 | 0 | 0 | 116.1752 | 175.1 | 100.7 | 377.9 | 0 | 0 | 139.3638
4601 | 144.9396 | 2.1 | 43.2 | 0 | 0 | 72.4698 | 224.2 | 104.3 | 395.1 | 0 | 0 | 220.8052
4602 | 121.1143 | 0.7 | 43 | 0 | 37.6 | 60.5572 | 962.7 | 82.2 | 404.9 | 0 | 0 | 210.6575
4603 | 87.5444 | 0 | 42.9 | 0 | 75.1 | 43.7722 | 964.6 | 0 | 323 | 0 | 0 | 252.6713
4604 | 63.3345 | 0 | 42.9 | 0 | 75.1 | 31.6673 | 842.3 | 0 | 237.8 | 0 | 0 | 209.8247
4605 | 47.0103 | 0 | 42.9 | 0 | 75.1 | 23.5051 | 698.4 | 0 | 184.4 | 0 | 0 | 229.3231
4606 | 44.4317 | 0 | 42.9 | 0 | 93.9 | 22.2159 | 657.8 | 0 | 146.7 | 0 | 0 | 202.3506
4607 | 41.5556 | 0 | 0 | 0 | 0 | 20.7778 | 18.8 | 0 | 4.8 | 0 | 0 | 167.0958
4608 | 39.6524 | 0 | 0 | 0 | 0 | 19.8262 | 13.1 | 0 | 0.4 | 0 | 0 | 86.1016
4609 | 42.9723 | 0 | 0 | 0 | 0 | 21.4862 | 4.6 | 0 | 0 | 0 | 0 | 99.1066
4610 | 42.2118 | 0 | 0 | 0 | 0 | 21.1059 | 0 | 0 | 0 | 0 | 0 | 57.1304
4611 | 41.6743 | 0 | 0 | 0 | 0 | 20.8372 | 0 | 0 | 0 | 0 | 0 | 56.4368
4612 | 43.1657 | 0 | 0 | 0 | 0 | 21.5828 | 0 | 0 | 0 | 0 | 0 | 47.5947
4613 | 43.4595 | 0 | 0 | 0 | 0 | 21.7298 | 0 | 0 | 0 | 0 | 0 | 52.4211
4614 | 59.9526 | 0 | 0 | 0 | 0 | 29.9763 | 0 | 0 | 0 | 0 | 0 | 51.6144
4615 | 100.1285 | 0 | 42.9 | 0 | 56.3 | 50.0643 | 439 | 0 | 43.4 | 0 | 0 | 50.0071
4616 | 167.1945 | 0.7 | 43 | 0 | 37.6 | 83.5973 | 415.7 | 26.7 | 119.5 | 0 | 0 | 52.3055
4617 | 242.0662 | 2.1 | 43.2 | 0 | 0 | 121.0331 | 0 | 18.8 | 148.3 | 0 | 0 | 117.6652
4618 | 257.0717 | 3.5 | 43.4 | 0 | 0 | 128.5359 | 0 | 25.4 | 143.4 | 0 | 0 | 80.6635
4619 | 277.6624 | 3.5 | 43.4 | 0 | 0 | 138.8312 | 0 | 28.3 | 146.9 | 0 | 0 | 92.4077
4620 | 273.6132 | 2.8 | 43.3 | 0 | 0 | 136.8066 | 0 | 39.1 | 153.7 | 0 | 0 | 87.1759
4621 | 257.5118 | 1.4 | 43.1 | 0 | 75.1 | 128.7559 | 594.1 | 30.8 | 200.1 | 0 | 0 | 147.5809
4622 | 250.7902 | 2.1 | 43.2 | 0 | 37.6 | 125.3951 | 563.5 | 35.1 | 267.5 | 0 | 0 | 203.3404
4623 | 236.7606 | 3.5 | 43.4 | 0 | 0 | 118.3803 | 15 | 52.8 | 307.8 | 0 | 0 | 200.1748
4624 | 193.7378 | 2.8 | 43.3 | 0 | 0 | 96.8689 | 21.8 | 48.5 | 291.7 | 0 | 0 | 163.5646
4625 | 138.5865 | 2.1 | 43.2 | 0 | 0 | 69.2932 | 18.3 | 50.3 | 245.5 | 0 | 0 | 117.7179
4626 | 118.9365 | 0.7 | 43 | 0 | 37.6 | 59.4682 | 662.4 | 31.8 | 232.1 | 0 | 0 | 121.6746
4627 | 91.2827 | 0 | 42.9 | 0 | 75.1 | 45.6414 | 653.5 | 0 | 156.5 | 0 | 0 | 235.1601
4628 | 71.2788 | 0 | 42.9 | 0 | 75.1 | 35.6394 | 528.7 | 0 | 91.9 | 0 | 0 | 87.888
4629 | 64.3393 | 0 | 42.9 | 0 | 75.1 | 32.1696 | 407.5 | 0 | 69.9 | 0 | 0 | 162.912
4630 | 60.6283 | 0 | 42.9 | 0 | 93.9 | 30.3141 | 329.9 | 0 | 46.2 | 0 | 0 | 127.3443
4631 | 61.8484 | 0 | 0 | 0 | 0 | 30.9242 | 0 | 0 | 0 | 0 | 0 | 122.9155
4632 | 60.5248 | 0 | 0 | 0 | 0 | 30.2624 | 0 | 0 | 0 | 0 | 0 | 78.4061
4633 | 57.71 | 0 | 0 | 0 | 0 | 28.855 | 0 | 0 | 0 | 0 | 0 | 50.8106
4634 | 57.3992 | 0 | 0 | 0 | 0 | 28.6996 | 0 | 0 | 0 | 0 | 0 | 48.285
4635 | 57.2064 | 0 | 0 | 0 | 0 | 28.6032 | 0 | 0 | 0 | 0 | 0 | 51.3848
4636 | 46.1298 | 0 | 0 | 0 | 0 | 23.0649 | 0 | 0 | 0 | 0 | 0 | 50.6961
4637 | 43.8841 | 0 | 0 | 0 | 0 | 21.942 | 0 | 0 | 0 | 0 | 0 | 55.5178
4638 | 65.6772 | 0 | 0 | 0 | 0 | 32.8386 | 0 | 0 | 0 | 0 | 0 | 65.1833
4639 | 114.1978 | 0 | 42.9 | 0 | 56.3 | 57.0989 | 135.9 | 0 | 8.2 | 0 | 0 | 86.6979
4640 | 169.8025 | 0.7 | 43 | 0 | 37.6 | 84.9013 | 185.4 | 13.3 | 74 | 0 | 0 | 58.7477
4641 | 260.9684 | 2.1 | 43.2 | 0 | 0 | 130.4842 | 0 | 22.9 | 139.7 | 0 | 0 | 75.7945
4642 | 307.8944 | 3.5 | 43.4 | 0 | 0 | 153.9472 | 0 | 48.1 | 210.7 | 0 | 0 | 74.0472
4643 | 300.9769 | 3.5 | 43.4 | 0 | 0 | 150.4884 | 0.3 | 71.7 | 266.6 | 0 | 0 | 96.3438
4644 | 292.7249 | 2.8 | 43.3 | 0 | 0 | 146.3625 | 5.3 | 101.2 | 281.2 | 0 | 0 | 148.3995
4645 | 281.4667 | 1.4 | 43.1 | 0 | 75.1 | 140.7333 | 657.9 | 94.7 | 294.6 | 0 | 0 | 110.9063
4646 | 261.1918 | 2.1 | 43.2 | 0 | 37.6 | 130.5959 | 565.3 | 111.2 | 304.2 | 0 | 0 | 97.6724
4647 | 260.2537 | 3.5 | 43.4 | 0 | 0 | 130.1269 | 22.5 | 144.8 | 321.5 | 0 | 0 | 201.7872
4648 | 230.2851 | 2.8 | 43.3 | 0 | 0 | 115.1426 | 50 | 142.3 | 330 | 0 | 0 | 98.6357
4649 | 176.737 | 2.1 | 43.2 | 0 | 0 | 88.3685 | 59.8 | 139.5 | 321 | 0 | 0 | 119.7346
4650 | 148.2626 | 0.7 | 43 | 0 | 37.6 | 74.1313 | 721.8 | 114.7 | 297.2 | 0 | 0 | 160.3232
4651 | 114.1194 | 0 | 42.9 | 0 | 75.1 | 57.0597 | 647.1 | 21.9 | 178.7 | 0 | 0 | 278.0283
4652 | 89.2016 | 0 | 42.9 | 0 | 75.1 | 44.6008 | 504.4 | 3.8 | 90.6 | 0 | 0 | 195.4247
4653 | 68.7253 | 0 | 42.9 | 0 | 75.1 | 34.3627 | 397 | 0.2 | 73.2 | 0 | 0 | 154.8434
4654 | 65.91 | 0 | 42.9 | 0 | 93.9 | 32.955 | 317.5 | 0 | 48.8 | 0 | 0 | 255.3534
4655 | 66.1973 | 0 | 0 | 0 | 0 | 33.0986 | 0 | 0 | 0 | 0 | 0 | 134.3712
4656 | 66.2732 | 0 | 0 | 0 | 0 | 33.1366 | 0 | 0 | 0 | 0 | 0 | 103.6565
4657 | 63.3776 | 0 | 0 | 0 | 0 | 31.6888 | 0 | 0 | 0 | 0 | 0 | 77.4447
4658 | 62.0056 | 0 | 0 | 0 | 0 | 31.0028 | 0 | 0 | 0 | 0 | 0 | 50.8124
4659 | 60.6249 | 0 | 0 | 0 | 0 | 30.3124 | 0 | 0 | 0 | 0 | 0 | 47.4777
4660 | 60.7541 | 0 | 0 | 0 | 0 | 30.3771 | 0 | 0 | 0 | 0 | 0 | 51.6154
4661 | 61.356 | 0 | 0 | 0 | 0 | 30.678 | 0 | 0 | 0 | 0 | 0 | 56.4353
4662 | 65.9462 | 0 | 0 | 0 | 0 | 32.9731 | 0 | 0 | 0 | 0 | 0 | 72.0875
4663 | 79.3064 | 0 | 42.9 | 0 | 56.3 | 39.6532 | 10.9 | 0 | 0 | 0 | 0 | 73.8169
4664 | 84.6377 | 0 | 42.9 | 0 | 37.6 | 42.3188 | 7.3 | 0 | 0 | 0 | 0 | 116.4824
4665 | 85.8811 | 0 | 42.9 | 0 | 0 | 42.9405 | 0 | 0 | 0 | 0 | 0 | 102.7038
4666 | 85.7401 | 0 | 42.9 | 0 | 0 | 42.87 | 0 | 1.1 | 0 | 0 | 0 | 87.882
4667 | 87.0662 | 0 | 42.9 | 0 | 0 | 43.5331 | 0 | 4.7 | 2.7 | 0 | 0 | 198.1175
4668 | 87.6349 | 0 | 42.9 | 0 | 0 | 43.8175 | 0 | 6.5 | 10.1 | 0 | 0 | 179.6031
4669 | 83.6754 | 0 | 42.9 | 0 | 75.1 | 41.8377 | 52.1 | 11.6 | 18.2 | 0 | 0 | 288.5298
4670 | 87.1694 | 0 | 42.9 | 0 | 37.6 | 43.5847 | 59.6 | 13.3 | 31.4 | 0 | 0 | 195.1137
4671 | 85.7931 | 0 | 42.9 | 0 | 0 | 42.8965 | 0 | 14.3 | 40.8 | 0 | 0 | 137.9839
4672 | 87.9455 | 0 | 42.9 | 0 | 0 | 43.9727 | 0 | 13.8 | 51.6 | 0 | 0 | 93.0041
4673 | 87.8522 | 0 | 42.9 | 0 | 0 | 43.9261 | 0 | 9.7 | 59 | 0 | 0 | 147.8869
4674 | 86.2133 | 0 | 42.9 | 0 | 37.6 | 43.1067 | 108.4 | 4.1 | 56.5 | 0 | 0 | 146.0306
4675 | 81.6804 | 0 | 42.9 | 0 | 75.1 | 40.8402 | 104.4 | 1 | 32.3 | 0 | 0 | 173.9824
4676 | 75.0065 | 0 | 42.9 | 0 | 75.1 | 37.5033 | 50.7 | 0 | 2.1 | 0 | 0 | 162.3915
4677 | 68.8291 | 0 | 42.9 | 0 | 75.1 | 34.4146 | 18.2 | 0 | 0 | 0 | 0 | 330.2196
4678 | 66.5562 | 0 | 42.9 | 0 | 93.9 | 33.2781 | 7.1 | 0 | 0 | 0 | 0 | 131.276
4679 | 67.1909 | 0 | 0 | 0 | 0 | 33.5954 | 0 | 0 | 0 | 0 | 0 | 139.3442
4680 | 65.5548 | 0 | 0 | 0 | 0 | 32.7774 | 0 | 0 | 0 | 0 | 0 | 192.4699
4681 | 62.0955 | 0 | 0 | 0 | 0 | 31.0477 | 0 | 0 | 0 | 0 | 0 | 54.7136
4682 | 64.2944 | 0 | 0 | 0 | 0 | 32.1472 | 0 | 0 | 0 | 0 | 0 | 45.315
4683 | 61.8977 | 0 | 0 | 0 | 0 | 30.9489 | 0 | 0 | 0 | 0 | 0 | 51.6159
4684 | 61.8345 | 0 | 0 | 0 | 0 | 30.9172 | 0 | 0 | 0 | 0 | 0 | 59.8956
4685 | 60.3961 | 0 | 0 | 0 | 0 | 30.1981 | 0 | 0 | 0 | 0 | 0 | 62.0855
4686 | 66.4031 | 0 | 0 | 0 | 0 | 33.2015 | 0 | 0 | 0 | 0 | 0 | 81.9639
4687 | 82.3346 | 0 | 42.9 | 0 | 56.3 | 41.1673 | 0 | 0 | 0 | 0 | 0 | 84.5687
4688 | 86.2849 | 0 | 42.9 | 0 | 37.6 | 43.1425 | 0 | 0 | 0 | 0 | 0 | 91.3395
4689 | 87.8327 | 0 | 42.9 | 0 | 0 | 43.9163 | 0 | 0 | 0 | 0 | 0 | 99.2288
4690 | 86.014 | 0 | 42.9 | 0 | 0 | 43.007 | 0 | 0 | 0 | 0 | 0 | 77.9287
4691 | 85.5959 | 0 | 42.9 | 0 | 0 | 42.798 | 0 | 0 | 0 | 0 | 0 | 131.88
4692 | 85.7177 | 0 | 42.9 | 0 | 0 | 42.8589 | 0 | 0 | 1 | 0 | 0 | 74.5112
4693 | 88.044 | 0 | 42.9 | 0 | 75.1 | 44.022 | 1.9 | 0.6 | 6.7 | 0 | 0 | 143.5809
4694 | 89.88 | 0 | 42.9 | 0 | 37.6 | 44.94 | 7.9 | 5.6 | 15.3 | 0 | 0 | 121.6874
4695 | 87.907 | 0 | 42.9 | 0 | 0 | 43.9535 | 0 | 10.4 | 27 | 0 | 0 | 134.167
4696 | 86.6825 | 0 | 42.9 | 0 | 0 | 43.3413 | 0 | 18.3 | 43.2 | 0 | 0 | 108.8504
4697 | 84.4433 | 0 | 42.9 | 0 | 0 | 42.2217 | 0 | 27 | 58.1 | 0 | 0 | 127.2542
4698 | 78.301 | 0 | 42.9 | 0 | 37.6 | 39.1505 | 70.7 | 31.5 | 64.7 | 0 | 0 | 172.3572
4699 | 69.2082 | 0 | 42.9 | 0 | 75.1 | 34.6041 | 81.3 | 30.8 | 73.6 | 0 | 0 | 194.5485
4700 | 63.5626 | 0 | 42.9 | 0 | 75.1 | 31.7813 | 40.9 | 4 | 22.2 | 0 | 0 | 246.2823
4701 | 63.0568 | 0 | 42.9 | 0 | 75.1 | 31.5284 | 14.3 | 0.1 | 2 | 0 | 0 | 267.9987
4702 | 63.4098 | 0 | 42.9 | 0 | 93.9 | 31.7049 | 3.3 | 0 | 0 | 0 | 0 | 224.3843
4703 | 60.0472 | 0 | 0 | 0 | 0 | 30.0236 | 0 | 0 | 0 | 0 | 0 | 128.9538
4704 | 61.5283 | 0 | 0 | 0 | 0 | 30.7641 | 0 | 0 | 0 | 0 | 0 | 72.0892
4705 | 60.8065 | 0 | 0 | 0 | 0 | 30.4032 | 0 | 0 | 0 | 0 | 0 | 61.6243
4706 | 59.794 | 0 | 0 | 0 | 0 | 29.897 | 0 | 0 | 0 | 0 | 0 | 66.6791
4707 | 59.9093 | 0 | 0 | 0 | 0 | 29.9546 | 0 | 0 | 0 | 0 | 0 | 61.8559
4708 | 57.1159 | 0 | 0 | 0 | 0 | 28.558 | 0 | 0 | 0 | 0 | 0 | 58.7487
4709 | 47.0698 | 0 | 0 | 0 | 0 | 23.5349 | 0 | 0 | 0 | 0 | 0 | 62.0865
4710 | 66.9061 | 0 | 0 | 0 | 0 | 33.453 | 0 | 0 | 0 | 0 | 0 | 56.321
4711 | 102.1774 | 0 | 42.9 | 0 | 56.3 | 51.0887 | 0 | 0 | 0 | 0 | 0 | 60.4725
4712 | 154.1657 | 0.7 | 43 | 0 | 37.6 | 77.0828 | 0 | 36.4 | 1.5 | 0 | 0 | 60.9336
4713 | 243.2293 | 2.1 | 43.2 | 0 | 0 | 121.6147 | 0 | 33.8 | 20.8 | 0 | 0 | 62.5447
4714 | 256.2882 | 3.5 | 43.4 | 0 | 0 | 128.1441 | 0 | 39.3 | 63.2 | 0 | 0 | 56.0923
4715 | 248.0911 | 3.5 | 43.4 | 0 | 0 | 124.0456 | 0 | 47.3 | 115.2 | 0 | 0 | 126.1811
4716 | 240.7063 | 2.8 | 43.3 | 0 | 0 | 120.3531 | 0 | 65.6 | 121.5 | 0 | 0 | 190.9554
4717 | 226.1464 | 1.4 | 43.1 | 0 | 75.1 | 113.0732 | 65.5 | 72.2 | 81.7 | 0 | 0 | 136.8934
4718 | 237.1195 | 2.1 | 43.2 | 0 | 37.6 | 118.5598 | 29.4 | 79.2 | 61.4 | 0 | 0 | 135.4561
4719 | 233.8691 | 3.5 | 43.4 | 0 | 0 | 116.9345 | 0 | 95 | 48.1 | 0 | 0 | 104.6202
4720 | 215.6363 | 2.8 | 43.3 | 0 | 0 | 107.8182 | 0 | 106.1 | 33.7 | 0 | 0 | 101.2649
4721 | 179.5084 | 2.1 | 43.2 | 0 | 0 | 89.7542 | 0 | 116.5 | 24.8 | 0 | 0 | 185.8281
4722 | 136.2044 | 0.7 | 43 | 0 | 37.6 | 68.1022 | 9.6 | 105.5 | 21.9 | 0 | 0 | 200.5623
4723 | 112.0202 | 0 | 42.9 | 0 | 75.1 | 56.0101 | 8 | 18.6 | 0 | 0 | 0 | 341.4188
4724 | 94.4222 | 0 | 42.9 | 0 | 75.1 | 47.2111 | 0 | 0.8 | 0 | 0 | 0 | 395.0503
4725 | 66.6327 | 0 | 42.9 | 0 | 75.1 | 33.3164 | 0 | 0 | 0 | 0 | 0 | 259.2136
4726 | 66.3786 | 0 | 42.9 | 0 | 93.9 | 33.1893 | 0 | 0 | 0 | 0 | 0 | 208.3898
4727 | 60.0066 | 0 | 0 | 0 | 0 | 30.0033 | 0 | 0 | 0 | 0 | 0 | 149.2743
4728 | 61.5878 | 0 | 0 | 0 | 0 | 30.7939 | 0 | 0 | 0 | 0 | 0 | 215.9721
4729 | 61.2887 | 0 | 0 | 0 | 0 | 30.6444 | 0 | 0 | 0 | 0 | 0 | 75.3259
4730 | 61.0442 | 0 | 0 | 0 | 0 | 30.5221 | 0 | 0 | 0 | 0 | 0 | 46.1088
4731 | 59.5581 | 0 | 0 | 0 | 0 | 29.7791 | 0 | 0 | 0 | 0 | 0 | 46.1068
4732 | 58.8608 | 0 | 0 | 0 | 0 | 29.4304 | 0 | 0 | 0 | 0 | 0 | 55.0581
4733 | 63.3928 | 0 | 0 | 0 | 0 | 31.6964 | 0 | 0 | 0 | 0 | 0 | 58.2877
4734 | 76.5416 | 0 | 0 | 0 | 0 | 38.2708 | 0 | 0 | 0 | 0 | 0 | 108.3651
4735 | 114.5966 | 0 | 42.9 | 0 | 56.3 | 57.2983 | 0 | 0 | 0 | 0 | 0 | 136.9934
4736 | 177.9702 | 0.7 | 43 | 0 | 37.6 | 88.9851 | 0 | 49.6 | 0 | 0 | 0 | 59.5514
4737 | 253.8485 | 2.1 | 43.2 | 0 | 0 | 126.9243 | 0 | 51.9 | 0 | 0 | 0 | 56.7832
4738 | 301.2974 | 3.5 | 43.4 | 0 | 0 | 150.6487 | 0 | 65.1 | 0 | 0 | 0 | 49.892
4739 | 272.2049 | 3.5 | 43.4 | 0 | 0 | 136.1025 | 0 | 74.2 | 0 | 0 | 0 | 108.7251
4740 | 246.7724 | 2.8 | 43.3 | 0 | 0 | 123.3862 | 0 | 96.9 | 1.2 | 0 | 0 | 143.1703
4741 | 235.424 | 1.4 | 43.1 | 0 | 75.1 | 117.712 | 0 | 100 | 4.8 | 0 | 0 | 94.3216
4742 | 233.5697 | 2.1 | 43.2 | 0 | 37.6 | 116.7848 | 0 | 110.6 | 9.4 | 0 | 0 | 202.4117
4743 | 238.8278 | 3.5 | 43.4 | 0 | 0 | 119.4139 | 0 | 134.4 | 14.8 | 0 | 0 | 95.7547
4744 | 211.1719 | 2.8 | 43.3 | 0 | 0 | 105.5859 | 0 | 146.6 | 21.5 | 0 | 0 | 151.8286
4745 | 150.5817 | 2.1 | 43.2 | 0 | 0 | 75.2909 | 0 | 155 | 41.1 | 0 | 0 | 107.1477
4746 | 115.0256 | 0.7 | 43 | 0 | 37.6 | 57.5128 | 0 | 135.8 | 50.8 | 0 | 0 | 129.4433
4747 | 101.9812 | 0 | 42.9 | 0 | 75.1 | 50.9906 | 6.8 | 38.8 | 22 | 0 | 0 | 126.0629
4748 | 77.7648 | 0 | 42.9 | 0 | 75.1 | 38.8824 | 0.3 | 15.9 | 0.1 | 0 | 0 | 144.9309
4749 | 64.1013 | 0 | 42.9 | 0 | 75.1 | 32.0506 | 0 | 5.4 | 0 | 0 | 0 | 137.9392
4750 | 62.022 | 0 | 42.9 | 0 | 93.9 | 31.011 | 0 | 1 | 0 | 0 | 0 | 152.2625
4751 | 62.9499 | 0 | 0 | 0 | 0 | 31.475 | 0 | 0 | 0 | 0 | 0 | 114.8962
4752 | 59.7493 | 0 | 0 | 0 | 0 | 29.8747 | 0 | 0 | 0 | 0 | 0 | 82.6735
4753 | 59.939 | 0 | 0 | 0 | 0 | 29.9695 | 0 | 0 | 0 | 0 | 0 | 67.2554
4754 | 60.0735 | 0 | 0 | 0 | 0 | 30.0368 | 0 | 0 | 0 | 0 | 0 | 59.4371
4755 | 60.6165 | 0 | 0 | 0 | 0 | 30.3083 | 0 | 0 | 0 | 0 | 0 | 50.1232
4756 | 61.545 | 0 | 0 | 0 | 0 | 30.7725 | 0 | 0 | 0 | 0 | 0 | 47.9402
4757 | 58.9079 | 0 | 0 | 0 | 0 | 29.4539 | 0 | 0 | 0 | 0 | 0 | 65.5246
4758 | 69.2088 | 0 | 0 | 0 | 0 | 34.6044 | 0 | 0 | 0 | 0 | 0 | 62.0848
4759 | 110.4719 | 0 | 42.9 | 0 | 56.3 | 55.2359 | 0 | 0 | 0 | 0 | 0 | 52.0749
4760 | 166.4557 | 0.7 | 43 | 0 | 37.6 | 83.2278 | 0 | 107.9 | 10.2 | 0 | 0 | 56.4371
4761 | 247.3129 | 2.1 | 43.2 | 0 | 0 | 123.6564 | 0 | 114.5 | 41.6 | 0 | 0 | 51.3861
4762 | 274.6803 | 3.5 | 43.4 | 0 | 0 | 137.3401 | 0 | 166.8 | 122 | 0 | 0 | 90.5006
4763 | 276.246 | 3.5 | 43.4 | 0 | 0 | 138.123 | 0 | 186 | 135.3 | 0 | 0 | 108.2445
4764 | 278.5593 | 2.8 | 43.3 | 0 | 0 | 139.2796 | 0 | 180.4 | 165.9 | 0 | 0 | 121.8948
4765 | 272.0714 | 1.4 | 43.1 | 0 | 75.1 | 136.0357 | 183.7 | 151.3 | 202.6 | 0 | 0 | 87.5254
4766 | 271.5222 | 2.1 | 43.2 | 0 | 37.6 | 135.7611 | 158.6 | 158.3 | 214.6 | 0 | 0 | 97.5504
4767 | 252.0163 | 3.5 | 43.4 | 0 | 0 | 126.0081 | 0 | 192.1 | 276.9 | 0 | 0 | 135.5364
4768 | 218.0215 | 2.8 | 43.3 | 0 | 0 | 109.0107 | 0 | 180.5 | 264.6 | 0 | 0 | 120.8202
4769 | 160.9369 | 2.1 | 43.2 | 0 | 0 | 80.4684 | 0 | 148.4 | 239.5 | 0 | 0 | 60.5898
4770 | 116.4754 | 0.7 | 43 | 0 | 37.6 | 58.2377 | 277.8 | 110.4 | 226.7 | 0 | 0 | 150.1101
4771 | 92.5968 | 0 | 42.9 | 0 | 75.1 | 46.2984 | 300.6 | 1.9 | 115.2 | 0 | 0 | 342.1074
4772 | 81.4854 | 0 | 42.9 | 0 | 75.1 | 40.7427 | 204.1 | 0 | 44.6 | 0 | 0 | 159.7074
4773 | 69.7316 | 0 | 42.9 | 0 | 75.1 | 34.8658 | 122.3 | 0 | 34.5 | 0 | 0 | 161.2235
4774 | 66.5087 | 0 | 42.9 | 0 | 93.9 | 33.2544 | 99.2 | 0 | 20.8 | 0 | 0 | 107.2708
4775 | 63.3429 | 0 | 0 | 0 | 0 | 31.6714 | 0 | 0 | 0 | 0 | 0 | 106.9114
4776 | 63.3051 | 0 | 0 | 0 | 0 | 31.6525 | 0 | 0 | 0 | 0 | 0 | 66.3332
4777 | 64.0573 | 0 | 0 | 0 | 0 | 32.0286 | 0 | 0 | 0 | 0 | 0 | 69.7853
4778 | 59.988 | 0 | 0 | 0 | 0 | 29.994 | 0 | 0 | 0 | 0 | 0 | 59.5527
4779 | 62.0446 | 0 | 0 | 0 | 0 | 31.0223 | 0 | 0 | 0 | 0 | 0 | 51.1555
4780 | 61.8351 | 0 | 0 | 0 | 0 | 30.9176 | 0 | 0 | 0 | 0 | 0 | 47.0197
4781 | 59.2566 | 0 | 0 | 0 | 0 | 29.6283 | 0 | 0 | 0 | 0 | 0 | 62.0845
4782 | 71.2053 | 0 | 0 | 0 | 0 | 35.6027 | 0 | 0 | 0 | 0 | 0 | 71.9721
4783 | 104.9602 | 0 | 42.9 | 0 | 56.3 | 52.4801 | 10.3 | 0 | 0 | 0 | 0 | 78.6503
4784 | 158.897 | 0.7 | 43 | 0 | 37.6 | 79.4485 | 30.7 | 64.2 | 38.4 | 0 | 0 | 66.3328
4785 | 277.7101 | 2.1 | 43.2 | 0 | 0 | 138.855 | 0 | 92.8 | 79.2 | 0 | 0 | 47.3641
4786 | 349.649 | 3.5 | 43.4 | 0 | 0 | 174.8245 | 0 | 127.1 | 136.5 | 0 | 0 | 149.0317
4787 | 351.6533 | 3.5 | 43.4 | 0 | 0 | 175.8266 | 0 | 145.9 | 187.1 | 0 | 0 | 150.8797
4788 | 329.0646 | 2.8 | 43.3 | 0 | 0 | 164.5323 | 0 | 145.2 | 222.8 | 0 | 0 | 158.6357
4789 | 295.4823 | 1.4 | 43.1 | 0 | 75.1 | 147.7411 | 418.3 | 124.4 | 250 | 0 | 0 | 216.9729
4790 | 287.86 | 2.1 | 43.2 | 0 | 37.6 | 143.93 | 383.7 | 122.7 | 274.5 | 0 | 0 | 142.0513
4791 | 263.7893 | 3.5 | 43.4 | 0 | 0 | 131.8946 | 0.3 | 133.1 | 305.1 | 0 | 0 | 225.1531
4792 | 233.0103 | 2.8 | 43.3 | 0 | 0 | 116.5051 | 10.9 | 123.6 | 320.7 | 0 | 0 | 116.5353
4793 | 182.9473 | 2.1 | 43.2 | 0 | 0 | 91.4736 | 29.8 | 113 | 322.9 | 0 | 0 | 214.0408
4794 | 145.9041 | 0.7 | 43 | 0 | 37.6 | 72.952 | 606.1 | 82.6 | 318.8 | 0 | 0 | 174.6655
4795 | 113.2438 | 0 | 42.9 | 0 | 75.1 | 56.6219 | 616.3 | 0.2 | 231.8 | 0 | 0 | 195.2986
4796 | 89.6652 | 0 | 42.9 | 0 | 75.1 | 44.8326 | 534.2 | 0 | 159.2 | 0 | 0 | 188.9133
4797 | 70.141 | 0 | 42.9 | 0 | 75.1 | 35.0705 | 433 | 0 | 122.5 | 0 | 0 | 177.5476
4798 | 67.7264 | 0 | 42.9 | 0 | 93.9 | 33.8632 | 376.1 | 0 | 87.8 | 0 | 0 | 190.5122
4799 | 69.3281 | 0 | 0 | 0 | 0 | 34.6641 | 0 | 0 | 0 | 0 | 0 | 209.2573
4800 | 67.9425 | 0 | 0 | 0 | 0 | 33.9712 | 0 | 0 | 0 | 0 | 0 | 66.4467
4801 | 66.1592 | 0 | 0 | 0 | 0 | 33.0796 | 0 | 0 | 0 | 0 | 0 | 51.9604
4802 | 65.2195 | 0 | 0 | 0 | 0 | 32.6097 | 0 | 0 | 0 | 0 | 0 | 52.0765
4803 | 64.2497 | 0 | 0 | 0 | 0 | 32.1249 | 0 | 0 | 0 | 0 | 0 | 53.683
4804 | 63.2741 | 0 | 0 | 0 | 0 | 31.637 | 0 | 0 | 0 | 0 | 0 | 48.7431
4805 | 63.6339 | 0 | 0 | 0 | 0 | 31.817 | 0 | 0 | 0 | 0 | 0 | 76.971
4806 | 76.7439 | 0 | 0 | 0 | 0 | 38.372 | 0 | 0 | 0 | 0 | 0 | 75.9111
4807 | 121.0607 | 0 | 42.9 | 0 | 56.3 | 60.5303 | 80.4 | 0 | 1 | 0 | 0 | 71.3934
4808 | 160.9784 | 0.7 | 43 | 0 | 37.6 | 80.4892 | 129.2 | 4.8 | 50.7 | 0 | 0 | 120.2812
4809 | 233.4026 | 2.1 | 43.2 | 0 | 0 | 116.7013 | 0 | 0.4 | 102.4 | 0 | 0 | 188.6101
4810 | 277.7423 | 3.5 | 43.4 | 0 | 0 | 138.8712 | 0 | 0.8 | 160.5 | 0 | 0 | 95.1555
4811 | 281.4171 | 3.5 | 43.4 | 0 | 0 | 140.7085 | 0 | 3.9 | 211.6 | 0 | 0 | 76.1485
4812 | 271.688 | 2.8 | 43.3 | 0 | 0 | 135.844 | 0 | 22.2 | 222.5 | 0 | 0 | 76.7343
4813 | 261.4323 | 1.4 | 43.1 | 0 | 75.1 | 130.7162 | 500.9 | 27.9 | 237.2 | 0 | 0 | 73.5876
4814 | 259.0329 | 2.1 | 43.2 | 0 | 37.6 | 129.5165 | 433.9 | 38.8 | 242.2 | 0 | 0 | 77.8052
4815 | 240.013 | 3.5 | 43.4 | 0 | 0 | 120.0065 | 0 | 56.2 | 253 | 0 | 0 | 73.2393
4816 | 186.9006 | 2.8 | 43.3 | 0 | 0 | 93.4503 | 0.3 | 62.1 | 248.7 | 0 | 0 | 112.3635
4817 | 137.5479 | 2.1 | 43.2 | 0 | 0 | 68.774 | 1.6 | 77.6 | 227.8 | 0 | 0 | 159.3543
4818 | 103.5197 | 0.7 | 43 | 0 | 37.6 | 51.7598 | 501.4 | 60 | 209.4 | 0 | 0 | 116.0559
4819 | 92.2621 | 0 | 42.9 | 0 | 75.1 | 46.131 | 462 | 0 | 110.1 | 0 | 0 | 248.9141
4820 | 80.4289 | 0 | 42.9 | 0 | 75.1 | 40.2145 | 337 | 0 | 46.1 | 0 | 0 | 180.8852
4821 | 66.9504 | 0 | 42.9 | 0 | 75.1 | 33.4752 | 236.4 | 0 | 24.9 | 0 | 0 | 134.5793
4822 | 66.0764 | 0 | 42.9 | 0 | 93.9 | 33.0382 | 174.8 | 0 | 12.6 | 0 | 0 | 157.4352
4823 | 62.1878 | 0 | 0 | 0 | 0 | 31.0939 | 0 | 0 | 0 | 0 | 0 | 143.2839
4824 | 64.021 | 0 | 0 | 0 | 0 | 32.0105 | 0 | 0 | 0 | 0 | 0 | 111.6249
4825 | 61.0293 | 0 | 0 | 0 | 0 | 30.5147 | 0 | 0 | 0 | 0 | 0 | 82.9114
4826 | 61.2413 | 0 | 0 | 0 | 0 | 30.6207 | 0 | 0 | 0 | 0 | 0 | 67.2546
4827 | 60.4042 | 0 | 0 | 0 | 0 | 30.2021 | 0 | 0 | 0 | 0 | 0 | 49.6632
4828 | 61.2676 | 0 | 0 | 0 | 0 | 30.6338 | 0 | 0 | 0 | 0 | 0 | 47.0206
4829 | 62.8228 | 0 | 0 | 0 | 0 | 31.4114 | 0 | 0 | 0 | 0 | 0 | 50.8103
4830 | 67.6496 | 0 | 0 | 0 | 0 | 33.8248 | 0 | 0 | 0 | 0 | 0 | 58.1716
4831 | 88.2046 | 0 | 42.9 | 0 | 56.3 | 44.1023 | 191.8 | 0 | 19.3 | 0 | 0 | 81.6104
4832 | 89.8998 | 0 | 42.9 | 0 | 37.6 | 44.9499 | 270.7 | 0 | 84.3 | 0 | 0 | 100.0702
4833 | 87.4158 | 0 | 42.9 | 0 | 0 | 43.7079 | 0 | 0.6 | 168.2 | 0 | 0 | 267.4479
4834 | 87.9368 | 0 | 42.9 | 0 | 0 | 43.9684 | 0.4 | 16.2 | 261.2 | 0 | 0 | 86.4622
4835 | 90.3595 | 0 | 42.9 | 0 | 0 | 45.1797 | 23.1 | 28.1 | 327.8 | 0 | 0 | 123.221
4836 | 88.9871 | 0 | 42.9 | 0 | 0 | 44.4936 | 81.2 | 29.8 | 377.9 | 0 | 0 | 130.447
4837 | 88.0205 | 0 | 42.9 | 0 | 75.1 | 44.0102 | 992.9 | 37.4 | 415.9 | 0 | 0 | 154.2926
4838 | 89.8654 | 0 | 42.9 | 0 | 37.6 | 44.9327 | 850.5 | 49.7 | 440.2 | 0 | 0 | 143.12
4839 | 83.1274 | 0 | 42.9 | 0 | 0 | 41.5637 | 200.8 | 60.5 | 482.2 | 0 | 0 | 126.0805
4840 | 86.1358 | 0 | 42.9 | 0 | 0 | 43.0679 | 321.8 | 66.7 | 491.3 | 0 | 0 | 88.4792
4841 | 83.4513 | 0 | 42.9 | 0 | 0 | 41.7256 | 374.1 | 66.2 | 496.6 | 0 | 0 | 201.1664
4842 | 83.3341 | 0 | 42.9 | 0 | 37.6 | 41.6671 | 1159.3 | 64.1 | 498.3 | 0 | 0 | 244.8951
4843 | 83.565 | 0 | 42.9 | 0 | 75.1 | 41.7825 | 1156.6 | 58.6 | 434.4 | 0 | 0 | 180.7944
4844 | 71.6612 | 0 | 42.9 | 0 | 75.1 | 35.8306 | 1032.8 | 23.1 | 335.3 | 0 | 0 | 238.6543
4845 | 66.0736 | 0 | 42.9 | 0 | 75.1 | 33.0368 | 897.2 | 18.5 | 282.4 | 0 | 0 | 330.1093
4846 | 61.5202 | 0 | 42.9 | 0 | 93.9 | 30.7601 | 910.5 | 13.6 | 262.2 | 0 | 0 | 288.4304
4847 | 61.3628 | 0 | 0 | 0 | 0 | 30.6814 | 133.9 | 8.8 | 63.7 | 0 | 0 | 159.3944
4848 | 62.3511 | 0 | 0 | 0 | 0 | 31.1756 | 145.8 | 4.7 | 62.3 | 0 | 0 | 102.8244
4849 | 62.4571 | 0 | 0 | 0 | 0 | 31.2286 | 119.4 | 0.9 | 49.1 | 0 | 0 | 50.9253
4850 | 59.9263 | 0 | 0 | 0 | 0 | 29.9632 | 87 | 0 | 34.5 | 0 | 0 | 47.0204
4851 | 61.9182 | 0 | 0 | 0 | 0 | 30.9591 | 63.4 | 0 | 22.5 | 0 | 0 | 46.6779
4852 | 61.0684 | 0 | 0 | 0 | 0 | 30.5342 | 45.3 | 0 | 15.2 | 0 | 0 | 61.1653
4853 | 61.1973 | 0 | 0 | 0 | 0 | 30.5986 | 32.4 | 0 | 10.4 | 0 | 0 | 58.4013
4854 | 71.4263 | 0 | 0 | 0 | 0 | 35.7131 | 29.9 | 0 | 7.7 | 0 | 0 | 67.1399
4855 | 86.0726 | 0 | 42.9 | 0 | 56.3 | 43.0363 | 937.8 | 22.4 | 197.3 | 0 | 0 | 64.2644
4856 | 92.1 | 0 | 42.9 | 0 | 37.6 | 46.05 | 781.2 | 45.4 | 181.5 | 0 | 0 | 81.8438
4857 | 89.9166 | 0 | 42.9 | 0 | 0 | 44.9583 | 31.6 | 64.1 | 188.1 | 0 | 0 | 104.2577
4858 | 85.8851 | 0 | 42.9 | 0 | 0 | 42.9426 | 64.8 | 78.3 | 204.1 | 0 | 0 | 124.3191
4859 | 85.2618 | 0 | 42.9 | 0 | 0 | 42.6309 | 90 | 82.1 | 223.9 | 0 | 0 | 177.2822
4860 | 79.9231 | 0 | 42.9 | 0 | 0 | 39.9616 | 113.6 | 76.2 | 250.9 | 0 | 0 | 123.1233
4861 | 81.9128 | 0 | 42.9 | 0 | 75.1 | 40.9564 | 1085.6 | 75.4 | 286.6 | 0 | 0 | 163.2541
4862 | 82.2742 | 0 | 42.9 | 0 | 37.6 | 41.1371 | 900.4 | 73.6 | 282.9 | 0 | 0 | 93.0054
4863 | 83.1634 | 0 | 42.9 | 0 | 0 | 41.5817 | 92 | 72.2 | 288.9 | 0 | 0 | 103.4185
4864 | 84.9352 | 0 | 42.9 | 0 | 0 | 42.4676 | 149.4 | 69.7 | 294.7 | 0 | 0 | 211.5664
4865 | 80.326 | 0 | 42.9 | 0 | 0 | 40.163 | 166.9 | 66.3 | 293 | 0 | 0 | 161.8651
4866 | 78.9233 | 0 | 42.9 | 0 | 37.6 | 39.4617 | 1032 | 59.5 | 270.7 | 0 | 0 | 125.9032
4867 | 86.372 | 0 | 42.9 | 0 | 75.1 | 43.186 | 955.2 | 48.8 | 239.2 | 0 | 0 | 123.4011
4868 | 76.032 | 0 | 42.9 | 0 | 75.1 | 38.016 | 810.7 | 16.7 | 149.8 | 0 | 0 | 232.7907
4869 | 66.6113 | 0 | 42.9 | 0 | 75.1 | 33.3057 | 701.5 | 12.4 | 140.6 | 0 | 0 | 260.6472
4870 | 62.3886 | 0 | 42.9 | 0 | 93.9 | 31.1943 | 651.9 | 6.8 | 115.5 | 0 | 0 | 197.656
4871 | 62.3533 | 0 | 0 | 0 | 0 | 31.1767 | 0 | 2.7 | 0 | 0 | 0 | 176.9613
4872 | 62.5145 | 0 | 0 | 0 | 0 | 31.2572 | 0 | 0.1 | 0 | 0 | 0 | 92.6529
4873 | 60.2982 | 0 | 0 | 0 | 0 | 30.1491 | 0 | 0 | 0 | 0 | 0 | 71.3943
4874 | 60.7157 | 0 | 0 | 0 | 0 | 30.3578 | 0 | 0 | 0 | 0 | 0 | 47.134
4875 | 61.4393 | 0 | 0 | 0 | 0 | 30.7197 | 0 | 0 | 0 | 0 | 0 | 48.0542
4876 | 60.0233 | 0 | 0 | 0 | 0 | 30.0117 | 0 | 0 | 0 | 0 | 0 | 49.0889
4877 | 62.229 | 0 | 0 | 0 | 0 | 31.1145 | 0 | 0 | 0 | 0 | 0 | 50.2366
4878 | 78.1206 | 0 | 0 | 0 | 0 | 39.0603 | 0 | 0 | 0 | 0 | 0 | 57.4785
4879 | 118.2252 | 0 | 42.9 | 0 | 56.3 | 59.1126 | 304.9 | 1.1 | 22.6 | 0 | 0 | 73.5867
4880 | 181.3245 | 0.7 | 43 | 0 | 37.6 | 90.6622 | 333.1 | 107.6 | 109.4 | 0 | 0 | 240.3265
4881 | 307.811 | 2.1 | 43.2 | 0 | 0 | 153.9055 | 0 | 99.5 | 179.7 | 0 | 0 | 76.2638
4882 | 391.2053 | 3.5 | 43.4 | 0 | 0 | 195.6026 | 3.6 | 120.4 | 257.5 | 0 | 0 | 78.7684
4883 | 356.6557 | 3.5 | 43.4 | 0 | 0 | 178.3279 | 28.2 | 135.2 | 306.2 | 0 | 0 | 78.2843
4884 | 312.7103 | 2.8 | 43.3 | 0 | 0 | 156.3551 | 67.7 | 145.6 | 338.3 | 0 | 0 | 113.4424
4885 | 287.2588 | 1.4 | 43.1 | 0 | 75.1 | 143.6294 | 845.8 | 123.1 | 362.6 | 0 | 0 | 196.365
4886 | 279.0865 | 2.1 | 43.2 | 0 | 37.6 | 139.5432 | 749.7 | 133.6 | 382.4 | 0 | 0 | 132.4085
4887 | 262.4198 | 3.5 | 43.4 | 0 | 0 | 131.2099 | 152.5 | 168.1 | 414.7 | 0 | 0 | 123.3686
4888 | 225.9422 | 2.8 | 43.3 | 0 | 0 | 112.9711 | 244.3 | 176.3 | 436.6 | 0 | 0 | 191.8164
4889 | 181.0446 | 2.1 | 43.2 | 0 | 0 | 90.5223 | 297.6 | 177.7 | 448.3 | 0 | 0 | 130.0031
4890 | 126.6811 | 0.7 | 43 | 0 | 37.6 | 63.3406 | 1051.8 | 155.5 | 456.3 | 0 | 0 | 132.3986
4891 | 99.4148 | 0 | 42.9 | 0 | 75.1 | 49.7074 | 1048.3 | 53.3 | 360.1 | 0 | 0 | 153.963
4892 | 82.6582 | 0 | 42.9 | 0 | 75.1 | 41.3291 | 914.3 | 33.4 | 271.2 | 0 | 0 | 257.7244
4893 | 65.415 | 0 | 42.9 | 0 | 75.1 | 32.7075 | 762 | 21.3 | 208.8 | 0 | 0 | 221.8404
4894 | 64.1533 | 0 | 42.9 | 0 | 93.9 | 32.0767 | 695.3 | 15.9 | 168.5 | 0 | 0 | 291.493
4895 | 65.3549 | 0 | 0 | 0 | 0 | 32.6775 | 27.8 | 9.7 | 12.6 | 0 | 0 | 249.297
4896 | 60.8121 | 0 | 0 | 0 | 0 | 30.406 | 22.7 | 4.2 | 5.1 | 0 | 0 | 113.922
4897 | 62.6886 | 0 | 0 | 0 | 0 | 31.3443 | 12.4 | 0.3 | 0 | 0 | 0 | 76.4995
4898 | 61.3024 | 0 | 0 | 0 | 0 | 30.6512 | 2.4 | 0 | 0 | 0 | 0 | 61.165
4899 | 60.4634 | 0 | 0 | 0 | 0 | 30.2317 | 0 | 0 | 0 | 0 | 0 | 58.054
4900 | 57.6676 | 0 | 0 | 0 | 0 | 28.8338 | 0 | 0 | 0 | 0 | 0 | 62.0838
4901 | 49.0102 | 0 | 0 | 0 | 0 | 24.5051 | 0 | 0 | 0 | 0 | 0 | 76.0318
4902 | 63.7613 | 0 | 0 | 0 | 0 | 31.8806 | 0 | 0 | 0 | 0 | 0 | 96.5908
4903 | 99.0382 | 0 | 42.9 | 0 | 56.3 | 49.5191 | 487.6 | 9.2 | 51.7 | 0 | 0 | 70.013
4904 | 186.9313 | 0.7 | 43 | 0 | 37.6 | 93.4657 | 477.2 | 134.9 | 145.5 | 0 | 0 | 49.6635
4905 | 326.9165 | 2.1 | 43.2 | 0 | 0 | 163.4582 | 4.5 | 137.2 | 214 | 0 | 0 | 73.5858
4906 | 375.3431 | 3.5 | 43.4 | 0 | 0 | 187.6716 | 26.6 | 166.2 | 287.2 | 0 | 0 | 73.3548
4907 | 331.6964 | 3.5 | 43.4 | 0 | 0 | 165.8482 | 66.1 | 174.7 | 336.1 | 0 | 0 | 203.2012
4908 | 278.0901 | 2.8 | 43.3 | 0 | 0 | 139.045 | 110.6 | 164.2 | 381.5 | 0 | 0 | 207.0348
4909 | 260.625 | 1.4 | 43.1 | 0 | 75.1 | 130.3125 | 1037.3 | 139.2 | 416.5 | 0 | 0 | 181.9155
4910 | 248.2588 | 2.1 | 43.2 | 0 | 37.6 | 124.1294 | 900.5 | 140.1 | 444.7 | 0 | 0 | 93.3647
4911 | 243.4782 | 3.5 | 43.4 | 0 | 0 | 121.7391 | 186.4 | 163.2 | 486.3 | 0 | 0 | 144.5032
4912 | 214.5473 | 2.8 | 43.3 | 0 | 0 | 107.2736 | 295.1 | 158.9 | 501.8 | 0 | 0 | 142.5561
4913 | 169.8078 | 2.1 | 43.2 | 0 | 0 | 84.9039 | 353.7 | 143.7 | 509.5 | 0 | 0 | 98.7542
4914 | 132.2628 | 0.7 | 43 | 0 | 37.6 | 66.1314 | 1247 | 112.5 | 509.9 | 0 | 0 | 99.2326
4915 | 107.0925 | 0 | 42.9 | 0 | 75.1 | 53.5462 | 1182.3 | 12.4 | 393.6 | 0 | 0 | 148.485
4916 | 92.7638 | 0 | 42.9 | 0 | 75.1 | 46.3819 | 1010.5 | 0 | 286.6 | 0 | 0 | 194.0247
4917 | 72.6142 | 0 | 42.9 | 0 | 75.1 | 36.3071 | 857.3 | 0 | 223 | 0 | 0 | 231.6215
4918 | 68.2899 | 0 | 42.9 | 0 | 93.9 | 34.1449 | 818.1 | 0 | 178.6 | 0 | 0 | 239.4311
4919 | 66.5503 | 0 | 0 | 0 | 0 | 33.2751 | 33.9 | 0 | 16.9 | 0 | 0 | 139.9913
4920 | 66.0163 | 0 | 0 | 0 | 0 | 33.0081 | 30.2 | 0 | 12 | 0 | 0 | 108.7288
4921 | 66.1031 | 0 | 0 | 0 | 0 | 33.0515 | 25.2 | 0 | 2.9 | 0 | 0 | 66.2177
4922 | 65.0348 | 0 | 0 | 0 | 0 | 32.5174 | 20.2 | 0 | 0 | 0 | 0 | 58.7496
4923 | 62.0474 | 0 | 0 | 0 | 0 | 31.0237 | 14.7 | 0 | 0 | 0 | 0 | 51.2705
4924 | 60.1402 | 0 | 0 | 0 | 0 | 30.0701 | 4.3 | 0 | 0 | 0 | 0 | 46.6774
4925 | 63.4855 | 0 | 0 | 0 | 0 | 31.7427 | 0 | 0 | 0 | 0 | 0 | 51.2698
4926 | 79.1282 | 0 | 0 | 0 | 0 | 39.5641 | 0 | 0 | 0 | 0 | 0 | 55.6333
4927 | 114.1441 | 0 | 42.9 | 0 | 56.3 | 57.0721 | 629 | 0 | 81.3 | 0 | 0 | 98.0362
4928 | 194.9586 | 0.7 | 43 | 0 | 37.6 | 97.4793 | 439.9 | 16.8 | 120.7 | 0 | 0 | 122.0061
4929 | 303.3729 | 2.1 | 43.2 | 0 | 0 | 151.6865 | 0 | 13.4 | 110.1 | 0 | 0 | 80.0709
4930 | 319.2161 | 3.5 | 43.4 | 0 | 0 | 159.6081 | 0 | 21.7 | 100.8 | 0 | 0 | 123.2105
4931 | 326.7538 | 3.5 | 43.4 | 0 | 0 | 163.3769 | 0 | 33.7 | 88.1 | 0 | 0 | 80.6619
4932 | 315.6523 | 2.8 | 43.3 | 0 | 0 | 157.8262 | 0 | 60.4 | 79.6 | 0 | 0 | 120.8283
4933 | 277.2815 | 1.4 | 43.1 | 0 | 75.1 | 138.6407 | 407.2 | 66.8 | 79.6 | 0 | 0 | 133.5455
4934 | 273.2534 | 2.1 | 43.2 | 0 | 37.6 | 136.6267 | 309.9 | 73.3 | 78.6 | 0 | 0 | 61.2794
4935 | 261.4051 | 3.5 | 43.4 | 0 | 0 | 130.7025 | 0 | 91.7 | 74.8 | 0 | 0 | 54.4852
4936 | 215.5409 | 2.8 | 43.3 | 0 | 0 | 107.7704 | 0 | 97.7 | 66.3 | 0 | 0 | 129.8916
4937 | 161.2707 | 2.1 | 43.2 | 0 | 0 | 80.6353 | 0 | 102.7 | 63.3 | 0 | 0 | 98.6365
4938 | 129.0245 | 0.7 | 43 | 0 | 37.6 | 64.5122 | 237.7 | 91.4 | 57.8 | 0 | 0 | 78.2853
4939 | 109.1745 | 0 | 42.9 | 0 | 75.1 | 54.5873 | 222.4 | 10.6 | 16.1 | 0 | 0 | 123.6009
4940 | 93.5575 | 0 | 42.9 | 0 | 75.1 | 46.7788 | 98.3 | 0.1 | 0 | 0 | 0 | 150.8592
4941 | 69.5801 | 0 | 42.9 | 0 | 75.1 | 34.79 | 50.1 | 0 | 0 | 0 | 0 | 250.0406
4942 | 67.8842 | 0 | 42.9 | 0 | 93.9 | 33.9421 | 37.1 | 0 | 0 | 0 | 0 | 173.0336
4943 | 66.9832 | 0 | 0 | 0 | 0 | 33.4916 | 0 | 0 | 0 | 0 | 0 | 142.8555
4944 | 65.7752 | 0 | 0 | 0 | 0 | 32.8876 | 0 | 0 | 0 | 0 | 0 | 82.4399
4945 | 63.8998 | 0 | 0 | 0 | 0 | 31.9499 | 0 | 0 | 0 | 0 | 0 | 56.6685
4946 | 61.8949 | 0 | 0 | 0 | 0 | 30.9475 | 0 | 0 | 0 | 0 | 0 | 50.2381
4947 | 62.1937 | 0 | 0 | 0 | 0 | 31.0968 | 0 | 0 | 0 | 0 | 0 | 46.5625
4948 | 64.2203 | 0 | 0 | 0 | 0 | 32.1101 | 0 | 0 | 0 | 0 | 0 | 48.7427
4949 | 64.5869 | 0 | 0 | 0 | 0 | 32.2935 | 0 | 0 | 0 | 0 | 0 | 51.4993
4950 | 90.9319 | 0 | 0 | 0 | 0 | 45.4659 | 0 | 0 | 0 | 0 | 0 | 56.7838
4951 | 138.1154 | 0 | 42.9 | 0 | 56.3 | 69.0577 | 0 | 0 | 0 | 0 | 0 | 58.9791
4952 | 194.8687 | 0.7 | 43 | 0 | 37.6 | 97.4344 | 0 | 30.5 | 0 | 0 | 0 | 89.0708
4953 | 262.7012 | 2.1 | 43.2 | 0 | 0 | 131.3506 | 0 | 27.7 | 0 | 0 | 0 | 87.885
4954 | 293.7374 | 3.5 | 43.4 | 0 | 0 | 146.8687 | 0 | 27.5 | 0 | 0 | 0 | 66.332
4955 | 277.3112 | 3.5 | 43.4 | 0 | 0 | 138.6556 | 0 | 29.2 | 10.4 | 0 | 0 | 99.5951
4956 | 243.5997 | 2.8 | 43.3 | 0 | 0 | 121.7999 | 0 | 52 | 24.6 | 0 | 0 | 327.2574
4957 | 230.08 | 1.4 | 43.1 | 0 | 75.1 | 115.04 | 26.6 | 61.3 | 48.3 | 0 | 0 | 322.1296
4958 | 235.7618 | 2.1 | 43.2 | 0 | 37.6 | 117.8809 | 42.6 | 60.7 | 72.2 | 0 | 0 | 201.7998
4959 | 229.1214 | 3.5 | 43.4 | 0 | 0 | 114.5607 | 0 | 67.4 | 96.1 | 0 | 0 | 150.4104
4960 | 201.4047 | 2.8 | 43.3 | 0 | 0 | 100.7023 | 0 | 75.9 | 118.4 | 0 | 0 | 175.3027
4961 | 153.5836 | 2.1 | 43.2 | 0 | 0 | 76.7918 | 0 | 93.8 | 138.2 | 0 | 0 | 70.2428
4962 | 127.8812 | 0.7 | 43 | 0 | 37.6 | 63.9406 | 161.1 | 94.9 | 147.7 | 0 | 0 | 149.7153
4963 | 118.2413 | 0 | 42.9 | 0 | 75.1 | 59.1207 | 169.2 | 10.5 | 84.1 | 0 | 0 | 208.363
4964 | 98.2702 | 0 | 42.9 | 0 | 75.1 | 49.1351 | 100.8 | 0 | 28 | 0 | 0 | 169.0047
4965 | 76.1225 | 0 | 42.9 | 0 | 75.1 | 38.0613 | 36.5 | 0 | 5 | 0 | 0 | 173.876
4966 | 66.8419 | 0 | 42.9 | 0 | 93.9 | 33.421 | 18.7 | 0 | 0 | 0 | 0 | 155.8893
4967 | 65.826 | 0 | 0 | 0 | 0 | 32.913 | 0 | 0 | 0 | 0 | 0 | 176.8594
4968 | 65.9035 | 0 | 0 | 0 | 0 | 32.9517 | 0 | 0 | 0 | 0 | 0 | 83.8513
4969 | 63.5217 | 0 | 0 | 0 | 0 | 31.7609 | 0 | 0 | 0 | 0 | 0 | 56.0929
4970 | 62.7509 | 0 | 0 | 0 | 0 | 31.3755 | 0 | 0 | 0 | 0 | 0 | 52.993
4971 | 61.0225 | 0 | 0 | 0 | 0 | 30.5113 | 0 | 0 | 0 | 0 | 0 | 50.3515
4972 | 59.6579 | 0 | 0 | 0 | 0 | 29.829 | 0 | 0 | 0 | 0 | 0 | 52.8783
4973 | 62.0136 | 0 | 0 | 0 | 0 | 31.0068 | 0 | 0 | 0 | 0 | 0 | 56.5533
4974 | 77.489 | 0 | 0 | 0 | 0 | 38.7445 | 0 | 0 | 0 | 0 | 0 | 59.4378
4975 | 129.5256 | 0 | 42.9 | 0 | 56.3 | 64.7628 | 0 | 0 | 0 | 0 | 0 | 103.0582
4976 | 199.5597 | 0.7 | 43 | 0 | 37.6 | 99.7799 | 0 | 3.5 | 1.4 | 0 | 0 | 142.7836
4977 | 281.7155 | 2.1 | 43.2 | 0 | 0 | 140.8578 | 0 | 1.3 | 22.2 | 0 | 0 | 68.8632
4978 | 303.2868 | 3.5 | 43.4 | 0 | 0 | 151.6434 | 0 | 3.3 | 61.2 | 0 | 0 | 57.8213
4979 | 258.5566 | 3.5 | 43.4 | 0 | 0 | 129.2783 | 0 | 11.2 | 102.1 | 0 | 0 | 126.0184
4980 | 247.2965 | 2.8 | 43.3 | 0 | 0 | 123.6482 | 0 | 34.1 | 147.9 | 0 | 0 | 198.5665
4981 | 241.3221 | 1.4 | 43.1 | 0 | 75.1 | 120.661 | 240.3 | 46.7 | 191.1 | 0 | 0 | 232.7066
4982 | 235.0607 | 2.1 | 43.2 | 0 | 37.6 | 117.5304 | 247.4 | 60.7 | 221.7 | 0 | 0 | 127.8512
4983 | 226.5651 | 3.5 | 43.4 | 0 | 0 | 113.2826 | 0 | 83.7 | 257 | 0 | 0 | 88.7197
4984 | 200.2093 | 2.8 | 43.3 | 0 | 0 | 100.1047 | 0.7 | 97.5 | 291.2 | 0 | 0 | 203.544
4985 | 152.109 | 2.1 | 43.2 | 0 | 0 | 76.0545 | 8.1 | 111 | 311.8 | 0 | 0 | 85.7481
4986 | 112.9172 | 0.7 | 43 | 0 | 37.6 | 56.4586 | 532.8 | 106.8 | 315.2 | 0 | 0 | 85.7487
4987 | 90.7878 | 0 | 42.9 | 0 | 75.1 | 45.3939 | 547.8 | 16.5 | 234.6 | 0 | 0 | 178.736
4988 | 78.0044 | 0 | 42.9 | 0 | 75.1 | 39.0022 | 454.4 | 0.5 | 155.5 | 0 | 0 | 326.1348
4989 | 72.0517 | 0 | 42.9 | 0 | 75.1 | 36.0259 | 339.7 | 0 | 108.6 | 0 | 0 | 221.8901
4990 | 69.4409 | 0 | 42.9 | 0 | 93.9 | 34.7205 | 296 | 0 | 79 | 0 | 0 | 170.315
4991 | 67.0263 | 0 | 0 | 0 | 0 | 33.5132 | 0 | 0 | 0 | 0 | 0 | 130.7016
4992 | 69.3988 | 0 | 0 | 0 | 0 | 34.6994 | 0 | 0 | 0 | 0 | 0 | 102.6973
4993 | 65.8864 | 0 | 0 | 0 | 0 | 32.9432 | 0 | 0 | 0 | 0 | 0 | 81.3729
4994 | 66.4942 | 0 | 0 | 0 | 0 | 33.2471 | 0 | 0 | 0 | 0 | 0 | 63.348
4995 | 64.5156 | 0 | 0 | 0 | 0 | 32.2578 | 0 | 0 | 0 | 0 | 0 | 59.668
4996 | 66.4815 | 0 | 0 | 0 | 0 | 33.2407 | 0 | 0 | 0 | 0 | 0 | 49.5489
4997 | 63.8329 | 0 | 0 | 0 | 0 | 31.9164 | 0 | 0 | 0 | 0 | 0 | 54.8287
4998 | 70.044 | 0 | 0 | 0 | 0 | 35.022 | 0 | 0 | 0 | 0 | 0 | 94.7988
4999 | 90.6282 | 0 | 42.9 | 0 | 56.3 | 45.3141 | 122.3 | 0 | 6.7 | 0 | 0 | 84.567
5000 | 84.3138 | 0 | 42.9 | 0 | 37.6 | 42.1569 | 157 | 0 | 42.6 | 0 | 0 | 103.4177
5001 | 84.3281 | 0 | 42.9 | 0 | 0 | 42.164 | 0 | 0 | 90 | 0 | 0 | 97.1912
5002 | 82.7245 | 0 | 42.9 | 0 | 0 | 41.3623 | 0 | 0 | 149.4 | 0 | 0 | 68.6312
5003 | 80.115 | 0 | 42.9 | 0 | 0 | 40.0575 | 0 | 0 | 213 | 0 | 0 | 125.6901
5004 | 78.9298 | 0 | 42.9 | 0 | 0 | 39.4649 | 0 | 2.3 | 265.4 | 0 | 0 | 299.276
5005 | 79.9699 | 0 | 42.9 | 0 | 75.1 | 39.985 | 674.1 | 7.7 | 306 | 0 | 0 | 161.3398
5006 | 82.9201 | 0 | 42.9 | 0 | 37.6 | 41.46 | 610.5 | 12.9 | 334 | 0 | 0 | 207.9399
5007 | 79.1369 | 0 | 42.9 | 0 | 0 | 39.5684 | 26.8 | 18.7 | 368.3 | 0 | 0 | 151.4508
5008 | 80.6936 | 0 | 42.9 | 0 | 0 | 40.3468 | 82.4 | 22.9 | 397.6 | 0 | 0 | 69.4378
5009 | 79.1471 | 0 | 42.9 | 0 | 0 | 39.5735 | 132.4 | 30.2 | 419.7 | 0 | 0 | 69.3222
5010 | 79.1508 | 0 | 42.9 | 0 | 37.6 | 39.5754 | 1001.3 | 32.5 | 430.3 | 0 | 0 | 88.4798
5011 | 77.0793 | 0 | 42.9 | 0 | 75.1 | 38.5396 | 975.1 | 32.8 | 362.2 | 0 | 0 | 125.9915
5012 | 69.3991 | 0 | 42.9 | 0 | 75.1 | 34.6995 | 823.7 | 6.8 | 248.9 | 0 | 0 | 275.538
5013 | 62.9728 | 0 | 42.9 | 0 | 75.1 | 31.4864 | 677.6 | 0.3 | 185.2 | 0 | 0 | 189.0188
5014 | 65.1705 | 0 | 42.9 | 0 | 93.9 | 32.5853 | 612 | 0 | 141 | 0 | 0 | 169.9824
5015 | 61.6758 | 0 | 0 | 0 | 0 | 30.8379 | 4.6 | 0 | 3 | 0 | 0 | 132.4047
5016 | 62.2653 | 0 | 0 | 0 | 0 | 31.1326 | 2.8 | 0 | 1 | 0 | 0 | 66.6784
5017 | 62.8476 | 0 | 0 | 0 | 0 | 31.4238 | 0.3 | 0 | 0 | 0 | 0 | 52.0771
5018 | 62.1819 | 0 | 0 | 0 | 0 | 31.091 | 0 | 0 | 0 | 0 | 0 | 53.3386
5019 | 63.24 | 0 | 0 | 0 | 0 | 31.62 | 0 | 0 | 0 | 0 | 0 | 47.2486
5020 | 58.9891 | 0 | 0 | 0 | 0 | 29.4945 | 0 | 0 | 0 | 0 | 0 | 47.4782
5021 | 61.5153 | 0 | 0 | 0 | 0 | 30.7576 | 0 | 0 | 0 | 0 | 0 | 51.6146
5022 | 64.8042 | 0 | 0 | 0 | 0 | 32.4021 | 0 | 0 | 0 | 0 | 0 | 65.9865
5023 | 81.632 | 0 | 42.9 | 0 | 56.3 | 40.816 | 603.1 | 0 | 115.9 | 0 | 0 | 51.5009
5024 | 82.8194 | 0 | 42.9 | 0 | 37.6 | 41.4097 | 492.5 | 0 | 119.2 | 0 | 0 | 74.0467
5025 | 86.4482 | 0 | 42.9 | 0 | 0 | 43.2241 | 0 | 0 | 132.8 | 0 | 0 | 85.9841
5026 | 85.3533 | 0 | 42.9 | 0 | 0 | 42.6766 | 0 | 0 | 149.1 | 0 | 0 | 159.548
5027 | 88.6239 | 0 | 42.9 | 0 | 0 | 44.3119 | 2.4 | 0 | 171.1 | 0 | 0 | 125.3422
5028 | 85.8721 | 0 | 42.9 | 0 | 0 | 42.936 | 9.8 | 0.2 | 184.4 | 0 | 0 | 97.1941
5029 | 87.6681 | 0 | 42.9 | 0 | 75.1 | 43.834 | 808.2 | 4.2 | 193.7 | 0 | 0 | 165.6528
5030 | 90.2559 | 0 | 42.9 | 0 | 37.6 | 45.128 | 663.2 | 21.5 | 202.8 | 0 | 0 | 110.295
5031 | 91.7749 | 0 | 42.9 | 0 | 0 | 45.8874 | 13.6 | 42.5 | 219.8 | 0 | 0 | 100.5479
5032 | 92.6334 | 0 | 42.9 | 0 | 0 | 46.3167 | 29.4 | 66.2 | 222.6 | 0 | 0 | 130.666
5033 | 93.0143 | 0 | 42.9 | 0 | 0 | 46.5071 | 36.9 | 66.5 | 214.5 | 0 | 0 | 129.4528
5034 | 91.2929 | 0 | 42.9 | 0 | 37.6 | 45.6465 | 748.8 | 59.8 | 206.7 | 0 | 0 | 115.1375
5035 | 84.8307 | 0 | 42.9 | 0 | 75.1 | 42.4154 | 744.8 | 43 | 187.4 | 0 | 0 | 306.9386
5036 | 75.4971 | 0 | 42.9 | 0 | 75.1 | 37.7486 | 623.6 | 13.9 | 112.7 | 0 | 0 | 252.4944
5037 | 66.1356 | 0 | 42.9 | 0 | 75.1 | 33.0678 | 512.4 | 13.1 | 98 | 0 | 0 | 191.881
5038 | 69.5138 | 0 | 42.9 | 0 | 93.9 | 34.7569 | 499 | 8.2 | 86.6 | 0 | 0 | 202.8246
5039 | 68.6856 | 0 | 0 | 0 | 0 | 34.3428 | 0 | 3.3 | 0 | 0 | 0 | 267.7937
5040 | 67.265 | 0 | 0 | 0 | 0 | 33.6325 | 0 | 0.1 | 0 | 0 | 0 | 86.6985
5041 | 62.6769 | 0 | 0 | 0 | 0 | 31.3384 | 0 | 0 | 0 | 0 | 0 | 66.7953
5042 | 62.432 | 0 | 0 | 0 | 0 | 31.216 | 0 | 0 | 0 | 0 | 0 | 59.4368
5043 | 60.7755 | 0 | 0 | 0 | 0 | 30.3877 | 0 | 0 | 0 | 0 | 0 | 55.978
5044 | 62.4454 | 0 | 0 | 0 | 0 | 31.2227 | 0 | 0 | 0 | 0 | 0 | 55.4029
5045 | 63.8955 | 0 | 0 | 0 | 0 | 31.9477 | 0 | 0 | 0 | 0 | 0 | 51.8445
5046 | 73.6593 | 0 | 0 | 0 | 0 | 36.8296 | 0 | 0 | 0 | 0 | 0 | 50.9273
5047 | 114.8192 | 0 | 42.9 | 0 | 56.3 | 57.4096 | 211 | 0 | 7.9 | 0 | 0 | 50.4657
5048 | 167.6467 | 0.7 | 43 | 0 | 37.6 | 83.8233 | 144.4 | 41.7 | 34.5 | 0 | 0 | 54.8299
5049 | 244.5372 | 2.1 | 43.2 | 0 | 0 | 122.2686 | 0 | 25 | 33 | 0 | 0 | 69.7833
5050 | 301.6655 | 3.5 | 43.4 | 0 | 0 | 150.8328 | 0 | 21.5 | 35.3 | 0 | 0 | 53.6822
5051 | 293.6113 | 3.5 | 43.4 | 0 | 0 | 146.8056 | 0 | 29 | 44.9 | 0 | 0 | 93.4838
5052 | 261.5306 | 2.8 | 43.3 | 0 | 0 | 130.7653 | 0 | 64.9 | 47 | 0 | 0 | 132.8906
5053 | 234.2137 | 1.4 | 43.1 | 0 | 75.1 | 117.1069 | 167.1 | 75.3 | 47.1 | 0 | 0 | 169.9924
5054 | 244.6956 | 2.1 | 43.2 | 0 | 37.6 | 122.3478 | 131.5 | 77.7 | 52.2 | 0 | 0 | 127.5031
5055 | 231.4139 | 3.5 | 43.4 | 0 | 0 | 115.7069 | 0 | 87.8 | 50.7 | 0 | 0 | 93.8433
5056 | 193.1434 | 2.8 | 43.3 | 0 | 0 | 96.5717 | 0 | 72.9 | 51 | 0 | 0 | 90.1434
5057 | 141.1762 | 2.1 | 43.2 | 0 | 0 | 70.5881 | 0 | 62.9 | 49.8 | 0 | 0 | 105.2239
5058 | 112.4436 | 0.7 | 43 | 0 | 37.6 | 56.2218 | 71.7 | 57.1 | 37.2 | 0 | 0 | 190.7449
5059 | 84.3962 | 0 | 42.9 | 0 | 75.1 | 42.1981 | 85.6 | 0 | 0.8 | 0 | 0 | 221.9662
5060 | 75.4286 | 0 | 42.9 | 0 | 75.1 | 37.7143 | 41.1 | 0 | 0 | 0 | 0 | 175.8342
5061 | 71.4802 | 0 | 42.9 | 0 | 75.1 | 35.7401 | 12.8 | 0 | 0 | 0 | 0 | 159.065
5062 | 68.4104 | 0 | 42.9 | 0 | 93.9 | 34.2052 | 4.8 | 0 | 0 | 0 | 0 | 149.0238
5063 | 66.8875 | 0 | 0 | 0 | 0 | 33.4437 | 0 | 0 | 0 | 0 | 0 | 153.0297
5064 | 68.2143 | 0 | 0 | 0 | 0 | 34.1071 | 0 | 0 | 0 | 0 | 0 | 80.4273
5065 | 63.2921 | 0 | 0 | 0 | 0 | 31.646 | 0 | 0 | 0 | 0 | 0 | 65.2972
5066 | 66.5856 | 0 | 0 | 0 | 0 | 33.2928 | 0 | 0 | 0 | 0 | 0 | 47.593
5067 | 63.6993 | 0 | 0 | 0 | 0 | 31.8497 | 0 | 0 | 0 | 0 | 0 | 47.1347
5068 | 62.5919 | 0 | 0 | 0 | 0 | 31.296 | 0 | 0 | 0 | 0 | 0 | 48.1674
5069 | 64.497 | 0 | 0 | 0 | 0 | 32.2485 | 0 | 0 | 0 | 0 | 0 | 48.9736
5070 | 79.6287 | 0 | 0 | 0 | 0 | 39.8143 | 0 | 0 | 0 | 0 | 0 | 69.7857
5071 | 113.175 | 0 | 42.9 | 0 | 56.3 | 56.5875 | 8.1 | 0 | 0 | 0 | 0 | 56.4386
5072 | 179.2917 | 0.7 | 43 | 0 | 37.6 | 89.6459 | 0.9 | 9 | 2.8 | 0 | 0 | 58.8645
5073 | 278.1279 | 2.1 | 43.2 | 0 | 0 | 139.0639 | 0 | 9.6 | 4 | 0 | 0 | 58.2864
5074 | 316.3692 | 3.5 | 43.4 | 0 | 0 | 158.1846 | 0 | 24.3 | 7.6 | 0 | 0 | 96.1054
5075 | 268.7914 | 3.5 | 43.4 | 0 | 0 | 134.3957 | 0 | 46.6 | 17.8 | 0 | 0 | 218.3892
5076 | 257.3869 | 2.8 | 43.3 | 0 | 0 | 128.6935 | 0 | 75.8 | 41 | 0 | 0 | 81.2539
5077 | 237.0858 | 1.4 | 43.1 | 0 | 75.1 | 118.5429 | 122.5 | 80.9 | 89 | 0 | 0 | 110.0589
5078 | 237.7626 | 2.1 | 43.2 | 0 | 37.6 | 118.8813 | 139.3 | 91.4 | 153 | 0 | 0 | 176.8266
5079 | 224.1787 | 3.5 | 43.4 | 0 | 0 | 112.0894 | 0 | 117.4 | 184.1 | 0 | 0 | 170.982
5080 | 203.2816 | 2.8 | 43.3 | 0 | 0 | 101.6408 | 0 | 116.4 | 192.4 | 0 | 0 | 112.122
5081 | 152.4214 | 2.1 | 43.2 | 0 | 0 | 76.2107 | 0 | 121.6 | 208.7 | 0 | 0 | 113.322
5082 | 122.3695 | 0.7 | 43 | 0 | 37.6 | 61.1847 | 322.3 | 97 | 210.9 | 0 | 0 | 267.7014
5083 | 96.6425 | 0 | 42.9 | 0 | 75.1 | 48.3213 | 353.5 | 2.1 | 130.8 | 0 | 0 | 327.4373
5084 | 82.3666 | 0 | 42.9 | 0 | 75.1 | 41.1833 | 303.6 | 0 | 82.5 | 0 | 0 | 169.9173
5085 | 72.8445 | 0 | 42.9 | 0 | 75.1 | 36.4222 | 232.5 | 0 | 62.4 | 0 | 0 | 187.4069
5086 | 70.9974 | 0 | 42.9 | 0 | 93.9 | 35.4987 | 203 | 0 | 43.4 | 0 | 0 | 120.8294
5087 | 70.8969 | 0 | 0 | 0 | 0 | 35.4485 | 0 | 0 | 0 | 0 | 0 | 127.9006
5088 | 69.1295 | 0 | 0 | 0 | 0 | 34.5647 | 0 | 0 | 0 | 0 | 0 | 99.833
5089 | 65.9267 | 0 | 0 | 0 | 0 | 32.9634 | 0 | 0 | 0 | 0 | 0 | 55.6327
5090 | 68.1231 | 0 | 0 | 0 | 0 | 34.0616 | 0 | 0 | 0 | 0 | 0 | 49.7788
5091 | 67.2247 | 0 | 0 | 0 | 0 | 33.6123 | 0 | 0 | 0 | 0 | 0 | 63.0034
5092 | 66.0333 | 0 | 0 | 0 | 0 | 33.0167 | 0 | 0 | 0 | 0 | 0 | 51.6157
5093 | 66.2013 | 0 | 0 | 0 | 0 | 33.1007 | 0 | 0 | 0 | 0 | 0 | 52.1919
5094 | 65.367 | 0 | 0 | 0 | 0 | 32.6835 | 0 | 0 | 0 | 0 | 0 | 64.8409
5095 | 89.8744 | 0 | 42.9 | 0 | 56.3 | 44.9372 | 0 | 0 | 0 | 0 | 0 | 80.5441
5096 | 105.546 | 0.7 | 43 | 0 | 37.6 | 52.773 | 0 | 15.1 | 0 | 0 | 0 | 92.0574
5097 | 104.1299 | 2.1 | 43.2 | 0 | 0 | 52.065 | 0 | 9 | 0 | 0 | 0 | 99.1058
5098 | 100.4524 | 3.5 | 43.4 | 0 | 0 | 50.2262 | 0 | 12.2 | 6.3 | 0 | 0 | 117.3682
5099 | 99.4383 | 3.5 | 43.4 | 0 | 0 | 49.7192 | 0 | 17 | 25.2 | 0 | 0 | 118.4509
5100 | 99.8989 | 2.8 | 43.3 | 0 | 0 | 49.9494 | 0 | 39.6 | 59.2 | 0 | 0 | 112.4837
5101 | 100.1651 | 1.4 | 43.1 | 0 | 75.1 | 50.0825 | 75.4 | 44.9 | 73.1 | 0 | 0 | 323.0219
5102 | 98.6238 | 2.1 | 43.2 | 0 | 37.6 | 49.3119 | 71.5 | 48.6 | 83.2 | 0 | 0 | 112.7243
5103 | 96.1051 | 3.5 | 43.4 | 0 | 0 | 48.0526 | 0 | 52.3 | 72 | 0 | 0 | 148.0401
5104 | 96.6726 | 2.8 | 43.3 | 0 | 0 | 48.3363 | 0 | 64.4 | 67.8 | 0 | 0 | 119.1079
5105 | 94.416 | 2.1 | 43.2 | 0 | 0 | 47.208 | 0 | 77.4 | 71.8 | 0 | 0 | 112.1211
5106 | 83.0273 | 0.7 | 43 | 0 | 37.6 | 41.5137 | 66.3 | 61.1 | 60.3 | 0 | 0 | 107.7678
5107 | 72.7487 | 0 | 42.9 | 0 | 75.1 | 36.3744 | 69.2 | 0 | 15.6 | 0 | 0 | 221.285
5108 | 69.9105 | 0 | 42.9 | 0 | 75.1 | 34.9552 | 24.9 | 0 | 0 | 0 | 0 | 163.3571
5109 | 68.2868 | 0 | 42.9 | 0 | 75.1 | 34.1434 | 3 | 0 | 0 | 0 | 0 | 156.5594
5110 | 67.3548 | 0 | 42.9 | 0 | 93.9 | 33.6774 | 0 | 0 | 0 | 0 | 0 | 193.143
5111 | 66.0823 | 0 | 0 | 0 | 0 | 33.0411 | 0 | 0 | 0 | 0 | 0 | 285.3164
5112 | 67.7094 | 0 | 0 | 0 | 0 | 33.8547 | 0 | 0 | 0 | 0 | 0 | 110.2988
5113 | 65.6803 | 0 | 0 | 0 | 0 | 32.8402 | 0 | 0 | 0 | 0 | 0 | 57.2451
5114 | 63.5822 | 0 | 0 | 0 | 0 | 31.7911 | 0 | 0 | 0 | 0 | 0 | 45.9941
5115 | 64.8107 | 0 | 0 | 0 | 0 | 32.4053 | 0 | 0 | 0 | 0 | 0 | 46.5638
5116 | 63.4551 | 0 | 0 | 0 | 0 | 31.7275 | 0 | 0 | 0 | 0 | 0 | 46.4484
5117 | 62.2061 | 0 | 0 | 0 | 0 | 31.103 | 0 | 0 | 0 | 0 | 0 | 54.5986
5118 | 79.0749 | 0 | 0 | 0 | 0 | 39.5374 | 0 | 0 | 0 | 0 | 0 | 78.0452
5119 | 123.0681 | 0 | 42.9 | 0 | 56.3 | 61.534 | 0 | 0 | 0 | 0 | 0 | 54.1411
5120 | 169.5946 | 0.7 | 43 | 0 | 37.6 | 84.7973 | 0 | 7.9 | 0 | 0 | 0 | 86.4651
5121 | 239.7117 | 2.1 | 43.2 | 0 | 0 | 119.8559 | 0 | 15 | 0 | 0 | 0 | 113.324
5122 | 282.825 | 3.5 | 43.4 | 0 | 0 | 141.4125 | 0 | 37.2 | 0 | 0 | 0 | 86.9348
5123 | 276.0942 | 3.5 | 43.4 | 0 | 0 | 138.0471 | 0 | 55.2 | 0 | 0 | 0 | 104.2519
5124 | 257.615 | 2.8 | 43.3 | 0 | 0 | 128.8075 | 0 | 67.4 | 0 | 0 | 0 | 77.9235
5125 | 251.8037 | 1.4 | 43.1 | 0 | 75.1 | 125.9018 | 0 | 63.7 | 21.6 | 0 | 0 | 175.5573
5126 | 250.4673 | 2.1 | 43.2 | 0 | 37.6 | 125.2336 | 0 | 67.1 | 48.5 | 0 | 0 | 71.6259
5127 | 238.0812 | 3.5 | 43.4 | 0 | 0 | 119.0406 | 0 | 79.2 | 63.8 | 0 | 0 | 120.6385
5128 | 215.6872 | 2.8 | 43.3 | 0 | 0 | 107.8436 | 0 | 77.8 | 83.8 | 0 | 0 | 111.3875
5129 | 166.1622 | 2.1 | 43.2 | 0 | 0 | 83.0811 | 0 | 76 | 78.4 | 0 | 0 | 184.3667
5130 | 132.384 | 0.7 | 43 | 0 | 37.6 | 66.192 | 6.4 | 59.9 | 52.4 | 0 | 0 | 125.6226
5131 | 98.101 | 0 | 42.9 | 0 | 75.1 | 49.0505 | 9.1 | 0 | 6.6 | 0 | 0 | 100.43
5132 | 82.4744 | 0 | 42.9 | 0 | 75.1 | 41.2372 | 0.3 | 0 | 0 | 0 | 0 | 169.0507
5133 | 72.6492 | 0 | 42.9 | 0 | 75.1 | 36.3246 | 0 | 0 | 0 | 0 | 0 | 223.7685
5134 | 73.4544 | 0 | 42.9 | 0 | 93.9 | 36.7272 | 0 | 0 | 0 | 0 | 0 | 178.2098
5135 | 70.2774 | 0 | 0 | 0 | 0 | 35.1387 | 0 | 0 | 0 | 0 | 0 | 141.9858
5136 | 66.2373 | 0 | 0 | 0 | 0 | 33.1186 | 0 | 0 | 0 | 0 | 0 | 100.4284
5137 | 66.5044 | 0 | 0 | 0 | 0 | 33.2522 | 0 | 0 | 0 | 0 | 0 | 67.7141
5138 | 65.3989 | 0 | 0 | 0 | 0 | 32.6995 | 0 | 0 | 0 | 0 | 0 | 61.624
5139 | 66.3454 | 0 | 0 | 0 | 0 | 33.1727 | 0 | 0 | 0 | 0 | 0 | 50.0076
5140 | 64.1267 | 0 | 0 | 0 | 0 | 32.0633 | 0 | 0 | 0 | 0 | 0 | 53.5675
5141 | 65.0698 | 0 | 0 | 0 | 0 | 32.5349 | 0 | 0 | 0 | 0 | 0 | 61.6233
5142 | 84.4046 | 0 | 0 | 0 | 0 | 42.2023 | 0 | 0 | 0 | 0 | 0 | 70.7066
5143 | 121.3374 | 0 | 42.9 | 0 | 56.3 | 60.6687 | 0 | 0 | 0 | 0 | 0 | 119.53
5144 | 194.9484 | 0.7 | 43 | 0 | 37.6 | 97.4742 | 0 | 0 | 0 | 0 | 0 | 49.2044
5145 | 281.2367 | 2.1 | 43.2 | 0 | 0 | 140.6183 | 0 | 0 | 0 | 0 | 0 | 84.6843
5146 | 313.1265 | 3.5 | 43.4 | 0 | 0 | 156.5632 | 0 | 0 | 0 | 0 | 0 | 75.0915
5147 | 290.3115 | 3.5 | 43.4 | 0 | 0 | 145.1558 | 0 | 0 | 0 | 0 | 0 | 182.7063
5148 | 278.0231 | 2.8 | 43.3 | 0 | 0 | 139.0116 | 0 | 0 | 0 | 0 | 0 | 253.017
5149 | 270.6197 | 1.4 | 43.1 | 0 | 75.1 | 135.3098 | 0 | 0 | 0 | 0 | 0 | 156.2518
5150 | 281.4087 | 2.1 | 43.2 | 0 | 37.6 | 140.7044 | 0 | 0 | 0 | 0 | 0 | 170.2678
5151 | 265.0897 | 3.5 | 43.4 | 0 | 0 | 132.5449 | 0 | 1.1 | 0 | 0 | 0 | 88.7203
5152 | 234.9851 | 2.8 | 43.3 | 0 | 0 | 117.4926 | 0 | 1.5 | 4.6 | 0 | 0 | 155.4318
5153 | 179.4055 | 2.1 | 43.2 | 0 | 0 | 89.7027 | 0 | 8.5 | 12.5 | 0 | 0 | 95.3936
5154 | 137.1621 | 0.7 | 43 | 0 | 37.6 | 68.581 | 0 | 7.8 | 31.1 | 0 | 0 | 74.6251
5155 | 109.7643 | 0 | 42.9 | 0 | 75.1 | 54.8822 | 0 | 0 | 7.9 | 0 | 0 | 205.1701
5156 | 93.8938 | 0 | 42.9 | 0 | 75.1 | 46.9469 | 0 | 0 | 0 | 0 | 0 | 339.325
5157 | 74.7108 | 0 | 42.9 | 0 | 75.1 | 37.3554 | 0 | 0 | 0 | 0 | 0 | 258.2327
5158 | 73.3751 | 0 | 42.9 | 0 | 93.9 | 36.6875 | 0 | 0 | 0 | 0 | 0 | 220.1158
5159 | 72.6043 | 0 | 0 | 0 | 0 | 36.3022 | 0 | 0 | 0 | 0 | 0 | 167.5777
5160 | 70.9561 | 0 | 0 | 0 | 0 | 35.4781 | 0 | 0 | 0 | 0 | 0 | 194.1499
5161 | 70.1816 | 0 | 0 | 0 | 0 | 35.0908 | 0 | 0 | 0 | 0 | 0 | 67.6004
5162 | 69.8327 | 0 | 0 | 0 | 0 | 34.9163 | 0 | 0 | 0 | 0 | 0 | 62.7751
5163 | 68.3416 | 0 | 0 | 0 | 0 | 34.1708 | 0 | 0 | 0 | 0 | 0 | 59.4374
5164 | 66.7691 | 0 | 0 | 0 | 0 | 33.3845 | 0 | 0 | 0 | 0 | 0 | 51.844
5165 | 70.4922 | 0 | 0 | 0 | 0 | 35.2461 | 0 | 0 | 0 | 0 | 0 | 50.4675
5166 | 72.269 | 0 | 0 | 0 | 0 | 36.1345 | 0 | 0 | 0 | 0 | 0 | 67.9428
5167 | 88.4091 | 0 | 42.9 | 0 | 56.3 | 44.2046 | 0 | 0 | 0 | 0 | 0 | 84.5653
5168 | 88.5464 | 0 | 42.9 | 0 | 37.6 | 44.2732 | 0 | 0 | 0 | 0 | 0 | 55.4032
5169 | 88.5858 | 0 | 42.9 | 0 | 0 | 44.2929 | 0 | 0 | 0 | 0 | 0 | 80.4258
5170 | 93.5665 | 0 | 42.9 | 0 | 0 | 46.7833 | 0 | 0 | 0 | 0 | 0 | 55.0584
5171 | 95.0281 | 0 | 42.9 | 0 | 0 | 47.5141 | 0 | 0 | 0 | 0 | 0 | 54.7133
5172 | 93.1974 | 0 | 42.9 | 0 | 0 | 46.5987 | 0 | 0 | 0 | 0 | 0 | 172.8639
5173 | 95.9669 | 0 | 42.9 | 0 | 75.1 | 47.9834 | 0 | 0 | 0 | 0 | 0 | 126.6817
5174 | 95.0439 | 0 | 42.9 | 0 | 37.6 | 47.522 | 0 | 0 | 0 | 0 | 0 | 176.2953
5175 | 93.1202 | 0 | 42.9 | 0 | 0 | 46.5601 | 0 | 0 | 0 | 0 | 0 | 161.6396
5176 | 96.7324 | 0 | 42.9 | 0 | 0 | 48.3662 | 0 | 0 | 1 | 0 | 0 | 136.0611
5177 | 94.6916 | 0 | 42.9 | 0 | 0 | 47.3458 | 0 | 0 | 2.4 | 0 | 0 | 137.5526
5178 | 94.4269 | 0 | 42.9 | 0 | 37.6 | 47.2134 | 0 | 0 | 0.2 | 0 | 0 | 189.6109
5179 | 97.6891 | 0 | 42.9 | 0 | 75.1 | 48.8446 | 0 | 0 | 0 | 0 | 0 | 143.4508
5180 | 87.5782 | 0 | 42.9 | 0 | 75.1 | 43.7891 | 0 | 0 | 0 | 0 | 0 | 200.411
5181 | 72.6393 | 0 | 42.9 | 0 | 75.1 | 36.3197 | 0 | 0 | 0 | 0 | 0 | 137.3455
5182 | 70.0072 | 0 | 42.9 | 0 | 93.9 | 35.0036 | 0 | 0 | 0 | 0 | 0 | 125.1126
5183 | 66.2903 | 0 | 0 | 0 | 0 | 33.1451 | 0 | 0 | 0 | 0 | 0 | 142.8631
5184 | 69.6312 | 0 | 0 | 0 | 0 | 34.8156 | 0 | 0 | 0 | 0 | 0 | 86.9372
5185 | 66.5503 | 0 | 0 | 0 | 0 | 33.2751 | 0 | 0 | 0 | 0 | 0 | 61.9697
5186 | 67.8678 | 0 | 0 | 0 | 0 | 33.9339 | 0 | 0 | 0 | 0 | 0 | 55.6353
5187 | 66.0922 | 0 | 0 | 0 | 0 | 33.0461 | 0 | 0 | 0 | 0 | 0 | 52.3065
5188 | 65.3394 | 0 | 0 | 0 | 0 | 32.6697 | 0 | 0 | 0 | 0 | 0 | 53.1071
5189 | 63.0447 | 0 | 0 | 0 | 0 | 31.5224 | 0 | 0 | 0 | 0 | 0 | 51.2708
5190 | 68.3546 | 0 | 0 | 0 | 0 | 34.1773 | 0 | 0 | 0 | 0 | 0 | 64.2651
5191 | 86.037 | 0 | 42.9 | 0 | 56.3 | 43.0185 | 0 | 0 | 0 | 0 | 0 | 56.7829
5192 | 96.1231 | 0 | 42.9 | 0 | 37.6 | 48.0615 | 0 | 0 | 0 | 0 | 0 | 57.8238
5193 | 95.7189 | 0 | 42.9 | 0 | 0 | 47.8595 | 0 | 0 | 0 | 0 | 0 | 48.7436
5194 | 93.8699 | 0 | 42.9 | 0 | 0 | 46.935 | 0 | 0 | 0 | 0 | 0 | 57.4779
5195 | 91.2936 | 0 | 42.9 | 0 | 0 | 45.6468 | 0 | 0 | 0 | 0 | 0 | 66.564
5196 | 92.9619 | 0 | 42.9 | 0 | 0 | 46.4809 | 0 | 0 | 0 | 0 | 0 | 188.8396
5197 | 92.2258 | 0 | 42.9 | 0 | 75.1 | 46.1129 | 0 | 0 | 0 | 0 | 0 | 211.295
5198 | 95.0244 | 0 | 42.9 | 0 | 37.6 | 47.5122 | 0 | 0 | 0 | 0 | 0 | 81.0166
5199 | 94.2468 | 0 | 42.9 | 0 | 0 | 47.1234 | 0 | 0 | 0 | 0 | 0 | 64.4939
5200 | 94.0382 | 0 | 42.9 | 0 | 0 | 47.0191 | 0 | 0 | 0 | 0 | 0 | 107.1495
5201 | 94.3017 | 0 | 42.9 | 0 | 0 | 47.1508 | 0 | 0 | 3.3 | 0 | 0 | 95.7519
5202 | 91.4138 | 0 | 42.9 | 0 | 37.6 | 45.7069 | 0 | 0 | 11.4 | 0 | 0 | 127.4399
5203 | 83.0577 | 0 | 42.9 | 0 | 75.1 | 41.5288 | 0 | 0 | 16.4 | 0 | 0 | 132.9512
5204 | 79.7539 | 0 | 42.9 | 0 | 75.1 | 39.877 | 0 | 0 | 0 | 0 | 0 | 170.3481
5205 | 77.6235 | 0 | 42.9 | 0 | 75.1 | 38.8117 | 0 | 0 | 0 | 0 | 0 | 198.2486
5206 | 72.7044 | 0 | 42.9 | 0 | 93.9 | 36.3522 | 0 | 0 | 0 | 0 | 0 | 169.4523
5207 | 72.4162 | 0 | 0 | 0 | 0 | 36.2081 | 0 | 0 | 0 | 0 | 0 | 123.2256
5208 | 71.9299 | 0 | 0 | 0 | 0 | 35.965 | 0 | 0 | 0 | 0 | 0 | 77.2101
5209 | 70.6509 | 0 | 0 | 0 | 0 | 35.3254 | 0 | 0 | 0 | 0 | 0 | 49.8935
5210 | 70.4469 | 0 | 0 | 0 | 0 | 35.2235 | 0 | 0 | 0 | 0 | 0 | 49.435
5211 | 66.3157 | 0 | 0 | 0 | 0 | 33.1578 | 0 | 0 | 0 | 0 | 0 | 48.6298
5212 | 66.735 | 0 | 0 | 0 | 0 | 33.3675 | 0 | 0 | 0 | 0 | 0 | 46.792
5213 | 64.943 | 0 | 0 | 0 | 0 | 32.4715 | 0 | 0 | 0 | 0 | 0 | 60.0119
5214 | 87.0864 | 0 | 0 | 0 | 0 | 43.5432 | 0 | 0 | 0 | 0 | 0 | 77.2059
5215 | 126.4363 | 0 | 42.9 | 0 | 56.3 | 63.2181 | 0 | 0 | 0 | 0 | 0 | 48.2857
5216 | 186.5089 | 0.7 | 43 | 0 | 37.6 | 93.2544 | 0 | 0 | 0 | 0 | 0 | 52.5358
5217 | 267.6119 | 2.1 | 43.2 | 0 | 0 | 133.8059 | 0 | 0 | 0 | 0 | 0 | 123.8188
5218 | 295.7147 | 3.5 | 43.4 | 0 | 0 | 147.8574 | 0 | 0 | 0 | 0 | 0 | 141.3717
5219 | 273.9266 | 3.5 | 43.4 | 0 | 0 | 136.9633 | 0 | 0 | 8.2 | 0 | 0 | 68.864
5220 | 264.9952 | 2.8 | 43.3 | 0 | 0 | 132.4976 | 0 | 0 | 42.4 | 0 | 0 | 80.6599
5221 | 249.3348 | 1.4 | 43.1 | 0 | 75.1 | 124.6674 | 0 | 0 | 84.6 | 0 | 0 | 70.244
5222 | 253.0288 | 2.1 | 43.2 | 0 | 37.6 | 126.5144 | 0 | 0 | 119.5 | 0 | 0 | 132.3676
5223 | 235.4487 | 3.5 | 43.4 | 0 | 0 | 117.7244 | 0 | 0 | 133.7 | 0 | 0 | 83.1489
5224 | 210.8505 | 2.8 | 43.3 | 0 | 0 | 105.4253 | 0 | 0 | 152.7 | 0 | 0 | 67.3698
5225 | 157.391 | 2.1 | 43.2 | 0 | 0 | 78.6955 | 0 | 0 | 173.7 | 0 | 0 | 103.0615
5226 | 125.9841 | 0.7 | 43 | 0 | 37.6 | 62.9921 | 58.4 | 0 | 180 | 0 | 0 | 131.9697
5227 | 99.9649 | 0 | 42.9 | 0 | 75.1 | 49.9824 | 71.4 | 0 | 101.2 | 0 | 0 | 193.1135
5228 | 82.7354 | 0 | 42.9 | 0 | 75.1 | 41.3677 | 17.3 | 0 | 20.6 | 0 | 0 | 161.8224
5229 | 71.92 | 0 | 42.9 | 0 | 75.1 | 35.96 | 0.8 | 0 | 2.4 | 0 | 0 | 179.7911
5230 | 68.2003 | 0 | 42.9 | 0 | 93.9 | 34.1002 | 0 | 0 | 0 | 0 | 0 | 231.3267
5231 | 68.9655 | 0 | 0 | 0 | 0 | 34.4828 | 0 | 0 | 0 | 0 | 0 | 245.2528
5232 | 69.4688 | 0 | 0 | 0 | 0 | 34.7344 | 0 | 0 | 0 | 0 | 0 | 76.8524
5233 | 67.8575 | 0 | 0 | 0 | 0 | 33.9288 | 0 | 0 | 0 | 0 | 0 | 50.8108
5234 | 69.0111 | 0 | 0 | 0 | 0 | 34.5055 | 0 | 0 | 0 | 0 | 0 | 56.3198
5235 | 66.0113 | 0 | 0 | 0 | 0 | 33.0057 | 0 | 0 | 0 | 0 | 0 | 46.4489
5236 | 65.3351 | 0 | 0 | 0 | 0 | 32.6675 | 0 | 0 | 0 | 0 | 0 | 48.7456
5237 | 64.948 | 0 | 0 | 0 | 0 | 32.474 | 0 | 0 | 0 | 0 | 0 | 48.3994
5238 | 77.3845 | 0 | 0 | 0 | 0 | 38.6923 | 0 | 0 | 0 | 0 | 0 | 72.7786
5239 | 109.9193 | 0 | 42.9 | 0 | 56.3 | 54.9596 | 0 | 0 | 0 | 0 | 0 | 51.2703
5240 | 169.1452 | 0.7 | 43 | 0 | 37.6 | 84.5726 | 0 | 0 | 0 | 0 | 0 | 121.2461
5241 | 251.5523 | 2.1 | 43.2 | 0 | 0 | 125.7762 | 0 | 0 | 0 | 0 | 0 | 86.1056
5242 | 326.7373 | 3.5 | 43.4 | 0 | 0 | 163.3687 | 0 | 0 | 0.5 | 0 | 0 | 153.4076
5243 | 325.6024 | 3.5 | 43.4 | 0 | 0 | 162.8012 | 0 | 0 | 11.1 | 0 | 0 | 163.7712
5244 | 266.4249 | 2.8 | 43.3 | 0 | 0 | 133.2124 | 0 | 0 | 39.1 | 0 | 0 | 141.6035
5245 | 260.9129 | 1.4 | 43.1 | 0 | 75.1 | 130.4565 | 1 | 0 | 76.3 | 0 | 0 | 230.24
5246 | 259.3075 | 2.1 | 43.2 | 0 | 37.6 | 129.6538 | 7.8 | 0.9 | 105.2 | 0 | 0 | 69.3234
5247 | 230.7602 | 3.5 | 43.4 | 0 | 0 | 115.3801 | 0 | 9 | 122.2 | 0 | 0 | 109.4484
5248 | 206.1028 | 2.8 | 43.3 | 0 | 0 | 103.0514 | 0 | 18.9 | 142.9 | 0 | 0 | 105.2213
5249 | 152.666 | 2.1 | 43.2 | 0 | 0 | 76.333 | 0 | 36.9 | 163.8 | 0 | 0 | 141.7972
5250 | 110.9445 | 0.7 | 43 | 0 | 37.6 | 55.4723 | 117.2 | 40.3 | 170.3 | 0 | 0 | 201.9556
5251 | 90.3985 | 0 | 42.9 | 0 | 75.1 | 45.1993 | 120.1 | 0 | 93.2 | 0 | 0 | 287.0916
5252 | 73.7929 | 0 | 42.9 | 0 | 75.1 | 36.8964 | 41.9 | 0 | 18.5 | 0 | 0 | 195.8855
5253 | 72.8699 | 0 | 42.9 | 0 | 75.1 | 36.435 | 9.4 | 0 | 2.3 | 0 | 0 | 207.589
5254 | 69.3799 | 0 | 42.9 | 0 | 93.9 | 34.6899 | 0.7 | 0 | 0 | 0 | 0 | 173.2531
5255 | 67.1137 | 0 | 0 | 0 | 0 | 33.5569 | 0 | 0 | 0 | 0 | 0 | 106.0624
5256 | 67.1791 | 0 | 0 | 0 | 0 | 33.5896 | 0 | 0 | 0 | 0 | 0 | 83.1456
5257 | 64.5584 | 0 | 0 | 0 | 0 | 32.2792 | 0 | 0 | 0 | 0 | 0 | 63.465
5258 | 66.9104 | 0 | 0 | 0 | 0 | 33.4552 | 0 | 0 | 0 | 0 | 0 | 47.9388
5259 | 65.6196 | 0 | 0 | 0 | 0 | 32.8098 | 0 | 0 | 0 | 0 | 0 | 51.0405
5260 | 63.293 | 0 | 0 | 0 | 0 | 31.6465 | 0 | 0 | 0 | 0 | 0 | 49.0882
5261 | 68.0097 | 0 | 0 | 0 | 0 | 34.0049 | 0 | 0 | 0 | 0 | 0 | 49.2054
5262 | 77.162 | 0 | 0 | 0 | 0 | 38.581 | 0 | 0 | 0 | 0 | 0 | 65.6396
5263 | 114.2117 | 0 | 42.9 | 0 | 56.3 | 57.1059 | 0 | 0 | 0 | 0 | 0 | 58.9797
5264 | 171.5867 | 0.7 | 43 | 0 | 37.6 | 85.7934 | 0 | 0 | 0 | 0 | 0 | 79.9512
5265 | 278.0516 | 2.1 | 43.2 | 0 | 0 | 139.0258 | 0 | 0 | 1 | 0 | 0 | 92.5313
5266 | 316.1529 | 3.5 | 43.4 | 0 | 0 | 158.0764 | 0 | 0 | 13.3 | 0 | 0 | 108.6045
5267 | 309.6185 | 3.5 | 43.4 | 0 | 0 | 154.8092 | 0 | 1 | 43.9 | 0 | 0 | 150.821
5268 | 304.3907 | 2.8 | 43.3 | 0 | 0 | 152.1953 | 0 | 17.2 | 89.4 | 0 | 0 | 173.2621
5269 | 282.1606 | 1.4 | 43.1 | 0 | 75.1 | 141.0803 | 74.4 | 23.5 | 137.3 | 0 | 0 | 372.7734
5270 | 269.9307 | 2.1 | 43.2 | 0 | 37.6 | 134.9654 | 105.1 | 29.3 | 171.4 | 0 | 0 | 187.7548
5271 | 265.8887 | 3.5 | 43.4 | 0 | 0 | 132.9444 | 0 | 46.4 | 197.2 | 0 | 0 | 134.1188
5272 | 239.7278 | 2.8 | 43.3 | 0 | 0 | 119.8639 | 0 | 54.1 | 219.4 | 0 | 0 | 191.8717
5273 | 190.4703 | 2.1 | 43.2 | 0 | 0 | 95.2352 | 0 | 60.2 | 237.1 | 0 | 0 | 144.5461
5274 | 165.7518 | 0.7 | 43 | 0 | 37.6 | 82.8759 | 306.5 | 50 | 241.4 | 0 | 0 | 331.5404
5275 | 141.0786 | 0 | 42.9 | 0 | 75.1 | 70.5393 | 305.7 | 0 | 154.5 | 0 | 0 | 182.3212
5276 | 95.1037 | 0 | 42.9 | 0 | 75.1 | 47.5519 | 190.9 | 0 | 59.4 | 0 | 0 | 253.0458
5277 | 66.497 | 0 | 42.9 | 0 | 75.1 | 33.2485 | 99.5 | 0 | 36.2 | 0 | 0 | 324.7078
5278 | 65.5666 | 0 | 42.9 | 0 | 93.9 | 32.7833 | 51.7 | 0 | 15.2 | 0 | 0 | 191.184
5279 | 64.6678 | 0 | 0 | 0 | 0 | 32.3339 | 0 | 0 | 0 | 0 | 0 | 169.6803
5280 | 63.0395 | 0 | 0 | 0 | 0 | 31.5197 | 0 | 0 | 0 | 0 | 0 | 144.783
5281 | 64.6353 | 0 | 0 | 0 | 0 | 32.3176 | 0 | 0 | 0 | 0 | 0 | 76.0291
5282 | 61.2711 | 0 | 0 | 0 | 0 | 30.6355 | 0 | 0 | 0 | 0 | 0 | 75.2063
5283 | 62.9828 | 0 | 0 | 0 | 0 | 31.4914 | 0 | 0 | 0 | 0 | 0 | 120.4963
5284 | 60.5189 | 0 | 0 | 0 | 0 | 30.2594 | 0 | 0 | 0 | 0 | 0 | 94.0851
5285 | 62.8557 | 0 | 0 | 0 | 0 | 31.4278 | 0 | 0 | 0 | 0 | 0 | 61.6236
5286 | 75.8334 | 0 | 0 | 0 | 0 | 37.9167 | 0 | 0 | 0 | 0 | 0 | 72.0879
5287 | 101.5551 | 0 | 42.9 | 0 | 56.3 | 50.7775 | 0 | 0 | 0 | 0 | 0 | 60.9326
5288 | 156.0224 | 0.7 | 43 | 0 | 37.6 | 78.0112 | 0 | 0 | 0 | 0 | 0 | 93.7241
5289 | 219.1729 | 2.1 | 43.2 | 0 | 0 | 109.5864 | 0 | 0 | 5.8 | 0 | 0 | 146.5443
5290 | 284.5643 | 3.5 | 43.4 | 0 | 0 | 142.2822 | 0 | 0 | 22.9 | 0 | 0 | 115.256
5291 | 262.774 | 3.5 | 43.4 | 0 | 0 | 131.387 | 0 | 3.1 | 53.8 | 0 | 0 | 192.7012
5292 | 240.961 | 2.8 | 43.3 | 0 | 0 | 120.4805 | 0 | 22.8 | 86.4 | 0 | 0 | 133.38
5293 | 224.5599 | 1.4 | 43.1 | 0 | 75.1 | 112.28 | 87.6 | 33.4 | 127.2 | 0 | 0 | 113.5598
5294 | 220.3614 | 2.1 | 43.2 | 0 | 37.6 | 110.1807 | 112.3 | 40.2 | 155.2 | 0 | 0 | 238.2229
5295 | 218.8031 | 3.5 | 43.4 | 0 | 0 | 109.4016 | 0 | 54.8 | 168.4 | 0 | 0 | 98.3936
5296 | 194.4193 | 2.8 | 43.3 | 0 | 0 | 97.2097 | 0 | 62.9 | 193.1 | 0 | 0 | 100.4253
5297 | 151.4244 | 2.1 | 43.2 | 0 | 0 | 75.7122 | 0 | 69.7 | 214.1 | 0 | 0 | 150.0588
5298 | 119.0096 | 0.7 | 43 | 0 | 37.6 | 59.5048 | 278.5 | 60.2 | 219.3 | 0 | 0 | 90.6225
5299 | 99.9739 | 0 | 42.9 | 0 | 75.1 | 49.9869 | 274.6 | 0 | 132.8 | 0 | 0 | 111.1436
5300 | 81.4597 | 0 | 42.9 | 0 | 75.1 | 40.7299 | 155.8 | 0 | 43.4 | 0 | 0 | 298.9716
5301 | 64.2953 | 0 | 42.9 | 0 | 75.1 | 32.1476 | 66.9 | 0 | 21.7 | 0 | 0 | 148.6311
5302 | 62.958 | 0 | 42.9 | 0 | 93.9 | 31.479 | 26.8 | 0 | 5.1 | 0 | 0 | 243.6703
5303 | 62.2111 | 0 | 0 | 0 | 0 | 31.1055 | 0 | 0 | 0 | 0 | 0 | 218.4052
5304 | 63.2171 | 0 | 0 | 0 | 0 | 31.6085 | 0 | 0 | 0 | 0 | 0 | 137.5733
5305 | 62.8324 | 0 | 0 | 0 | 0 | 31.4162 | 0 | 0 | 0 | 0 | 0 | 74.3934
5306 | 61.2658 | 0 | 0 | 0 | 0 | 30.6329 | 0 | 0 | 0 | 0 | 0 | 66.7946
5307 | 61.9644 | 0 | 0 | 0 | 0 | 30.9822 | 0 | 0 | 0 | 0 | 0 | 63.4646
5308 | 60.1708 | 0 | 0 | 0 | 0 | 30.0854 | 0 | 0 | 0 | 0 | 0 | 64.8391
5309 | 60.1361 | 0 | 0 | 0 | 0 | 30.0681 | 0 | 0 | 0 | 0 | 0 | 66.2166
5310 | 81.2586 | 0 | 0 | 0 | 0 | 40.6293 | 0 | 0 | 0 | 0 | 0 | 72.4334
5311 | 120.704 | 0 | 42.9 | 0 | 56.3 | 60.352 | 0 | 0 | 0 | 0 | 0 | 67.3713
5312 | 173.9849 | 0.7 | 43 | 0 | 37.6 | 86.9925 | 0 | 0 | 9.7 | 0 | 0 | 48.4002
5313 | 207.8895 | 2.1 | 43.2 | 0 | 0 | 103.9448 | 0 | 0 | 51.3 | 0 | 0 | 45.4281
5314 | 256.2182 | 3.5 | 43.4 | 0 | 0 | 128.1091 | 0 | 3.6 | 108.5 | 0 | 0 | 45.2021
5315 | 264.3183 | 3.5 | 43.4 | 0 | 0 | 132.1592 | 0 | 18 | 173.1 | 0 | 0 | 50.5806
5316 | 251.8787 | 2.8 | 43.3 | 0 | 0 | 125.9393 | 0 | 49.2 | 191.2 | 0 | 0 | 150.0077
5317 | 239.3237 | 1.4 | 43.1 | 0 | 75.1 | 119.6619 | 277.3 | 59.9 | 206 | 0 | 0 | 220.2006
5318 | 236.5552 | 2.1 | 43.2 | 0 | 37.6 | 118.2776 | 242 | 70.4 | 216.3 | 0 | 0 | 177.9144
5319 | 239.8834 | 3.5 | 43.4 | 0 | 0 | 119.9417 | 0 | 95.3 | 221.2 | 0 | 0 | 71.3938
5320 | 216.2339 | 2.8 | 43.3 | 0 | 0 | 108.1169 | 0 | 107.5 | 223.4 | 0 | 0 | 75.0902
5321 | 163.4138 | 2.1 | 43.2 | 0 | 0 | 81.7069 | 0 | 117.4 | 217.6 | 0 | 0 | 90.1409
5322 | 119.1708 | 0.7 | 43 | 0 | 37.6 | 59.5854 | 306.8 | 99.1 | 194.6 | 0 | 0 | 79.1191
5323 | 101.4088 | 0 | 42.9 | 0 | 75.1 | 50.7044 | 284.9 | 6 | 97.2 | 0 | 0 | 229.1212
5324 | 80.5876 | 0 | 42.9 | 0 | 75.1 | 40.2938 | 175 | 0 | 32.2 | 0 | 0 | 191.6631
5325 | 61.0337 | 0 | 42.9 | 0 | 75.1 | 30.5168 | 96.2 | 0 | 18 | 0 | 0 | 176.7273
5326 | 60.8821 | 0 | 42.9 | 0 | 93.9 | 30.4411 | 58.9 | 0 | 8.1 | 0 | 0 | 154.1419
5327 | 60.7092 | 0 | 0 | 0 | 0 | 30.3546 | 0 | 0 | 0 | 0 | 0 | 114.0425
5328 | 58.4501 | 0 | 0 | 0 | 0 | 29.2251 | 0 | 0 | 0 | 0 | 0 | 84.3263
5329 | 57.8201 | 0 | 0 | 0 | 0 | 28.91 | 0 | 0 | 0 | 0 | 0 | 52.5355
5330 | 60.2108 | 0 | 0 | 0 | 0 | 30.1054 | 0 | 0 | 0 | 0 | 0 | 48.8589
5331 | 59.1825 | 0 | 0 | 0 | 0 | 29.5912 | 0 | 0 | 0 | 0 | 0 | 47.7119
5332 | 57.8861 | 0 | 0 | 0 | 0 | 28.943 | 0 | 0 | 0 | 0 | 0 | 49.6617
5333 | 60.0865 | 0 | 0 | 0 | 0 | 30.0433 | 0 | 0 | 0 | 0 | 0 | 55.4026
5334 | 57.6434 | 0 | 0 | 0 | 0 | 28.8217 | 0 | 0 | 0 | 0 | 0 | 60.2428
5335 | 69.8249 | 0 | 42.9 | 0 | 56.3 | 34.9125 | 1.4 | 0 | 0 | 0 | 0 | 53.9114
5336 | 82.0619 | 0 | 42.9 | 0 | 37.6 | 41.0309 | 12.8 | 0 | 15.9 | 0 | 0 | 48.7453
5337 | 79.399 | 0 | 42.9 | 0 | 0 | 39.6995 | 0 | 0 | 71.6 | 0 | 0 | 51.7292
5338 | 77.9288 | 0 | 42.9 | 0 | 0 | 38.9644 | 0 | 0 | 157.6 | 0 | 0 | 98.7557
5339 | 79.951 | 0 | 42.9 | 0 | 0 | 39.9755 | 0 | 0 | 193.3 | 0 | 0 | 80.8977
5340 | 75.349 | 0 | 42.9 | 0 | 0 | 37.6745 | 0 | 0 | 194.2 | 0 | 0 | 57.8222
5341 | 76.5822 | 0 | 42.9 | 0 | 75.1 | 38.2911 | 401.2 | 0 | 211.5 | 0 | 0 | 74.9741
5342 | 79.3042 | 0 | 42.9 | 0 | 37.6 | 39.6521 | 339.7 | 0 | 223.7 | 0 | 0 | 128.1092
5343 | 78.3462 | 0 | 42.9 | 0 | 0 | 39.1731 | 0 | 0 | 203.3 | 0 | 0 | 93.7248
5344 | 78.4829 | 0 | 42.9 | 0 | 0 | 39.2415 | 0 | 0 | 188.3 | 0 | 0 | 68.862
5345 | 76.6705 | 0 | 42.9 | 0 | 0 | 38.3352 | 0 | 0 | 166 | 0 | 0 | 70.8207
5346 | 75.7906 | 0 | 42.9 | 0 | 37.6 | 37.8953 | 320 | 0 | 149 | 0 | 0 | 136.124
5347 | 72.1465 | 0 | 42.9 | 0 | 75.1 | 36.0733 | 348.8 | 0 | 118.8 | 0 | 0 | 119.0941
5348 | 68.7259 | 0 | 42.9 | 0 | 75.1 | 34.363 | 236.3 | 0 | 38.1 | 0 | 0 | 135.5073
5349 | 61.6383 | 0 | 42.9 | 0 | 75.1 | 30.8192 | 133.1 | 0 | 20.9 | 0 | 0 | 162.59
5350 | 62.6567 | 0 | 42.9 | 0 | 93.9 | 31.3284 | 84.7 | 0 | 9.8 | 0 | 0 | 133.2618
5351 | 60.2576 | 0 | 0 | 0 | 0 | 30.1288 | 0 | 0 | 0 | 0 | 0 | 151.5214
5352 | 60.2604 | 0 | 0 | 0 | 0 | 30.1302 | 0 | 0 | 0 | 0 | 0 | 76.4976
5353 | 60.6726 | 0 | 0 | 0 | 0 | 30.3363 | 0 | 0 | 0 | 0 | 0 | 71.6267
5354 | 59.6108 | 0 | 0 | 0 | 0 | 29.8054 | 0 | 0 | 0 | 0 | 0 | 54.9438
5355 | 58.7021 | 0 | 0 | 0 | 0 | 29.3511 | 0 | 0 | 0 | 0 | 0 | 47.3645
5356 | 55.8893 | 0 | 0 | 0 | 0 | 27.9446 | 0 | 0 | 0 | 0 | 0 | 48.9746
5357 | 58.2896 | 0 | 0 | 0 | 0 | 29.1448 | 0 | 0 | 0 | 0 | 0 | 49.8925
5358 | 62.2817 | 0 | 0 | 0 | 0 | 31.1409 | 0 | 0 | 0 | 0 | 0 | 64.7245
5359 | 75.1323 | 0 | 42.9 | 0 | 56.3 | 37.5662 | 4.9 | 0 | 0 | 0 | 0 | 54.142
5360 | 79.312 | 0 | 42.9 | 0 | 37.6 | 39.656 | 39.3 | 0 | 12.1 | 0 | 0 | 106.1835
5361 | 77.7019 | 0 | 42.9 | 0 | 0 | 38.851 | 0 | 0 | 56.7 | 0 | 0 | 180.4903
5362 | 84.0051 | 0 | 42.9 | 0 | 0 | 42.0026 | 0 | 0 | 123.1 | 0 | 0 | 67.7144
5363 | 83.9642 | 0 | 42.9 | 0 | 0 | 41.9821 | 0 | 0 | 179 | 0 | 0 | 240.9962
5364 | 89.0215 | 0 | 42.9 | 0 | 0 | 44.5108 | 0 | 0 | 184 | 0 | 0 | 221.1951
5365 | 88.6447 | 0 | 42.9 | 0 | 75.1 | 44.3223 | 481.2 | 0 | 195.8 | 0 | 0 | 81.9644
5366 | 86.4541 | 0 | 42.9 | 0 | 37.6 | 43.2271 | 408.8 | 0 | 209.1 | 0 | 0 | 96.1061
5367 | 85.9852 | 0 | 42.9 | 0 | 0 | 42.9926 | 0 | 0 | 218.4 | 0 | 0 | 197.1678
5368 | 86.2756 | 0 | 42.9 | 0 | 0 | 43.1378 | 0 | 0 | 218.4 | 0 | 0 | 97.4299
5369 | 87.5943 | 0 | 42.9 | 0 | 0 | 43.7972 | 0 | 0 | 209.1 | 0 | 0 | 92.6496
5370 | 82.436 | 0 | 42.9 | 0 | 37.6 | 41.218 | 517.6 | 0 | 197.8 | 0 | 0 | 145.2707
5371 | 74.8584 | 0 | 42.9 | 0 | 75.1 | 37.4292 | 491.8 | 0 | 171.1 | 0 | 0 | 268.2214
5372 | 73.0016 | 0 | 42.9 | 0 | 75.1 | 36.5008 | 364.8 | 0 | 75.6 | 0 | 0 | 121.6028
5373 | 68.3856 | 0 | 42.9 | 0 | 75.1 | 34.1928 | 260.8 | 0 | 59.5 | 0 | 0 | 178.4505
5374 | 65.1866 | 0 | 42.9 | 0 | 93.9 | 32.5933 | 203.9 | 0 | 36.5 | 0 | 0 | 132.3237
5375 | 63.2078 | 0 | 0 | 0 | 0 | 31.6039 | 0 | 0 | 0 | 0 | 0 | 143.1007
5376 | 63.7926 | 0 | 0 | 0 | 0 | 31.8963 | 0 | 0 | 0 | 0 | 0 | 181.3594
5377 | 62.0003 | 0 | 0 | 0 | 0 | 31.0002 | 0 | 0 | 0 | 0 | 0 | 56.5542
5378 | 61.7338 | 0 | 0 | 0 | 0 | 30.8669 | 0 | 0 | 0 | 0 | 0 | 49.8922
5379 | 61.7514 | 0 | 0 | 0 | 0 | 30.8757 | 0 | 0 | 0 | 0 | 0 | 48.2833
5380 | 62.9192 | 0 | 0 | 0 | 0 | 31.4596 | 0 | 0 | 0 | 0 | 0 | 48.4004
5381 | 61.2023 | 0 | 0 | 0 | 0 | 30.6011 | 0 | 0 | 0 | 0 | 0 | 47.7109
5382 | 81.0884 | 0 | 0 | 0 | 0 | 40.5442 | 0 | 0 | 0 | 0 | 0 | 57.8226
5383 | 115.6061 | 0 | 42.9 | 0 | 56.3 | 57.803 | 0 | 0 | 0 | 0 | 0 | 73.4707
5384 | 154.0389 | 0.7 | 43 | 0 | 37.6 | 77.0195 | 0 | 0 | 2.4 | 0 | 0 | 115.0189
5385 | 251.1107 | 2.1 | 43.2 | 0 | 0 | 125.5553 | 0 | 0 | 21.3 | 0 | 0 | 114.7736
5386 | 299.4177 | 3.5 | 43.4 | 0 | 0 | 149.7088 | 0 | 0 | 54.8 | 0 | 0 | 50.5812
5387 | 270.5422 | 3.5 | 43.4 | 0 | 0 | 135.2711 | 0 | 0 | 105.5 | 0 | 0 | 58.6319
5388 | 244.8003 | 2.8 | 43.3 | 0 | 0 | 122.4002 | 0 | 0 | 165.9 | 0 | 0 | 93.1238
5389 | 216.6696 | 1.4 | 43.1 | 0 | 75.1 | 108.3348 | 288.4 | 0.2 | 218.1 | 0 | 0 | 56.5548
5390 | 218.5818 | 2.1 | 43.2 | 0 | 37.6 | 109.2909 | 288.3 | 3.8 | 252.7 | 0 | 0 | 53.2248
5391 | 206.6644 | 3.5 | 43.4 | 0 | 0 | 103.3322 | 0 | 14.1 | 265.6 | 0 | 0 | 84.0869
5392 | 187.0116 | 2.8 | 43.3 | 0 | 0 | 93.5058 | 0 | 29.7 | 273.5 | 0 | 0 | 103.3003
5393 | 141.744 | 2.1 | 43.2 | 0 | 0 | 70.872 | 0 | 70.4 | 279.5 | 0 | 0 | 114.6561
5394 | 105.9811 | 0.7 | 43 | 0 | 37.6 | 52.9905 | 467.7 | 70.1 | 268.5 | 0 | 0 | 144.6024
5395 | 85.5306 | 0 | 42.9 | 0 | 75.1 | 42.7653 | 434.8 | 0 | 166.6 | 0 | 0 | 105.6976
5396 | 67.9006 | 0 | 42.9 | 0 | 75.1 | 33.9503 | 313.9 | 0 | 72.8 | 0 | 0 | 95.3964
5397 | 62.4277 | 0 | 42.9 | 0 | 75.1 | 31.2138 | 217.8 | 0 | 55.5 | 0 | 0 | 77.2069
5398 | 64.193 | 0 | 42.9 | 0 | 93.9 | 32.0965 | 164.9 | 0 | 31.9 | 0 | 0 | 63.8075
5399 | 63.1043 | 0 | 0 | 0 | 0 | 31.5521 | 0 | 0 | 0 | 0 | 0 | 69.4386
5400 | 63.0277 | 0 | 0 | 0 | 0 | 31.5138 | 0 | 0 | 0 | 0 | 0 | 57.9389
5401 | 60.1851 | 0 | 0 | 0 | 0 | 30.0925 | 0 | 0 | 0 | 0 | 0 | 49.8932
5402 | 62.5284 | 0 | 0 | 0 | 0 | 31.2642 | 0 | 0 | 0 | 0 | 0 | 45.5414
5403 | 60.5266 | 0 | 0 | 0 | 0 | 30.2633 | 0 | 0 | 0 | 0 | 0 | 45.4279
5404 | 59.8243 | 0 | 0 | 0 | 0 | 29.9122 | 0 | 0 | 0 | 0 | 0 | 46.5623
5405 | 63.9259 | 0 | 0 | 0 | 0 | 31.9629 | 0 | 0 | 0 | 0 | 0 | 55.2863
5406 | 83.0781 | 0 | 0 | 0 | 0 | 41.5391 | 0 | 0 | 0 | 0 | 0 | 61.5092
5407 | 104.7668 | 0 | 42.9 | 0 | 56.3 | 52.3834 | 5.1 | 0 | 0 | 0 | 0 | 52.7645
5408 | 150.3202 | 0.7 | 43 | 0 | 37.6 | 75.1601 | 28.8 | 11.5 | 31.1 | 0 | 0 | 53.5669
5409 | 233.565 | 2.1 | 43.2 | 0 | 0 | 116.7825 | 0 | 39.3 | 83.9 | 0 | 0 | 48.7446
5410 | 285.3494 | 3.5 | 43.4 | 0 | 0 | 142.6747 | 0 | 67.3 | 157.1 | 0 | 0 | 51.9612
5411 | 259.8967 | 3.5 | 43.4 | 0 | 0 | 129.9483 | 0 | 89.8 | 234.9 | 0 | 0 | 50.9255
5412 | 243.3961 | 2.8 | 43.3 | 0 | 0 | 121.698 | 0 | 103.9 | 294 | 0 | 0 | 51.8429
5413 | 239.2031 | 1.4 | 43.1 | 0 | 75.1 | 119.6016 | 576.5 | 92.7 | 335.2 | 0 | 0 | 91.8169
5414 | 253.176 | 2.1 | 43.2 | 0 | 37.6 | 126.588 | 522 | 100.9 | 367.3 | 0 | 0 | 86.581
5415 | 254.9221 | 3.5 | 43.4 | 0 | 0 | 127.4611 | 8 | 128.3 | 411.3 | 0 | 0 | 93.9652
5416 | 228.2508 | 2.8 | 43.3 | 0 | 0 | 114.1254 | 48 | 128.9 | 424 | 0 | 0 | 93.2482
5417 | 168.1103 | 2.1 | 43.2 | 0 | 0 | 84.0552 | 86.3 | 115.1 | 419.2 | 0 | 0 | 83.2665
5418 | 117.955 | 0.7 | 43 | 0 | 37.6 | 58.9775 | 819.2 | 93.3 | 394.9 | 0 | 0 | 103.1797
5419 | 102.6761 | 0 | 42.9 | 0 | 75.1 | 51.338 | 745.8 | 2.6 | 275.6 | 0 | 0 | 84.328
5420 | 84.3184 | 0 | 42.9 | 0 | 75.1 | 42.1592 | 611.2 | 0 | 167.8 | 0 | 0 | 65.6418
5421 | 64.2144 | 0 | 42.9 | 0 | 75.1 | 32.1072 | 497.1 | 0 | 132.6 | 0 | 0 | 69.0937
5422 | 60.5703 | 0 | 42.9 | 0 | 93.9 | 30.2852 | 439.1 | 0 | 95.1 | 0 | 0 | 106.309
5423 | 61.9405 | 0 | 0 | 0 | 0 | 30.9702 | 0 | 0 | 0 | 0 | 0 | 105.459
5424 | 59.9613 | 0 | 0 | 0 | 0 | 29.9807 | 0 | 0 | 0 | 0 | 0 | 82.3186
5425 | 59.8687 | 0 | 0 | 0 | 0 | 29.9343 | 0 | 0 | 0 | 0 | 0 | 66.5637
5426 | 58.2676 | 0 | 0 | 0 | 0 | 29.1338 | 0 | 0 | 0 | 0 | 0 | 55.4021
5427 | 61.0284 | 0 | 0 | 0 | 0 | 30.5142 | 0 | 0 | 0 | 0 | 0 | 47.94
5428 | 59.0322 | 0 | 0 | 0 | 0 | 29.5161 | 0 | 0 | 0 | 0 | 0 | 48.1693
5429 | 57.4776 | 0 | 0 | 0 | 0 | 28.7388 | 0 | 0 | 0 | 0 | 0 | 48.6279
5430 | 78.4553 | 0 | 0 | 0 | 0 | 39.2277 | 0 | 0 | 0 | 0 | 0 | 55.635
5431 | 118.7961 | 0 | 42.9 | 0 | 56.3 | 59.398 | 62.3 | 0 | 0 | 0 | 0 | 56.8985
5432 | 183.7236 | 0.7 | 43 | 0 | 37.6 | 91.8618 | 100.4 | 14.5 | 39.7 | 0 | 0 | 70.5896
5433 | 240.1899 | 2.1 | 43.2 | 0 | 0 | 120.095 | 0 | 22.7 | 98.5 | 0 | 0 | 65.7554
5434 | 262.4715 | 3.5 | 43.4 | 0 | 0 | 131.2358 | 0 | 37.8 | 159.9 | 0 | 0 | 49.6642
5435 | 263.5153 | 3.5 | 43.4 | 0 | 0 | 131.7577 | 0 | 53 | 195.3 | 0 | 0 | 90.9761
5436 | 256.6856 | 2.8 | 43.3 | 0 | 0 | 128.3428 | 0 | 74.8 | 225 | 0 | 0 | 73.1246
5437 | 250.3012 | 1.4 | 43.1 | 0 | 75.1 | 125.1506 | 480.8 | 75.6 | 241.6 | 0 | 0 | 68.0568
5438 | 260.6083 | 2.1 | 43.2 | 0 | 37.6 | 130.3041 | 421.4 | 86.5 | 256.3 | 0 | 0 | 95.1527
5439 | 243.0171 | 3.5 | 43.4 | 0 | 0 | 121.5085 | 0 | 110.2 | 253 | 0 | 0 | 120.139
5440 | 204.6874 | 2.8 | 43.3 | 0 | 0 | 102.3437 | 0 | 107.9 | 241.7 | 0 | 0 | 47.8251
5441 | 180.8385 | 2.1 | 43.2 | 0 | 0 | 90.4193 | 0 | 106.3 | 230.5 | 0 | 0 | 47.2481
5442 | 140.1355 | 0.7 | 43 | 0 | 37.6 | 70.0677 | 479.1 | 84.6 | 223.7 | 0 | 0 | 45.4277
5443 | 107.9745 | 0 | 42.9 | 0 | 75.1 | 53.9873 | 461 | 0 | 146.6 | 0 | 0 | 102.826
5444 | 80.2842 | 0 | 42.9 | 0 | 75.1 | 40.1421 | 345.1 | 0 | 64.6 | 0 | 0 | 96.9526
5445 | 66.3622 | 0 | 42.9 | 0 | 75.1 | 33.1811 | 252 | 0 | 50.7 | 0 | 0 | 153.3984
5446 | 63.5316 | 0 | 42.9 | 0 | 93.9 | 31.7658 | 212.5 | 0 | 33.7 | 0 | 0 | 103.3011
5447 | 60.9996 | 0 | 0 | 0 | 0 | 30.4998 | 0 | 0 | 0 | 0 | 0 | 65.6415
5448 | 62.8591 | 0 | 0 | 0 | 0 | 31.4296 | 0 | 0 | 0 | 0 | 0 | 61.626
5449 | 62.5495 | 0 | 0 | 0 | 0 | 31.2747 | 0 | 0 | 0 | 0 | 0 | 49.7781
5450 | 59.1865 | 0 | 0 | 0 | 0 | 29.5933 | 0 | 0 | 0 | 0 | 0 | 47.8246
5451 | 58.2949 | 0 | 0 | 0 | 0 | 29.1474 | 0 | 0 | 0 | 0 | 0 | 45.8799
5452 | 59.5432 | 0 | 0 | 0 | 0 | 29.7716 | 0 | 0 | 0 | 0 | 0 | 54.3701
5453 | 60.8911 | 0 | 0 | 0 | 0 | 30.4455 | 0 | 0 | 0 | 0 | 0 | 44.5257
5454 | 79.1836 | 0 | 0 | 0 | 0 | 39.5918 | 0 | 0 | 0 | 0 | 0 | 53.1093
5455 | 117.0893 | 0 | 42.9 | 0 | 56.3 | 58.5447 | 53 | 0 | 0 | 0 | 0 | 54.9441
5456 | 189.835 | 0.7 | 43 | 0 | 37.6 | 94.9175 | 22.3 | 4.3 | 14.8 | 0 | 0 | 48.2845
5457 | 286.3021 | 2.1 | 43.2 | 0 | 0 | 143.151 | 0 | 4.7 | 9.1 | 0 | 0 | 47.1351
5458 | 328.3753 | 3.5 | 43.4 | 0 | 0 | 164.1876 | 0 | 15.7 | 13.1 | 0 | 0 | 46.5636
5459 | 280.9565 | 3.5 | 43.4 | 0 | 0 | 140.4783 | 0 | 31 | 28.7 | 0 | 0 | 72.5493
5460 | 259.5973 | 2.8 | 43.3 | 0 | 0 | 129.7986 | 0 | 56.4 | 43.9 | 0 | 0 | 82.0809
5461 | 257.3593 | 1.4 | 43.1 | 0 | 75.1 | 128.6797 | 97.5 | 62.6 | 54.3 | 0 | 0 | 76.6175
5462 | 262.527 | 2.1 | 43.2 | 0 | 37.6 | 131.2635 | 60 | 69.1 | 60.2 | 0 | 0 | 57.015
5463 | 260.7183 | 3.5 | 43.4 | 0 | 0 | 130.3591 | 0 | 86.6 | 66.4 | 0 | 0 | 119.3939
5464 | 241.6841 | 2.8 | 43.3 | 0 | 0 | 120.842 | 0 | 88.5 | 67.5 | 0 | 0 | 137.7373
5465 | 184.1885 | 2.1 | 43.2 | 0 | 0 | 92.0942 | 0 | 93.1 | 65.3 | 0 | 0 | 146.4347
5466 | 139.7905 | 0.7 | 43 | 0 | 37.6 | 69.8953 | 39.1 | 77.8 | 58.5 | 0 | 0 | 98.1554
5467 | 108.9353 | 0 | 42.9 | 0 | 75.1 | 54.4676 | 62.3 | 0 | 7.1 | 0 | 0 | 71.8571
5468 | 79.8255 | 0 | 42.9 | 0 | 75.1 | 39.9127 | 14 | 0 | 0 | 0 | 0 | 113.92
5469 | 62.207 | 0 | 42.9 | 0 | 75.1 | 31.1035 | 0 | 0 | 0 | 0 | 0 | 86.464
5470 | 62.8904 | 0 | 42.9 | 0 | 93.9 | 31.4452 | 0 | 0 | 0 | 0 | 0 | 82.1995
5471 | 62.4838 | 0 | 0 | 0 | 0 | 31.2419 | 0 | 0 | 0 | 0 | 0 | 72.7794
5472 | 61.9851 | 0 | 0 | 0 | 0 | 30.9926 | 0 | 0 | 0 | 0 | 0 | 65.0698
5473 | 62.9614 | 0 | 0 | 0 | 0 | 31.4807 | 0 | 0 | 0 | 0 | 0 | 63.2331
5474 | 64.8677 | 0 | 0 | 0 | 0 | 32.4339 | 0 | 0 | 0 | 0 | 0 | 48.7451
5475 | 60.7925 | 0 | 0 | 0 | 0 | 30.3963 | 0 | 0 | 0 | 0 | 0 | 45.9937
5476 | 62.9883 | 0 | 0 | 0 | 0 | 31.4942 | 0 | 0 | 0 | 0 | 0 | 48.8586
5477 | 63.0677 | 0 | 0 | 0 | 0 | 31.5338 | 0 | 0 | 0 | 0 | 0 | 54.4835
5478 | 82.1883 | 0 | 0 | 0 | 0 | 41.0942 | 0 | 0 | 0 | 0 | 0 | 58.6326
5479 | 125.2056 | 0 | 42.9 | 0 | 56.3 | 62.6028 | 0 | 0 | 0 | 0 | 0 | 52.9938
5480 | 219.5531 | 0.7 | 43 | 0 | 37.6 | 109.7766 | 0 | 23.6 | 0.7 | 0 | 0 | 46.1081
5481 | 379.541 | 2.1 | 43.2 | 0 | 0 | 189.7705 | 0 | 43.1 | 22.1 | 0 | 0 | 45.0895
5482 | 436.303 | 3.5 | 43.4 | 0 | 0 | 218.1515 | 0 | 75.2 | 71.7 | 0 | 0 | 48.1677
5483 | 427.6456 | 3.5 | 43.4 | 0 | 0 | 213.8228 | 0 | 103 | 144.1 | 0 | 0 | 152.2764
5484 | 348.6966 | 2.8 | 43.3 | 0 | 0 | 174.3483 | 0 | 129.8 | 213.6 | 0 | 0 | 204.0001
5485 | 314.3532 | 1.4 | 43.1 | 0 | 75.1 | 157.1766 | 306.1 | 121.3 | 258.5 | 0 | 0 | 206.9186
5486 | 291.2946 | 2.1 | 43.2 | 0 | 37.6 | 145.6473 | 294.3 | 145.8 | 288.1 | 0 | 0 | 85.6301
5487 | 278.0739 | 3.5 | 43.4 | 0 | 0 | 139.037 | 0 | 199.1 | 330.8 | 0 | 0 | 57.0156
5488 | 211.0696 | 2.8 | 43.3 | 0 | 0 | 105.5348 | 0 | 206.9 | 350 | 0 | 0 | 82.3197
5489 | 160.3396 | 2.1 | 43.2 | 0 | 0 | 80.1698 | 1 | 195.2 | 363 | 0 | 0 | 97.0723
5490 | 122.486 | 0.7 | 43 | 0 | 37.6 | 61.243 | 616.5 | 153.5 | 373.3 | 0 | 0 | 109.3295
5491 | 117.967 | 0 | 42.9 | 0 | 75.1 | 58.9835 | 607.6 | 34.8 | 255.2 | 0 | 0 | 105.5783
5492 | 86.7743 | 0 | 42.9 | 0 | 75.1 | 43.3871 | 473.8 | 5.3 | 138.1 | 0 | 0 | 97.6716
5493 | 65.3345 | 0 | 42.9 | 0 | 75.1 | 32.6672 | 362.5 | 2.9 | 105.4 | 0 | 0 | 108.6054
5494 | 63.5549 | 0 | 42.9 | 0 | 93.9 | 31.7774 | 318.4 | 0.3 | 82.9 | 0 | 0 | 79.475
5495 | 62.0781 | 0 | 0 | 0 | 0 | 31.039 | 0 | 0 | 0 | 0 | 0 | 74.975
5496 | 63.1858 | 0 | 0 | 0 | 0 | 31.5929 | 0 | 0 | 0 | 0 | 0 | 74.7407
5497 | 61.3396 | 0 | 0 | 0 | 0 | 30.6698 | 0 | 0 | 0 | 0 | 0 | 57.9392
5498 | 64.3346 | 0 | 0 | 0 | 0 | 32.1673 | 0 | 0 | 0 | 0 | 0 | 56.6682
5499 | 63.9079 | 0 | 0 | 0 | 0 | 31.9539 | 0 | 0 | 0 | 0 | 0 | 58.4032
5500 | 63.4306 | 0 | 0 | 0 | 0 | 31.7153 | 0 | 0 | 0 | 0 | 0 | 51.3851
5501 | 61.6383 | 0 | 0 | 0 | 0 | 30.8192 | 0 | 0 | 0 | 0 | 0 | 50.2364
5502 | 66.7133 | 0 | 0 | 0 | 0 | 33.3566 | 0 | 0 | 0 | 0 | 0 | 59.8966
5503 | 80.1983 | 0 | 42.9 | 0 | 56.3 | 40.0992 | 222.9 | 0 | 29.2 | 0 | 0 | 54.1428
5504 | 83.4857 | 0 | 42.9 | 0 | 37.6 | 41.7428 | 261.4 | 0 | 108.4 | 0 | 0 | 49.319
5505 | 86.1594 | 0 | 42.9 | 0 | 0 | 43.0797 | 0 | 1.1 | 194.9 | 0 | 0 | 71.5092
5506 | 82.2798 | 0 | 42.9 | 0 | 0 | 41.1399 | 0 | 18.3 | 282.4 | 0 | 0 | 138.092
5507 | 86.0537 | 0 | 42.9 | 0 | 0 | 43.0269 | 0 | 35.4 | 326.3 | 0 | 0 | 114.2875
5508 | 84.6377 | 0 | 42.9 | 0 | 0 | 42.3188 | 20 | 56.2 | 378.2 | 0 | 0 | 100.5487
5509 | 85.1233 | 0 | 42.9 | 0 | 75.1 | 42.5617 | 937.1 | 69.9 | 431.5 | 0 | 0 | 125.7973
5510 | 82.8271 | 0 | 42.9 | 0 | 37.6 | 41.4135 | 876.7 | 77.8 | 464.6 | 0 | 0 | 80.0674
5511 | 85.5442 | 0 | 42.9 | 0 | 0 | 42.7721 | 147.9 | 75.1 | 500.2 | 0 | 0 | 130.7507
5512 | 86.279 | 0 | 42.9 | 0 | 0 | 43.1395 | 253.2 | 72.8 | 508 | 0 | 0 | 73.2406
5513 | 81.69 | 0 | 42.9 | 0 | 0 | 40.845 | 306.4 | 65.1 | 498 | 0 | 0 | 93.605
5514 | 78.9035 | 0 | 42.9 | 0 | 37.6 | 39.4517 | 1171.5 | 55.5 | 487.8 | 0 | 0 | 74.7411
5515 | 73.2638 | 0 | 42.9 | 0 | 75.1 | 36.6319 | 1106.1 | 48.5 | 395.3 | 0 | 0 | 150.3303
5516 | 73.9134 | 0 | 42.9 | 0 | 75.1 | 36.9567 | 933.8 | 14.5 | 263.7 | 0 | 0 | 173.0552
5517 | 66.9997 | 0 | 42.9 | 0 | 75.1 | 33.4998 | 835.9 | 12.3 | 230.2 | 0 | 0 | 131.5088
5518 | 63.6296 | 0 | 42.9 | 0 | 93.9 | 31.8148 | 796.7 | 8.5 | 195.1 | 0 | 0 | 122.1486
5519 | 64.4688 | 0 | 0 | 0 | 0 | 32.2344 | 17 | 5.5 | 18.7 | 0 | 0 | 108.2481
5520 | 63.218 | 0 | 0 | 0 | 0 | 31.609 | 14.6 | 2.3 | 11.1 | 0 | 0 | 85.2756
5521 | 63.1585 | 0 | 0 | 0 | 0 | 31.5792 | 5.8 | 0.2 | 3.7 | 0 | 0 | 67.2543
5522 | 64.4196 | 0 | 0 | 0 | 0 | 32.2098 | 0.3 | 0 | 0 | 0 | 0 | 57.2478
5523 | 63.1616 | 0 | 0 | 0 | 0 | 31.5808 | 0 | 0 | 0 | 0 | 0 | 54.5994
5524 | 63.6881 | 0 | 0 | 0 | 0 | 31.8441 | 0 | 0 | 0 | 0 | 0 | 51.8432
5525 | 63.7291 | 0 | 0 | 0 | 0 | 31.8645 | 0 | 0 | 0 | 0 | 0 | 55.059
5526 | 66.6185 | 0 | 0 | 0 | 0 | 33.3092 | 0 | 0 | 0 | 0 | 0 | 55.4018
5527 | 80.137 | 0 | 42.9 | 0 | 56.3 | 40.0685 | 770.9 | 16.4 | 148.3 | 0 | 0 | 58.4028
5528 | 89.6054 | 0 | 42.9 | 0 | 37.6 | 44.8027 | 683.6 | 36.4 | 190.3 | 0 | 0 | 49.0877
5529 | 88.4863 | 0 | 42.9 | 0 | 0 | 44.2431 | 28.5 | 53.9 | 267 | 0 | 0 | 87.7619
5530 | 91.5942 | 0 | 42.9 | 0 | 0 | 45.7971 | 111.1 | 67.4 | 321 | 0 | 0 | 75.677
5531 | 87.4722 | 0 | 42.9 | 0 | 0 | 43.7361 | 183.7 | 77.4 | 363.5 | 0 | 0 | 78.0456
5532 | 89.6448 | 0 | 42.9 | 0 | 0 | 44.8224 | 248.6 | 86.1 | 410 | 0 | 0 | 80.307
5533 | 86.6934 | 0 | 42.9 | 0 | 75.1 | 43.3467 | 1314.1 | 96.6 | 464.1 | 0 | 0 | 54.2559
5534 | 85.3232 | 0 | 42.9 | 0 | 37.6 | 42.6616 | 1189.5 | 104 | 481.1 | 0 | 0 | 55.1724
5535 | 84.6953 | 0 | 42.9 | 0 | 0 | 42.3477 | 344.3 | 106.7 | 486.1 | 0 | 0 | 83.5036
5536 | 86.7262 | 0 | 42.9 | 0 | 0 | 43.3631 | 471.9 | 113.6 | 497.2 | 0 | 0 | 58.9784
5537 | 87.1787 | 0 | 42.9 | 0 | 0 | 43.5894 | 530.7 | 122.2 | 510.5 | 0 | 0 | 56.785
5538 | 84.722 | 0 | 42.9 | 0 | 37.6 | 42.361 | 1469.6 | 123.6 | 532.2 | 0 | 0 | 116.8757
5539 | 88.141 | 0 | 42.9 | 0 | 75.1 | 44.0705 | 1431.6 | 112.1 | 484 | 0 | 0 | 73.5871
5540 | 76.8301 | 0 | 42.9 | 0 | 75.1 | 38.415 | 1243.9 | 67 | 335.4 | 0 | 0 | 100.1912
5541 | 70.5793 | 0 | 42.9 | 0 | 75.1 | 35.2896 | 1112.3 | 62.3 | 297.2 | 0 | 0 | 122.2008
5542 | 66.5509 | 0 | 42.9 | 0 | 93.9 | 33.2754 | 1049.4 | 55.9 | 262.3 | 0 | 0 | 119.4942
5543 | 65.3044 | 0 | 0 | 0 | 0 | 32.6522 | 141.3 | 47.6 | 55.8 | 0 | 0 | 90.5
5544 | 63.09 | 0 | 0 | 0 | 0 | 31.545 | 141 | 39.1 | 49.8 | 0 | 0 | 69.5551
5545 | 62.9778 | 0 | 0 | 0 | 0 | 31.4889 | 100.6 | 30.1 | 34.1 | 0 | 0 | 54.5997
5546 | 61.8243 | 0 | 0 | 0 | 0 | 30.9121 | 54.6 | 20.6 | 20.6 | 0 | 0 | 52.0768
5547 | 60.6652 | 0 | 0 | 0 | 0 | 30.3326 | 30.7 | 12.3 | 9.5 | 0 | 0 | 46.7913
5548 | 62.0521 | 0 | 0 | 0 | 0 | 31.026 | 19.3 | 7 | 2.9 | 0 | 0 | 48.399
5549 | 62.4026 | 0 | 0 | 0 | 0 | 31.2013 | 11.9 | 2.9 | 0 | 0 | 0 | 46.9067
5550 | 81.6116 | 0 | 0 | 0 | 0 | 40.8058 | 5.6 | 2.8 | 0 | 0 | 0 | 57.0166
5551 | 120.9302 | 0 | 42.9 | 0 | 56.3 | 60.4651 | 834.7 | 47.7 | 141.8 | 0 | 0 | 50.3513
5552 | 181.1748 | 0.7 | 43 | 0 | 37.6 | 90.5874 | 637.5 | 186.4 | 177.2 | 0 | 0 | 76.8519
5553 | 220.1383 | 2.1 | 43.2 | 0 | 0 | 110.0691 | 2.2 | 190.4 | 188.5 | 0 | 0 | 78.646
5554 | 263.6954 | 3.5 | 43.4 | 0 | 0 | 131.8477 | 11.3 | 234.3 | 247.1 | 0 | 0 | 90.5012
5555 | 267.9547 | 3.5 | 43.4 | 0 | 0 | 133.9773 | 20.9 | 254.6 | 284.6 | 0 | 0 | 59.3228
5556 | 241.9051 | 2.8 | 43.3 | 0 | 0 | 120.9525 | 38.9 | 236.4 | 291 | 0 | 0 | 60.8185
5557 | 230.3078 | 1.4 | 43.1 | 0 | 75.1 | 115.1539 | 940.3 | 193.2 | 302.6 | 0 | 0 | 77.2064
5558 | 236.4916 | 2.1 | 43.2 | 0 | 37.6 | 118.2458 | 770.6 | 202.5 | 303 | 0 | 0 | 86.2231
5559 | 236.5911 | 3.5 | 43.4 | 0 | 0 | 118.2956 | 40.1 | 248.1 | 323.9 | 0 | 0 | 66.217
5560 | 217.9078 | 2.8 | 43.3 | 0 | 0 | 108.9539 | 74.1 | 234.1 | 327.3 | 0 | 0 | 68.402
5561 | 185.9349 | 2.1 | 43.2 | 0 | 0 | 92.9675 | 111.2 | 199.5 | 353.3 | 0 | 0 | 60.1265
5562 | 144.6287 | 0.7 | 43 | 0 | 37.6 | 72.3144 | 1002 | 147 | 389.4 | 0 | 0 | 88.1246
5563 | 131.1335 | 0 | 42.9 | 0 | 75.1 | 65.5667 | 963 | 31.3 | 277.4 | 0 | 0 | 117.5328
5564 | 91.4448 | 0 | 42.9 | 0 | 75.1 | 45.7224 | 789.9 | 8.6 | 159.8 | 0 | 0 | 156.6883
5565 | 72.3948 | 0 | 42.9 | 0 | 75.1 | 36.1974 | 663.3 | 6.3 | 126.4 | 0 | 0 | 122.1556
5566 | 69.2488 | 0 | 42.9 | 0 | 93.9 | 34.6244 | 585.7 | 2.9 | 94.6 | 0 | 0 | 164.0949
5567 | 63.8961 | 0 | 0 | 0 | 0 | 31.9481 | 0 | 0.7 | 0 | 0 | 0 | 211.0635
5568 | 66.2103 | 0 | 0 | 0 | 0 | 33.1051 | 0 | 0 | 0 | 0 | 0 | 78.527
5569 | 64.9536 | 0 | 0 | 0 | 0 | 32.4768 | 0 | 0 | 0 | 0 | 0 | 68.2872
5570 | 62.2321 | 0 | 0 | 0 | 0 | 31.1161 | 0 | 0 | 0 | 0 | 0 | 56.7826
5571 | 63.5412 | 0 | 0 | 0 | 0 | 31.7706 | 0 | 0 | 0 | 0 | 0 | 55.5175
5572 | 60.8303 | 0 | 0 | 0 | 0 | 30.4152 | 0 | 0 | 0 | 0 | 0 | 55.6356
5573 | 62.4144 | 0 | 0 | 0 | 0 | 31.2072 | 0 | 0 | 0 | 0 | 0 | 52.5363
5574 | 69.5271 | 0 | 0 | 0 | 0 | 34.7635 | 0 | 0 | 0 | 0 | 0 | 58.1697
5575 | 96.8663 | 0 | 42.9 | 0 | 56.3 | 48.4331 | 280 | 0 | 13.2 | 0 | 0 | 50.4655
5576 | 137.0446 | 0.7 | 43 | 0 | 37.6 | 68.5223 | 191.4 | 56.5 | 32.1 | 0 | 0 | 65.9862
5577 | 213.9451 | 2.1 | 43.2 | 0 | 0 | 106.9725 | 0 | 44.1 | 28.7 | 0 | 0 | 53.453
5578 | 272.4318 | 3.5 | 43.4 | 0 | 0 | 136.2159 | 0 | 36.6 | 41.3 | 0 | 0 | 77.4452
5579 | 273.475 | 3.5 | 43.4 | 0 | 0 | 136.7375 | 0 | 34.4 | 78.8 | 0 | 0 | 57.4782
5580 | 255.7062 | 2.8 | 43.3 | 0 | 0 | 127.8531 | 0 | 52.6 | 165.9 | 0 | 0 | 57.3626
5581 | 239.4449 | 1.4 | 43.1 | 0 | 75.1 | 119.7224 | 518.9 | 63.7 | 252 | 0 | 0 | 64.6103
5582 | 243.0694 | 2.1 | 43.2 | 0 | 37.6 | 121.5347 | 456.3 | 90.3 | 272.2 | 0 | 0 | 67.8288
5583 | 250.5348 | 3.5 | 43.4 | 0 | 0 | 125.2674 | 0 | 138 | 256.9 | 0 | 0 | 95.0326
5584 | 226.4167 | 2.8 | 43.3 | 0 | 0 | 113.2083 | 0 | 154.8 | 223.5 | 0 | 0 | 68.2884
5585 | 172.7945 | 2.1 | 43.2 | 0 | 0 | 86.3973 | 0 | 156.2 | 193.6 | 0 | 0 | 95.5123
5586 | 133.2543 | 0.7 | 43 | 0 | 37.6 | 66.6271 | 410.5 | 129.4 | 160.7 | 0 | 0 | 65.6404
5587 | 126.7549 | 0 | 42.9 | 0 | 75.1 | 63.3774 | 370.5 | 29 | 72.4 | 0 | 0 | 99.1096
5588 | 86.425 | 0 | 42.9 | 0 | 75.1 | 43.2125 | 287.1 | 3.9 | 25.1 | 0 | 0 | 135.0807
5589 | 69.8835 | 0 | 42.9 | 0 | 75.1 | 34.9417 | 213.2 | 1.2 | 21.4 | 0 | 0 | 102.2169
5590 | 66.594 | 0 | 42.9 | 0 | 93.9 | 33.297 | 176.3 | 0 | 12.9 | 0 | 0 | 102.2177
5591 | 64.0985 | 0 | 0 | 0 | 0 | 32.0492 | 0 | 0 | 0 | 0 | 0 | 122.7332
5592 | 66.6541 | 0 | 0 | 0 | 0 | 33.3271 | 0 | 0 | 0 | 0 | 0 | 63.8079
5593 | 66.0088 | 0 | 0 | 0 | 0 | 33.0044 | 0 | 0 | 0 | 0 | 0 | 52.0757
5594 | 65.5319 | 0 | 0 | 0 | 0 | 32.7659 | 0 | 0 | 0 | 0 | 0 | 48.8591
5595 | 65.0233 | 0 | 0 | 0 | 0 | 32.5116 | 0 | 0 | 0 | 0 | 0 | 49.0899
5596 | 62.335 | 0 | 0 | 0 | 0 | 31.1675 | 0 | 0 | 0 | 0 | 0 | 50.3523
5597 | 62.3412 | 0 | 0 | 0 | 0 | 31.1706 | 0 | 0 | 0 | 0 | 0 | 54.8302
5598 | 81.2471 | 0 | 0 | 0 | 0 | 40.6236 | 0 | 0 | 0 | 0 | 0 | 54.7142
5599 | 123.8336 | 0 | 42.9 | 0 | 56.3 | 61.9168 | 0 | 0 | 0 | 0 | 0 | 49.8927
5600 | 205.1752 | 0.7 | 43 | 0 | 37.6 | 102.5876 | 0 | 37.9 | 0 | 0 | 0 | 49.0896
5601 | 294.25 | 2.1 | 43.2 | 0 | 0 | 147.125 | 0 | 36.7 | 0 | 0 | 0 | 47.7116
5602 | 330.0123 | 3.5 | 43.4 | 0 | 0 | 165.0061 | 0 | 60 | 2.4 | 0 | 0 | 57.0153
5603 | 290.4243 | 3.5 | 43.4 | 0 | 0 | 145.2122 | 0 | 80.7 | 10 | 0 | 0 | 70.5892
5604 | 262.6609 | 2.8 | 43.3 | 0 | 0 | 131.3304 | 0 | 92.5 | 20.6 | 0 | 0 | 69.7849
5605 | 259.7064 | 1.4 | 43.1 | 0 | 75.1 | 129.8532 | 42.6 | 91.1 | 40.3 | 0 | 0 | 141.2427
5606 | 262.1951 | 2.1 | 43.2 | 0 | 37.6 | 131.0975 | 45.5 | 102.3 | 55.7 | 0 | 0 | 139.8685
5607 | 252.4638 | 3.5 | 43.4 | 0 | 0 | 126.2319 | 0 | 107.3 | 68.5 | 0 | 0 | 92.5332
5608 | 210.4966 | 2.8 | 43.3 | 0 | 0 | 105.2483 | 0 | 90.6 | 77 | 0 | 0 | 66.5618
5609 | 165.2194 | 2.1 | 43.2 | 0 | 0 | 82.6097 | 0 | 101.2 | 86.1 | 0 | 0 | 150.2275
5610 | 141.3584 | 0.7 | 43 | 0 | 37.6 | 70.6792 | 86.5 | 82.1 | 77.5 | 0 | 0 | 152.4188
5611 | 106.0638 | 0 | 42.9 | 0 | 75.1 | 53.0319 | 92.7 | 0 | 24.9 | 0 | 0 | 139.8325
5612 | 74.9163 | 0 | 42.9 | 0 | 75.1 | 37.4582 | 35.7 | 0 | 0 | 0 | 0 | 122.8492
5613 | 69.3024 | 0 | 42.9 | 0 | 75.1 | 34.6512 | 10.6 | 0 | 0 | 0 | 0 | 118.8024
5614 | 65.9174 | 0 | 42.9 | 0 | 93.9 | 32.9587 | 2.3 | 0 | 0 | 0 | 0 | 109.8154
5615 | 68.8146 | 0 | 0 | 0 | 0 | 34.4073 | 0 | 0 | 0 | 0 | 0 | 115.6275
5616 | 66.7183 | 0 | 0 | 0 | 0 | 33.3591 | 0 | 0 | 0 | 0 | 0 | 100.9063
5617 | 67.2811 | 0 | 0 | 0 | 0 | 33.6405 | 0 | 0 | 0 | 0 | 0 | 50.122
5618 | 63.9069 | 0 | 0 | 0 | 0 | 31.9535 | 0 | 0 | 0 | 0 | 0 | 50.351
5619 | 64.9514 | 0 | 0 | 0 | 0 | 32.4757 | 0 | 0 | 0 | 0 | 0 | 45.9932
5620 | 62.3369 | 0 | 0 | 0 | 0 | 31.1684 | 0 | 0 | 0 | 0 | 0 | 50.1227
5621 | 64.9656 | 0 | 0 | 0 | 0 | 32.4828 | 0 | 0 | 0 | 0 | 0 | 58.6335
5622 | 82.8407 | 0 | 0 | 0 | 0 | 41.4204 | 0 | 0 | 0 | 0 | 0 | 74.393
5623 | 125.9178 | 0 | 42.9 | 0 | 56.3 | 62.9589 | 0 | 0 | 0 | 0 | 0 | 78.7688
5624 | 206.7087 | 0.7 | 43 | 0 | 37.6 | 103.3544 | 0 | 4.4 | 0 | 0 | 0 | 93.4858
5625 | 320.3266 | 2.1 | 43.2 | 0 | 0 | 160.1633 | 0 | 7.6 | 0 | 0 | 0 | 55.9788
5626 | 344.8666 | 3.5 | 43.4 | 0 | 0 | 172.4333 | 0 | 19.1 | 0 | 0 | 0 | 91.4577
5627 | 348.427 | 3.5 | 43.4 | 0 | 0 | 174.2135 | 0 | 32.9 | 0 | 0 | 0 | 86.3424
5628 | 288.5692 | 2.8 | 43.3 | 0 | 0 | 144.2846 | 0 | 61.5 | 7.1 | 0 | 0 | 120.2315
5629 | 247.691 | 1.4 | 43.1 | 0 | 75.1 | 123.8455 | 0 | 70.1 | 19.9 | 0 | 0 | 167.7598
5630 | 258.5702 | 2.1 | 43.2 | 0 | 37.6 | 129.2851 | 0 | 81.5 | 32.5 | 0 | 0 | 141.512
5631 | 248.569 | 3.5 | 43.4 | 0 | 0 | 124.2845 | 0 | 103.5 | 43.7 | 0 | 0 | 214.2031
5632 | 220.7324 | 2.8 | 43.3 | 0 | 0 | 110.3662 | 0 | 109.8 | 37.5 | 0 | 0 | 87.0542
5633 | 162.347 | 2.1 | 43.2 | 0 | 0 | 81.1735 | 0 | 116.1 | 34.8 | 0 | 0 | 172.2137
5634 | 141.1957 | 0.7 | 43 | 0 | 37.6 | 70.5979 | 1.5 | 101.5 | 29.2 | 0 | 0 | 129.7114
5635 | 119.9505 | 0 | 42.9 | 0 | 75.1 | 59.9753 | 4.8 | 12 | 1.7 | 0 | 0 | 135.4523
5636 | 88.4079 | 0 | 42.9 | 0 | 75.1 | 44.2039 | 0 | 0 | 0 | 0 | 0 | 144.2902
5637 | 68.9581 | 0 | 42.9 | 0 | 75.1 | 34.479 | 0 | 0 | 0 | 0 | 0 | 146.3398
5638 | 65.4039 | 0 | 42.9 | 0 | 93.9 | 32.7019 | 0 | 0 | 0 | 0 | 0 | 152.2489
5639 | 64.8631 | 0 | 0 | 0 | 0 | 32.4315 | 0 | 0 | 0 | 0 | 0 | 99.1126
5640 | 63.1349 | 0 | 0 | 0 | 0 | 31.5675 | 0 | 0 | 0 | 0 | 0 | 73.472
5641 | 62.6549 | 0 | 0 | 0 | 0 | 31.3274 | 0 | 0 | 0 | 0 | 0 | 59.8962
5642 | 63.3757 | 0 | 0 | 0 | 0 | 31.6879 | 0 | 0 | 0 | 0 | 0 | 50.1217
5643 | 61.9659 | 0 | 0 | 0 | 0 | 30.983 | 0 | 0 | 0 | 0 | 0 | 47.4801
5644 | 60.676 | 0 | 0 | 0 | 0 | 30.338 | 0 | 0 | 0 | 0 | 0 | 55.8639
5645 | 63.5586 | 0 | 0 | 0 | 0 | 31.7793 | 0 | 0 | 0 | 0 | 0 | 57.5924
5646 | 86.9475 | 0 | 0 | 0 | 0 | 43.4738 | 0 | 0 | 0 | 0 | 0 | 66.3324
5647 | 123.761 | 0 | 42.9 | 0 | 56.3 | 61.8805 | 0 | 0 | 0 | 0 | 0 | 70.7045
5648 | 167.6929 | 0.7 | 43 | 0 | 37.6 | 83.8464 | 0 | 24 | 0 | 0 | 0 | 82.4378
5649 | 214.3653 | 2.1 | 43.2 | 0 | 0 | 107.1827 | 0 | 27.3 | 0 | 0 | 0 | 82.9141
5650 | 269.4789 | 3.5 | 43.4 | 0 | 0 | 134.7394 | 0 | 44.9 | 10.5 | 0 | 0 | 190.945
5651 | 283.7877 | 3.5 | 43.4 | 0 | 0 | 141.8938 | 0 | 66.6 | 53 | 0 | 0 | 90.6218
5652 | 262.4743 | 2.8 | 43.3 | 0 | 0 | 131.2371 | 0 | 90.6 | 111.1 | 0 | 0 | 79.0025
5653 | 252.3801 | 1.4 | 43.1 | 0 | 75.1 | 126.1901 | 58.3 | 92.5 | 166.9 | 0 | 0 | 79.2372
5654 | 253.1283 | 2.1 | 43.2 | 0 | 37.6 | 126.5641 | 93 | 106.6 | 210.2 | 0 | 0 | 100.0694
5655 | 256.6223 | 3.5 | 43.4 | 0 | 0 | 128.3112 | 0 | 138.2 | 254.8 | 0 | 0 | 73.7014
5656 | 236.0283 | 2.8 | 43.3 | 0 | 0 | 118.0141 | 0 | 140.8 | 286.6 | 0 | 0 | 104.2527
5657 | 167.5884 | 2.1 | 43.2 | 0 | 0 | 83.7942 | 0 | 131.5 | 301.2 | 0 | 0 | 86.0999
5658 | 123.8088 | 0.7 | 43 | 0 | 37.6 | 61.9044 | 359.3 | 104.4 | 298.5 | 0 | 0 | 152.9972
5659 | 91.8083 | 0 | 42.9 | 0 | 75.1 | 45.9042 | 370.8 | 9.4 | 197.2 | 0 | 0 | 166.8267
5660 | 75.883 | 0 | 42.9 | 0 | 75.1 | 37.9415 | 239 | 0 | 83 | 0 | 0 | 173.2279
5661 | 61.0042 | 0 | 42.9 | 0 | 75.1 | 30.5021 | 146.2 | 0 | 57.2 | 0 | 0 | 231.8909
5662 | 60.0602 | 0 | 42.9 | 0 | 93.9 | 30.0301 | 111.4 | 0 | 36.1 | 0 | 0 | 176.2805
5663 | 59.8752 | 0 | 0 | 0 | 0 | 29.9376 | 0 | 0 | 0 | 0 | 0 | 79.0035
5664 | 62.1426 | 0 | 0 | 0 | 0 | 31.0713 | 0 | 0 | 0 | 0 | 0 | 53.5666
5665 | 61.1025 | 0 | 0 | 0 | 0 | 30.5512 | 0 | 0 | 0 | 0 | 0 | 51.3858
5666 | 60.3732 | 0 | 0 | 0 | 0 | 30.1866 | 0 | 0 | 0 | 0 | 0 | 51.0423
5667 | 59.2699 | 0 | 0 | 0 | 0 | 29.6349 | 0 | 0 | 0 | 0 | 0 | 46.2219
5668 | 58.2481 | 0 | 0 | 0 | 0 | 29.124 | 0 | 0 | 0 | 0 | 0 | 47.8258
5669 | 60.6571 | 0 | 0 | 0 | 0 | 30.3286 | 0 | 0 | 0 | 0 | 0 | 49.2052
5670 | 64.2534 | 0 | 0 | 0 | 0 | 32.1267 | 0 | 0 | 0 | 0 | 0 | 60.0106
5671 | 70.8362 | 0 | 42.9 | 0 | 56.3 | 35.4181 | 7.8 | 0 | 0 | 0 | 0 | 58.2874
5672 | 75.6896 | 0 | 42.9 | 0 | 37.6 | 37.8448 | 29.5 | 0 | 16.2 | 0 | 0 | 61.5089
5673 | 72.7001 | 0 | 42.9 | 0 | 0 | 36.35 | 0 | 6.7 | 62.5 | 0 | 0 | 63.1175
5674 | 72.4109 | 0 | 42.9 | 0 | 0 | 36.2055 | 0 | 20 | 125 | 0 | 0 | 120.5182
5675 | 70.1094 | 0 | 42.9 | 0 | 0 | 35.0547 | 0 | 28.8 | 189.3 | 0 | 0 | 108.1267
5676 | 67.8188 | 0 | 42.9 | 0 | 0 | 33.9094 | 0 | 41.1 | 249.5 | 0 | 0 | 101.2609
5677 | 65.9462 | 0 | 42.9 | 0 | 75.1 | 32.9731 | 556.3 | 53.9 | 297.8 | 0 | 0 | 87.0536
5678 | 66.7902 | 0 | 42.9 | 0 | 37.6 | 33.3951 | 522 | 62.4 | 337.8 | 0 | 0 | 61.627
5679 | 66.4365 | 0 | 42.9 | 0 | 0 | 33.2183 | 14 | 67.8 | 376.6 | 0 | 0 | 69.0921
5680 | 67.2811 | 0 | 42.9 | 0 | 0 | 33.6405 | 61.6 | 75.4 | 386.7 | 0 | 0 | 76.2647
5681 | 73.4417 | 0 | 42.9 | 0 | 0 | 36.7209 | 101.7 | 82 | 398.9 | 0 | 0 | 199.4834
5682 | 72.6049 | 0 | 42.9 | 0 | 37.6 | 36.3025 | 892.3 | 82.7 | 403.7 | 0 | 0 | 127.8162
5683 | 61.5627 | 0 | 42.9 | 0 | 75.1 | 30.7813 | 845.4 | 72.1 | 320.8 | 0 | 0 | 229.227
5684 | 57.8483 | 0 | 42.9 | 0 | 75.1 | 28.9241 | 686.9 | 32.1 | 194 | 0 | 0 | 170.7519
5685 | 53.8122 | 0 | 42.9 | 0 | 75.1 | 26.9061 | 598 | 26 | 160.5 | 0 | 0 | 200.9285
5686 | 54.088 | 0 | 42.9 | 0 | 93.9 | 27.044 | 550.2 | 19.7 | 126.6 | 0 | 0 | 240.7563
5687 | 58.276 | 0 | 0 | 0 | 0 | 29.138 | 0 | 12.2 | 0 | 0 | 0 | 252.6912
5688 | 57.3936 | 0 | 0 | 0 | 0 | 28.6968 | 0 | 5.1 | 0 | 0 | 0 | 78.2829
5689 | 56.1477 | 0 | 0 | 0 | 0 | 28.0739 | 0 | 0.7 | 0 | 0 | 0 | 60.5885
5690 | 56.9727 | 0 | 0 | 0 | 0 | 28.4864 | 0 | 0 | 0 | 0 | 0 | 49.4343
5691 | 54.1125 | 0 | 0 | 0 | 0 | 27.0562 | 0 | 0 | 0 | 0 | 0 | 48.1681
5692 | 54.5101 | 0 | 0 | 0 | 0 | 27.255 | 0 | 0 | 0 | 0 | 0 | 48.5146
5693 | 55.7042 | 0 | 0 | 0 | 0 | 27.8521 | 0 | 0 | 0 | 0 | 0 | 61.0493
5694 | 66.0776 | 0 | 0 | 0 | 0 | 33.0388 | 0 | 0 | 0 | 0 | 0 | 105.58
5695 | 73.6066 | 0 | 42.9 | 0 | 56.3 | 36.8033 | 313.2 | 0.4 | 27.3 | 0 | 0 | 61.3938
5696 | 78.4026 | 0 | 42.9 | 0 | 37.6 | 39.2013 | 227.9 | 7.7 | 18.1 | 0 | 0 | 54.1409
5697 | 75.229 | 0 | 42.9 | 0 | 0 | 37.6145 | 0 | 18.1 | 33.6 | 0 | 0 | 67.0248
5698 | 77.0923 | 0 | 42.9 | 0 | 0 | 38.5461 | 0 | 29.8 | 79.5 | 0 | 0 | 85.5127
5699 | 78.3059 | 0 | 42.9 | 0 | 0 | 39.153 | 0 | 38.8 | 82.8 | 0 | 0 | 189.4501
5700 | 74.4933 | 0 | 42.9 | 0 | 0 | 37.2466 | 0 | 47.4 | 98.8 | 0 | 0 | 152.4451
5701 | 73.8375 | 0 | 42.9 | 0 | 75.1 | 36.9187 | 549.2 | 54.2 | 137 | 0 | 0 | 433.0394
5702 | 74.7828 | 0 | 42.9 | 0 | 37.6 | 37.3914 | 444.7 | 59.8 | 148.2 | 0 | 0 | 375.6853
5703 | 74.6975 | 0 | 42.9 | 0 | 0 | 37.3488 | 0 | 62.6 | 144.8 | 0 | 0 | 117.6697
5704 | 75.7131 | 0 | 42.9 | 0 | 0 | 37.8566 | 0 | 65.6 | 129.8 | 0 | 0 | 142.9509
5705 | 79.5332 | 0 | 42.9 | 0 | 0 | 39.7666 | 0 | 67.9 | 102.2 | 0 | 0 | 337.5918
5706 | 74.0764 | 0 | 42.9 | 0 | 37.6 | 37.0382 | 391.5 | 63.5 | 81 | 0 | 0 | 159.1347
5707 | 64.798 | 0 | 42.9 | 0 | 75.1 | 32.399 | 375.9 | 53.3 | 70.4 | 0 | 0 | 168.4963
5708 | 58.7136 | 0 | 42.9 | 0 | 75.1 | 29.3568 | 270.8 | 17.2 | 20.3 | 0 | 0 | 159.3366
5709 | 60.7268 | 0 | 42.9 | 0 | 75.1 | 30.3634 | 191.3 | 11.5 | 14 | 0 | 0 | 148.9628
5710 | 56.8832 | 0 | 42.9 | 0 | 93.9 | 28.4416 | 139.2 | 5.8 | 3.5 | 0 | 0 | 154.0333
5711 | 57.5576 | 0 | 0 | 0 | 0 | 28.7788 | 0 | 1.8 | 0 | 0 | 0 | 135.4484
5712 | 59.0483 | 0 | 0 | 0 | 0 | 29.5241 | 0 | 0 | 0 | 0 | 0 | 77.4461
5713 | 55.8979 | 0 | 0 | 0 | 0 | 27.949 | 0 | 0 | 0 | 0 | 0 | 70.4739
5714 | 55.2186 | 0 | 0 | 0 | 0 | 27.6093 | 0 | 0 | 0 | 0 | 0 | 52.7653
5715 | 56.4298 | 0 | 0 | 0 | 0 | 28.2149 | 0 | 0 | 0 | 0 | 0 | 48.3992
5716 | 55.8927 | 0 | 0 | 0 | 0 | 27.9463 | 0 | 0 | 0 | 0 | 0 | 50.4667
5717 | 59.9068 | 0 | 0 | 0 | 0 | 29.9534 | 0 | 0 | 0 | 0 | 0 | 58.5177
5718 | 73.5108 | 0 | 0 | 0 | 0 | 36.7554 | 0 | 0 | 0 | 0 | 0 | 74.8563
5719 | 114.8495 | 0 | 42.9 | 0 | 56.3 | 57.4248 | 23.3 | 0 | 0 | 0 | 0 | 71.6263
5720 | 195.5233 | 0.7 | 43 | 0 | 37.6 | 97.7616 | 25.6 | 112 | 14.8 | 0 | 0 | 66.7942
5721 | 320.431 | 2.1 | 43.2 | 0 | 0 | 160.2155 | 0 | 119.4 | 52.7 | 0 | 0 | 140.7871
5722 | 380.309 | 3.5 | 43.4 | 0 | 0 | 190.1545 | 0 | 150.1 | 118.3 | 0 | 0 | 222.0766
5723 | 371.9808 | 3.5 | 43.4 | 0 | 0 | 185.9904 | 0 | 174.5 | 161.9 | 0 | 0 | 59.3235
5724 | 305.6496 | 2.8 | 43.3 | 0 | 0 | 152.8248 | 0 | 189.2 | 189.3 | 0 | 0 | 80.8982
5725 | 307.5965 | 1.4 | 43.1 | 0 | 75.1 | 153.7983 | 412.7 | 164.3 | 230 | 0 | 0 | 159.0072
5726 | 321.6856 | 2.1 | 43.2 | 0 | 37.6 | 160.8428 | 373.6 | 181.4 | 256.8 | 0 | 0 | 234.8834
5727 | 310.6954 | 3.5 | 43.4 | 0 | 0 | 155.3477 | 0 | 233.9 | 279.1 | 0 | 0 | 126.8638
5728 | 283.8329 | 2.8 | 43.3 | 0 | 0 | 141.9165 | 0 | 241.8 | 269 | 0 | 0 | 185.1535
5729 | 241.5654 | 2.1 | 43.2 | 0 | 0 | 120.7827 | 0 | 216.9 | 255.7 | 0 | 0 | 126.1368
5730 | 208.2952 | 0.7 | 43 | 0 | 37.6 | 104.1476 | 464.4 | 167.9 | 235.1 | 0 | 0 | 88.2412
5731 | 139.5008 | 0 | 42.9 | 0 | 75.1 | 69.7504 | 457 | 46.7 | 136.9 | 0 | 0 | 154.2422
5732 | 82.8792 | 0 | 42.9 | 0 | 75.1 | 41.4396 | 360.2 | 16.5 | 63.1 | 0 | 0 | 203.8529
5733 | 67.8433 | 0 | 42.9 | 0 | 75.1 | 33.9216 | 265.4 | 12.7 | 49.7 | 0 | 0 | 197.0734
5734 | 63.8372 | 0 | 42.9 | 0 | 93.9 | 31.9186 | 223.9 | 8.2 | 31.8 | 0 | 0 | 231.5354
5735 | 62.477 | 0 | 0 | 0 | 0 | 31.2385 | 0 | 4.2 | 0 | 0 | 0 | 210.2445
5736 | 61.7226 | 0 | 0 | 0 | 0 | 30.8613 | 0 | 1.1 | 0 | 0 | 0 | 95.1596
5737 | 61.3575 | 0 | 0 | 0 | 0 | 30.6788 | 0 | 0 | 0 | 0 | 0 | 74.1623
5738 | 61.5692 | 0 | 0 | 0 | 0 | 30.7846 | 0 | 0 | 0 | 0 | 0 | 65.8708
5739 | 58.5059 | 0 | 0 | 0 | 0 | 29.253 | 0 | 0 | 0 | 0 | 0 | 51.2711
5740 | 59.8463 | 0 | 0 | 0 | 0 | 29.9232 | 0 | 0 | 0 | 0 | 0 | 51.3856
5741 | 62.737 | 0 | 0 | 0 | 0 | 31.3685 | 0 | 0 | 0 | 0 | 0 | 58.6329
5742 | 84.497 | 0 | 0 | 0 | 0 | 42.2485 | 0 | 0 | 0 | 0 | 0 | 72.664
5743 | 112.0485 | 0 | 42.9 | 0 | 56.3 | 56.0242 | 38.2 | 0 | 0 | 0 | 0 | 58.4035
5744 | 176.6478 | 0.7 | 43 | 0 | 37.6 | 88.3239 | 58.4 | 89.8 | 33.5 | 0 | 0 | 50.1215
5745 | 228.5675 | 2.1 | 43.2 | 0 | 0 | 114.2838 | 0 | 77.5 | 83.2 | 0 | 0 | 84.9246
5746 | 224.3163 | 3.5 | 43.4 | 0 | 0 | 112.1582 | 0 | 93 | 140.1 | 0 | 0 | 165.0524
5747 | 213.5716 | 3.5 | 43.4 | 0 | 0 | 106.7858 | 0 | 90 | 188.3 | 0 | 0 | 92.4123
5748 | 198.2807 | 2.8 | 43.3 | 0 | 0 | 99.1403 | 0 | 90 | 244.6 | 0 | 0 | 122.202
5749 | 184.7721 | 1.4 | 43.1 | 0 | 75.1 | 92.386 | 506 | 72.6 | 298.2 | 0 | 0 | 80.5426
5750 | 186.3753 | 2.1 | 43.2 | 0 | 37.6 | 93.1877 | 488.2 | 93.9 | 333 | 0 | 0 | 185.811
5751 | 179.566 | 3.5 | 43.4 | 0 | 0 | 89.783 | 0 | 150.3 | 365.4 | 0 | 0 | 132.5358
5752 | 155.0201 | 2.8 | 43.3 | 0 | 0 | 77.5101 | 0.9 | 175.9 | 374.5 | 0 | 0 | 94.6801
5753 | 123.2038 | 2.1 | 43.2 | 0 | 0 | 61.6019 | 6.3 | 182.8 | 360.3 | 0 | 0 | 88.1234
5754 | 102.3011 | 0.7 | 43 | 0 | 37.6 | 51.1505 | 695.3 | 142.1 | 333.7 | 0 | 0 | 253.296
5755 | 79.6526 | 0 | 42.9 | 0 | 75.1 | 39.8263 | 671.9 | 30.8 | 220 | 0 | 0 | 259.459
5756 | 71.6067 | 0 | 42.9 | 0 | 75.1 | 35.8033 | 524.2 | 3.7 | 105.2 | 0 | 0 | 219.5444
5757 | 64.1874 | 0 | 42.9 | 0 | 75.1 | 32.0937 | 407.2 | 1.6 | 81.5 | 0 | 0 | 368.947
5758 | 63.0937 | 0 | 42.9 | 0 | 93.9 | 31.5469 | 347.5 | 0.1 | 66.3 | 0 | 0 | 214.6295
5759 | 62.344 | 0 | 0 | 0 | 0 | 31.172 | 0 | 0 | 0 | 0 | 0 | 227.4699
5760 | 58.9959 | 0 | 0 | 0 | 0 | 29.498 | 0 | 0 | 0 | 0 | 0 | 91.8195
5761 | 59.6368 | 0 | 0 | 0 | 0 | 29.8184 | 0 | 0 | 0 | 0 | 0 | 65.6411
5762 | 63.4346 | 0 | 0 | 0 | 0 | 31.7173 | 0 | 0 | 0 | 0 | 0 | 58.0534
5763 | 61.2844 | 0 | 0 | 0 | 0 | 30.6422 | 0 | 0 | 0 | 0 | 0 | 57.2481
5764 | 60.036 | 0 | 0 | 0 | 0 | 30.018 | 0 | 0 | 0 | 0 | 0 | 57.2472
5765 | 60.3208 | 0 | 0 | 0 | 0 | 30.1604 | 0 | 0 | 0 | 0 | 0 | 54.1423
5766 | 71.7812 | 0 | 0 | 0 | 0 | 35.8906 | 0 | 0 | 0 | 0 | 0 | 102.3398
5767 | 104.8579 | 0 | 42.9 | 0 | 56.3 | 52.429 | 192.6 | 0 | 6.4 | 0 | 0 | 86.8149
5768 | 165.3074 | 0.7 | 43 | 0 | 37.6 | 82.6537 | 130.6 | 69.2 | 39.5 | 0 | 0 | 169.6668
5769 | 200.3327 | 2.1 | 43.2 | 0 | 0 | 100.1663 | 0 | 68.8 | 45.2 | 0 | 0 | 91.9365
5770 | 219.9951 | 3.5 | 43.4 | 0 | 0 | 109.9975 | 0 | 83.6 | 60 | 0 | 0 | 122.601
5771 | 205.103 | 3.5 | 43.4 | 0 | 0 | 102.5515 | 0 | 93.2 | 73.6 | 0 | 0 | 158.5897
5772 | 194.3115 | 2.8 | 43.3 | 0 | 0 | 97.1557 | 0 | 111.5 | 87 | 0 | 0 | 68.5176
5773 | 189.3081 | 1.4 | 43.1 | 0 | 75.1 | 94.6541 | 243.8 | 106.5 | 92.9 | 0 | 0 | 164.3586
5774 | 184.9022 | 2.1 | 43.2 | 0 | 37.6 | 92.4511 | 185.9 | 119.3 | 93.5 | 0 | 0 | 185.7924
5775 | 179.1507 | 3.5 | 43.4 | 0 | 0 | 89.5754 | 0 | 156 | 113.3 | 0 | 0 | 110.7806
5776 | 143.9934 | 2.8 | 43.3 | 0 | 0 | 71.9967 | 0 | 157.1 | 131.6 | 0 | 0 | 138.8207
5777 | 103.9641 | 2.1 | 43.2 | 0 | 0 | 51.9821 | 0 | 144.2 | 125.9 | 0 | 0 | 105.5808
5778 | 86.5812 | 0.7 | 43 | 0 | 37.6 | 43.2906 | 198.6 | 112.1 | 107.8 | 0 | 0 | 126.1894
5779 | 74.1332 | 0 | 42.9 | 0 | 75.1 | 37.0666 | 211.3 | 9.6 | 28.3 | 0 | 0 | 127.9746
5780 | 64.881 | 0 | 42.9 | 0 | 75.1 | 32.4405 | 101.9 | 0 | 0 | 0 | 0 | 254.1432
5781 | 61.3343 | 0 | 42.9 | 0 | 75.1 | 30.6671 | 27 | 0 | 0 | 0 | 0 | 205.2665
5782 | 61.3916 | 0 | 42.9 | 0 | 93.9 | 30.6958 | 17.3 | 0 | 0 | 0 | 0 | 166.9996
5783 | 61.4037 | 0 | 0 | 0 | 0 | 30.7019 | 0 | 0 | 0 | 0 | 0 | 143.0451
5784 | 61.541 | 0 | 0 | 0 | 0 | 30.7705 | 0 | 0 | 0 | 0 | 0 | 107.3939
5785 | 60.8995 | 0 | 0 | 0 | 0 | 30.4497 | 0 | 0 | 0 | 0 | 0 | 76.1476
5786 | 60.4247 | 0 | 0 | 0 | 0 | 30.2123 | 0 | 0 | 0 | 0 | 0 | 68.8624
5787 | 60.2945 | 0 | 0 | 0 | 0 | 30.1472 | 0 | 0 | 0 | 0 | 0 | 53.2228
5788 | 59.7063 | 0 | 0 | 0 | 0 | 29.8531 | 0 | 0 | 0 | 0 | 0 | 50.2361
5789 | 62.644 | 0 | 0 | 0 | 0 | 31.322 | 0 | 0 | 0 | 0 | 0 | 58.518
5790 | 77.546 | 0 | 0 | 0 | 0 | 38.773 | 0 | 0 | 0 | 0 | 0 | 75.6739
5791 | 119.8904 | 0 | 42.9 | 0 | 56.3 | 59.9452 | 0 | 0 | 0 | 0 | 0 | 77.2092
5792 | 197.4777 | 0.7 | 43 | 0 | 37.6 | 98.7388 | 0 | 51.5 | 0 | 0 | 0 | 96.4691
5793 | 292.3378 | 2.1 | 43.2 | 0 | 0 | 146.1689 | 0 | 52.5 | 14 | 0 | 0 | 47.5944
5794 | 337.4114 | 3.5 | 43.4 | 0 | 0 | 168.7057 | 0 | 66.6 | 53.1 | 0 | 0 | 68.748
5795 | 337.6023 | 3.5 | 43.4 | 0 | 0 | 168.8012 | 0 | 79.5 | 99.3 | 0 | 0 | 117.8458
5796 | 298.5986 | 2.8 | 43.3 | 0 | 0 | 149.2993 | 0 | 103.6 | 91.3 | 0 | 0 | 122.7344
5797 | 270.3637 | 1.4 | 43.1 | 0 | 75.1 | 135.1818 | 142.5 | 101.9 | 103.3 | 0 | 0 | 138.6741
5798 | 275.3593 | 2.1 | 43.2 | 0 | 37.6 | 137.6797 | 123.5 | 117 | 132.4 | 0 | 0 | 136.8378
5799 | 247.0042 | 3.5 | 43.4 | 0 | 0 | 123.5021 | 0 | 152.6 | 155.1 | 0 | 0 | 77.0887
5800 | 183.7754 | 2.8 | 43.3 | 0 | 0 | 91.8877 | 0 | 166 | 159.7 | 0 | 0 | 94.203
5801 | 130.1761 | 2.1 | 43.2 | 0 | 0 | 65.0881 | 0 | 172.1 | 149 | 0 | 0 | 82.6713
5802 | 113.3008 | 0.7 | 43 | 0 | 37.6 | 56.6504 | 165.1 | 143.2 | 143.9 | 0 | 0 | 111.1483
5803 | 76.8998 | 0 | 42.9 | 0 | 75.1 | 38.4499 | 198.5 | 25.5 | 50 | 0 | 0 | 326.6863
5804 | 61.536 | 0 | 42.9 | 0 | 75.1 | 30.768 | 104.1 | 0.1 | 1.4 | 0 | 0 | 179.0835
5805 | 60.6063 | 0 | 42.9 | 0 | 75.1 | 30.3031 | 32.5 | 0 | 0 | 0 | 0 | 219.5282
5806 | 62.3462 | 0 | 42.9 | 0 | 93.9 | 31.1731 | 13.2 | 0 | 0 | 0 | 0 | 196.3156
5807 | 61.6619 | 0 | 0 | 0 | 0 | 30.8309 | 0 | 0 | 0 | 0 | 0 | 143.9307
5808 | 62.0087 | 0 | 0 | 0 | 0 | 31.0043 | 0 | 0 | 0 | 0 | 0 | 97.5533
5809 | 59.7834 | 0 | 0 | 0 | 0 | 29.8917 | 0 | 0 | 0 | 0 | 0 | 52.306
5810 | 59.7875 | 0 | 0 | 0 | 0 | 29.8937 | 0 | 0 | 0 | 0 | 0 | 51.9596
5811 | 60.4107 | 0 | 0 | 0 | 0 | 30.2054 | 0 | 0 | 0 | 0 | 0 | 48.6282
5812 | 57.3803 | 0 | 0 | 0 | 0 | 28.6901 | 0 | 0 | 0 | 0 | 0 | 48.6286
5813 | 58.0714 | 0 | 0 | 0 | 0 | 29.0357 | 0 | 0 | 0 | 0 | 0 | 48.2838
5814 | 66.4372 | 0 | 0 | 0 | 0 | 33.2186 | 0 | 0 | 0 | 0 | 0 | 63.9232
5815 | 106.8734 | 0 | 42.9 | 0 | 56.3 | 53.4367 | 0 | 0 | 0 | 0 | 0 | 123.6196
5816 | 165.5634 | 0.7 | 43 | 0 | 37.6 | 82.7817 | 0 | 80.1 | 10.4 | 0 | 0 | 79.7178
5817 | 276.3554 | 2.1 | 43.2 | 0 | 0 | 138.1777 | 0 | 80.1 | 65 | 0 | 0 | 76.1462
5818 | 291.4688 | 3.5 | 43.4 | 0 | 0 | 145.7344 | 0 | 104.1 | 147.9 | 0 | 0 | 153.1471
5819 | 272.6367 | 3.5 | 43.4 | 0 | 0 | 136.3183 | 0 | 126.4 | 227.8 | 0 | 0 | 156.2167
5820 | 266.3945 | 2.8 | 43.3 | 0 | 0 | 133.1973 | 0 | 141.6 | 308.5 | 0 | 0 | 109.5747
5821 | 245.6728 | 1.4 | 43.1 | 0 | 75.1 | 122.8364 | 537.5 | 126.8 | 375.5 | 0 | 0 | 99.5875
5822 | 235.2901 | 2.1 | 43.2 | 0 | 37.6 | 117.645 | 542 | 146.1 | 425.5 | 0 | 0 | 159.8764
5823 | 208.4313 | 3.5 | 43.4 | 0 | 0 | 104.2156 | 14.8 | 193.5 | 468.3 | 0 | 0 | 96.9562
5824 | 170.8547 | 2.8 | 43.3 | 0 | 0 | 85.4273 | 64.6 | 204.3 | 483 | 0 | 0 | 90.9806
5825 | 144.6839 | 2.1 | 43.2 | 0 | 0 | 72.342 | 104.3 | 214.3 | 477.2 | 0 | 0 | 118.5235
5826 | 100.7059 | 0.7 | 43 | 0 | 37.6 | 50.353 | 906.6 | 158.4 | 460.6 | 0 | 0 | 112.605
5827 | 74.7294 | 0 | 42.9 | 0 | 75.1 | 37.3647 | 868.3 | 38.9 | 324.6 | 0 | 0 | 162.6848
5828 | 60.0029 | 0 | 42.9 | 0 | 75.1 | 30.0014 | 692.9 | 9 | 194.8 | 0 | 0 | 171.6565
5829 | 57.0391 | 0 | 42.9 | 0 | 75.1 | 28.5195 | 576.7 | 5.7 | 154.3 | 0 | 0 | 216.7754
5830 | 60.0106 | 0 | 42.9 | 0 | 93.9 | 30.0053 | 499.6 | 1.2 | 111.1 | 0 | 0 | 164.6086
5831 | 56.9126 | 0 | 0 | 0 | 0 | 28.4563 | 0 | 0 | 0 | 0 | 0 | 140.4021
5832 | 56.7921 | 0 | 0 | 0 | 0 | 28.396 | 0 | 0 | 0 | 0 | 0 | 108.0052
5833 | 60.7894 | 0 | 0 | 0 | 0 | 30.3947 | 0 | 0 | 0 | 0 | 0 | 87.4089
5834 | 59.11 | 0 | 0 | 0 | 0 | 29.555 | 0 | 0 | 0 | 0 | 0 | 77.2097
5835 | 58.6628 | 0 | 0 | 0 | 0 | 29.3314 | 0 | 0 | 0 | 0 | 0 | 56.9003
5836 | 58.7976 | 0 | 0 | 0 | 0 | 29.3988 | 0 | 0 | 0 | 0 | 0 | 55.6336
5837 | 59.4118 | 0 | 0 | 0 | 0 | 29.7059 | 0 | 0 | 0 | 0 | 0 | 72.3193
5838 | 64.8355 | 0 | 0 | 0 | 0 | 32.4177 | 0 | 0 | 0 | 0 | 0 | 88.0045
5839 | 79.5618 | 0 | 42.9 | 0 | 56.3 | 39.7809 | 63.1 | 0 | 0 | 0 | 0 | 74.9728
5840 | 87.7422 | 0 | 42.9 | 0 | 37.6 | 43.8711 | 24.3 | 0 | 0 | 0 | 0 | 156.9138
5841 | 84.969 | 0 | 42.9 | 0 | 0 | 42.4845 | 0 | 0 | 0 | 0 | 0 | 145.8983
5842 | 79.7304 | 0 | 42.9 | 0 | 0 | 39.8652 | 0 | 0.1 | 0 | 0 | 0 | 63.809
5843 | 79.4412 | 0 | 42.9 | 0 | 0 | 39.7206 | 0 | 2 | 8.1 | 0 | 0 | 48.8593
5844 | 78.4919 | 0 | 42.9 | 0 | 0 | 39.246 | 0 | 7.6 | 13.7 | 0 | 0 | 117.7134
5845 | 73.6212 | 0 | 42.9 | 0 | 75.1 | 36.8106 | 95.2 | 13 | 21.3 | 0 | 0 | 188.0739
5846 | 71.5902 | 0 | 42.9 | 0 | 37.6 | 35.7951 | 98.7 | 15.3 | 39.4 | 0 | 0 | 207.3694
5847 | 73.614 | 0 | 42.9 | 0 | 0 | 36.807 | 0 | 8.6 | 56.5 | 0 | 0 | 130.6837
5848 | 77.3226 | 0 | 42.9 | 0 | 0 | 38.6613 | 0 | 4.6 | 85.7 | 0 | 0 | 186.6229
5849 | 77.2584 | 0 | 42.9 | 0 | 0 | 38.6292 | 0 | 2.3 | 116.6 | 0 | 0 | 201.5193
5850 | 84.4626 | 0 | 42.9 | 0 | 37.6 | 42.2313 | 293.5 | 0.4 | 140.6 | 0 | 0 | 324.0049
5851 | 67.0914 | 0 | 42.9 | 0 | 75.1 | 33.5457 | 318.3 | 0 | 109.8 | 0 | 0 | 437.7639
5852 | 59.2178 | 0 | 42.9 | 0 | 75.1 | 29.6089 | 205.2 | 0 | 29.3 | 0 | 0 | 321.3302
5853 | 56.365 | 0 | 42.9 | 0 | 75.1 | 28.1825 | 130.2 | 0 | 16.4 | 0 | 0 | 233.6024
5854 | 56.1781 | 0 | 42.9 | 0 | 93.9 | 28.0891 | 88.7 | 0 | 4.8 | 0 | 0 | 242.4319
5855 | 56.493 | 0 | 0 | 0 | 0 | 28.2465 | 0 | 0 | 0 | 0 | 0 | 164.5598
5856 | 56.7363 | 0 | 0 | 0 | 0 | 28.3681 | 0 | 0 | 0 | 0 | 0 | 95.8714
5857 | 55.292 | 0 | 0 | 0 | 0 | 27.646 | 0 | 0 | 0 | 0 | 0 | 66.9089
5858 | 58.6438 | 0 | 0 | 0 | 0 | 29.3219 | 0 | 0 | 0 | 0 | 0 | 57.7078
5859 | 60.4897 | 0 | 0 | 0 | 0 | 30.2449 | 0 | 0 | 0 | 0 | 0 | 56.5524
5860 | 55.1067 | 0 | 0 | 0 | 0 | 27.5534 | 0 | 0 | 0 | 0 | 0 | 51.27
5861 | 58.7808 | 0 | 0 | 0 | 0 | 29.3904 | 0 | 0 | 0 | 0 | 0 | 60.0109
5862 | 64.0396 | 0 | 0 | 0 | 0 | 32.0198 | 0 | 0 | 0 | 0 | 0 | 87.7625
5863 | 91.8824 | 0 | 42.9 | 0 | 56.3 | 45.9412 | 0 | 0 | 0 | 0 | 0 | 103.6582
5864 | 94.3286 | 0 | 42.9 | 0 | 37.6 | 47.1643 | 0 | 0 | 0 | 0 | 0 | 69.0925
5865 | 88.5421 | 0 | 42.9 | 0 | 0 | 44.271 | 0 | 0 | 0 | 0 | 0 | 119.1771
5866 | 85.6121 | 0 | 42.9 | 0 | 0 | 42.806 | 0 | 0 | 0 | 0 | 0 | 139.28
5867 | 84.7852 | 0 | 42.9 | 0 | 0 | 42.3926 | 0 | 0 | 0 | 0 | 0 | 124.6381
5868 | 78.35 | 0 | 42.9 | 0 | 0 | 39.175 | 0 | 0 | 3.6 | 0 | 0 | 140.1847
5869 | 74.2342 | 0 | 42.9 | 0 | 75.1 | 37.1171 | 45.7 | 3.1 | 7.5 | 0 | 0 | 147.8994
5870 | 74.5832 | 0 | 42.9 | 0 | 37.6 | 37.2916 | 41.3 | 9.3 | 15.3 | 0 | 0 | 116.7561
5871 | 75.3381 | 0 | 42.9 | 0 | 0 | 37.6691 | 0 | 17.4 | 25.7 | 0 | 0 | 130.517
5872 | 75.6155 | 0 | 42.9 | 0 | 0 | 37.8078 | 0 | 23.7 | 44.1 | 0 | 0 | 76.3805
5873 | 87.2655 | 0 | 42.9 | 0 | 0 | 43.6327 | 0 | 31 | 62.5 | 0 | 0 | 107.5196
5874 | 90.313 | 0 | 42.9 | 0 | 37.6 | 45.1565 | 201 | 37.8 | 86.7 | 0 | 0 | 149.6721
5875 | 76.0063 | 0 | 42.9 | 0 | 75.1 | 38.0032 | 220.5 | 31 | 74.1 | 0 | 0 | 250.4693
5876 | 64.0477 | 0 | 42.9 | 0 | 75.1 | 32.0238 | 114.6 | 0 | 7.1 | 0 | 0 | 249.0115
5877 | 57.3905 | 0 | 42.9 | 0 | 75.1 | 28.6953 | 35.9 | 0 | 1.3 | 0 | 0 | 301.9368
5878 | 58.1641 | 0 | 42.9 | 0 | 93.9 | 29.082 | 11.2 | 0 | 0 | 0 | 0 | 190.9609
5879 | 58.4188 | 0 | 0 | 0 | 0 | 29.2094 | 0 | 0 | 0 | 0 | 0 | 164.343
5880 | 58.545 | 0 | 0 | 0 | 0 | 29.2725 | 0 | 0 | 0 | 0 | 0 | 108.7242
5881 | 55.5697 | 0 | 0 | 0 | 0 | 27.7849 | 0 | 0 | 0 | 0 | 0 | 84.0891
5882 | 57.3694 | 0 | 0 | 0 | 0 | 28.6847 | 0 | 0 | 0 | 0 | 0 | 65.8704
5883 | 58.8379 | 0 | 0 | 0 | 0 | 29.4189 | 0 | 0 | 0 | 0 | 0 | 62.5451
5884 | 55.8335 | 0 | 0 | 0 | 0 | 27.9167 | 0 | 0 | 0 | 0 | 0 | 65.525
5885 | 56.0244 | 0 | 0 | 0 | 0 | 28.0122 | 0 | 0 | 0 | 0 | 0 | 61.1647
5886 | 74.2057 | 0 | 0 | 0 | 0 | 37.1028 | 0 | 0 | 0 | 0 | 0 | 63.5791
5887 | 123.6268 | 0 | 42.9 | 0 | 56.3 | 61.8134 | 0 | 0 | 0 | 0 | 0 | 69.2077
5888 | 220.2446 | 0.7 | 43 | 0 | 37.6 | 110.1223 | 0 | 50.3 | 0 | 0 | 0 | 77.6803
5889 | 310.8873 | 2.1 | 43.2 | 0 | 0 | 155.4436 | 0 | 63.2 | 1.8 | 0 | 0 | 109.9362
5890 | 370.0893 | 3.5 | 43.4 | 0 | 0 | 185.0447 | 0 | 85.8 | 21.5 | 0 | 0 | 95.87
5891 | 398.2262 | 3.5 | 43.4 | 0 | 0 | 199.1131 | 0 | 111.4 | 56.2 | 0 | 0 | 93.7255
5892 | 378.804 | 2.8 | 43.3 | 0 | 0 | 189.402 | 0 | 148.1 | 155.1 | 0 | 0 | 75.2054
5893 | 350.8667 | 1.4 | 43.1 | 0 | 75.1 | 175.4333 | 210.7 | 140.2 | 208.7 | 0 | 0 | 117.7008
5894 | 313.6633 | 2.1 | 43.2 | 0 | 37.6 | 156.8316 | 145.2 | 157.8 | 176 | 0 | 0 | 110.5368
5895 | 296.3302 | 3.5 | 43.4 | 0 | 0 | 148.1651 | 0 | 203.9 | 140.2 | 0 | 0 | 139.6688
5896 | 246.0304 | 2.8 | 43.3 | 0 | 0 | 123.0152 | 0 | 208.2 | 108.8 | 0 | 0 | 177.1056
5897 | 176.7482 | 2.1 | 43.2 | 0 | 0 | 88.3741 | 0 | 193.1 | 80.6 | 0 | 0 | 91.4603
5898 | 136.9045 | 0.7 | 43 | 0 | 37.6 | 68.4523 | 38.3 | 152.3 | 60.8 | 0 | 0 | 121.9574
5899 | 116.992 | 0 | 42.9 | 0 | 75.1 | 58.496 | 46.2 | 33.8 | 7.6 | 0 | 0 | 171.7278
5900 | 82.4806 | 0 | 42.9 | 0 | 75.1 | 41.2403 | 7.5 | 4.5 | 0 | 0 | 0 | 200.4637
5901 | 63.1644 | 0 | 42.9 | 0 | 75.1 | 31.5822 | 0 | 1.5 | 0 | 0 | 0 | 235.8776
5902 | 57.4742 | 0 | 42.9 | 0 | 93.9 | 28.7371 | 0 | 0 | 0 | 0 | 0 | 156.4329
5903 | 58.6711 | 0 | 0 | 0 | 0 | 29.3356 | 0 | 0 | 0 | 0 | 0 | 94.0817
5904 | 57.9354 | 0 | 0 | 0 | 0 | 28.9677 | 0 | 0 | 0 | 0 | 0 | 74.3943
5905 | 55.9943 | 0 | 0 | 0 | 0 | 27.9972 | 0 | 0 | 0 | 0 | 0 | 56.8991
5906 | 56.8652 | 0 | 0 | 0 | 0 | 28.4326 | 0 | 0 | 0 | 0 | 0 | 45.6543
5907 | 55.7678 | 0 | 0 | 0 | 0 | 27.8839 | 0 | 0 | 0 | 0 | 0 | 44.8639
5908 | 57.3388 | 0 | 0 | 0 | 0 | 28.6694 | 0 | 0 | 0 | 0 | 0 | 47.2493
5909 | 59.1286 | 0 | 0 | 0 | 0 | 29.5643 | 0 | 0 | 0 | 0 | 0 | 58.7481
5910 | 85.8213 | 0 | 0 | 0 | 0 | 42.9106 | 0 | 0 | 0 | 0 | 0 | 93.846
5911 | 116.2956 | 0 | 42.9 | 0 | 56.3 | 58.1478 | 0 | 0 | 0 | 0 | 0 | 99.1118
5912 | 177.5704 | 0.7 | 43 | 0 | 37.6 | 88.7852 | 0 | 79.1 | 0 | 0 | 0 | 80.8992
5913 | 274.8365 | 2.1 | 43.2 | 0 | 0 | 137.4182 | 0 | 79.9 | 0 | 0 | 0 | 110.5378
5914 | 295.4888 | 3.5 | 43.4 | 0 | 0 | 147.7444 | 0 | 109.6 | 6 | 0 | 0 | 90.6244
5915 | 270.3968 | 3.5 | 43.4 | 0 | 0 | 135.1984 | 0 | 131.9 | 27.8 | 0 | 0 | 95.3957
5916 | 261.7928 | 2.8 | 43.3 | 0 | 0 | 130.8964 | 0 | 142.6 | 72.6 | 0 | 0 | 120.8445
5917 | 247.5661 | 1.4 | 43.1 | 0 | 75.1 | 123.783 | 96.4 | 128.5 | 138 | 0 | 0 | 103.1788
5918 | 239.2871 | 2.1 | 43.2 | 0 | 37.6 | 119.6436 | 123.4 | 143.8 | 187.9 | 0 | 0 | 190.8919
5919 | 232.3474 | 3.5 | 43.4 | 0 | 0 | 116.1737 | 0 | 189.2 | 225.6 | 0 | 0 | 168.0851
5920 | 203.8478 | 2.8 | 43.3 | 0 | 0 | 101.9239 | 0 | 200.4 | 257.4 | 0 | 0 | 132.6222
5921 | 154.9978 | 2.1 | 43.2 | 0 | 0 | 77.4989 | 0 | 191.7 | 286.6 | 0 | 0 | 117.9977
5922 | 129.0347 | 0.7 | 43 | 0 | 37.6 | 64.5173 | 383.5 | 152.4 | 285.4 | 0 | 0 | 191.1109
5923 | 91.3537 | 0 | 42.9 | 0 | 75.1 | 45.6768 | 399.5 | 35.3 | 177.5 | 0 | 0 | 279.3029
5924 | 67.8523 | 0 | 42.9 | 0 | 75.1 | 33.9261 | 264.2 | 6.5 | 64.2 | 0 | 0 | 159.1051
5925 | 62.2464 | 0 | 42.9 | 0 | 75.1 | 31.1232 | 166 | 3.6 | 44.1 | 0 | 0 | 164.2796
5926 | 59.2643 | 0 | 42.9 | 0 | 93.9 | 29.6322 | 125.3 | 0.3 | 25.6 | 0 | 0 | 196.9418
5927 | 58.1241 | 0 | 0 | 0 | 0 | 29.0621 | 0 | 0 | 0 | 0 | 0 | 227.1295
5928 | 58.9928 | 0 | 0 | 0 | 0 | 29.4964 | 0 | 0 | 0 | 0 | 0 | 84.2047
5929 | 57.6412 | 0 | 0 | 0 | 0 | 28.8206 | 0 | 0 | 0 | 0 | 0 | 56.0926
5930 | 58.4226 | 0 | 0 | 0 | 0 | 29.2113 | 0 | 0 | 0 | 0 | 0 | 50.2369
5931 | 59.9756 | 0 | 0 | 0 | 0 | 29.9878 | 0 | 0 | 0 | 0 | 0 | 46.5629
5932 | 58.8565 | 0 | 0 | 0 | 0 | 29.4282 | 0 | 0 | 0 | 0 | 0 | 49.0886
5933 | 58.9191 | 0 | 0 | 0 | 0 | 29.4595 | 0 | 0 | 0 | 0 | 0 | 54.8296
5934 | 69.4918 | 0 | 0 | 0 | 0 | 34.7459 | 0 | 0 | 0 | 0 | 0 | 78.6479
5935 | 97.514 | 0 | 42.9 | 0 | 56.3 | 48.757 | 0 | 0.1 | 0 | 0 | 0 | 66.9093
5936 | 154.7068 | 0.7 | 43 | 0 | 37.6 | 77.3534 | 0 | 116.9 | 0.2 | 0 | 0 | 61.3945
5937 | 221.8859 | 2.1 | 43.2 | 0 | 0 | 110.943 | 0 | 125.4 | 5.4 | 0 | 0 | 93.4865
5938 | 285.624 | 3.5 | 43.4 | 0 | 0 | 142.812 | 0 | 161.3 | 23.8 | 0 | 0 | 199.2221
5939 | 288.236 | 3.5 | 43.4 | 0 | 0 | 144.118 | 0 | 190.5 | 59.7 | 0 | 0 | 124.3889
5940 | 270.1601 | 2.8 | 43.3 | 0 | 0 | 135.08 | 0 | 209.5 | 104.5 | 0 | 0 | 128.3605
5941 | 268.2469 | 1.4 | 43.1 | 0 | 75.1 | 134.1235 | 229.5 | 174.5 | 182.2 | 0 | 0 | 163.5061
5942 | 265.6222 | 2.1 | 43.2 | 0 | 37.6 | 132.8111 | 258.7 | 169.7 | 233.2 | 0 | 0 | 211.4869
5943 | 263.3442 | 3.5 | 43.4 | 0 | 0 | 131.6721 | 0 | 184.6 | 266.1 | 0 | 0 | 85.0431
5944 | 240.4881 | 2.8 | 43.3 | 0 | 0 | 120.244 | 0 | 164.5 | 280 | 0 | 0 | 112.9689
5945 | 188.7735 | 2.1 | 43.2 | 0 | 0 | 94.3867 | 0 | 142.1 | 268.4 | 0 | 0 | 235.5322
5946 | 160.6855 | 0.7 | 43 | 0 | 37.6 | 80.3428 | 368.9 | 119.6 | 215.9 | 0 | 0 | 99.2311
5947 | 127.9608 | 0 | 42.9 | 0 | 75.1 | 63.9804 | 345.2 | 5.8 | 90.9 | 0 | 0 | 254.8831
5948 | 79.2844 | 0 | 42.9 | 0 | 75.1 | 39.6422 | 229.3 | 0 | 25.3 | 0 | 0 | 179.3282
5949 | 63.0466 | 0 | 42.9 | 0 | 75.1 | 31.5233 | 133.1 | 0 | 13.7 | 0 | 0 | 191.0789
5950 | 66.3773 | 0 | 42.9 | 0 | 93.9 | 33.1887 | 89.1 | 0 | 5.4 | 0 | 0 | 158.7394
5951 | 62.547 | 0 | 0 | 0 | 0 | 31.2735 | 0 | 0 | 0 | 0 | 0 | 91.1019
5952 | 62.5687 | 0 | 0 | 0 | 0 | 31.2844 | 0 | 0 | 0 | 0 | 0 | 93.8467
5953 | 58.7219 | 0 | 0 | 0 | 0 | 29.361 | 0 | 0 | 0 | 0 | 0 | 81.9655
5954 | 58.682 | 0 | 0 | 0 | 0 | 29.341 | 0 | 0 | 0 | 0 | 0 | 49.2042
5955 | 61.0739 | 0 | 0 | 0 | 0 | 30.537 | 0 | 0 | 0 | 0 | 0 | 44.8637
5956 | 59.5652 | 0 | 0 | 0 | 0 | 29.7826 | 0 | 0 | 0 | 0 | 0 | 50.9266
5957 | 60.1129 | 0 | 0 | 0 | 0 | 30.0564 | 0 | 0 | 0 | 0 | 0 | 51.5011
5958 | 75.728 | 0 | 0 | 0 | 0 | 37.864 | 0 | 0 | 0 | 0 | 0 | 83.3842
5959 | 93.4953 | 0 | 42.9 | 0 | 56.3 | 46.7476 | 0 | 0 | 0 | 0 | 0 | 88.1228
5960 | 153.04 | 0.7 | 43 | 0 | 37.6 | 76.52 | 0 | 24.3 | 0 | 0 | 0 | 53.4519
5961 | 229.3631 | 2.1 | 43.2 | 0 | 0 | 114.6816 | 0 | 18.1 | 0 | 0 | 0 | 133.2854
5962 | 274.2129 | 3.5 | 43.4 | 0 | 0 | 137.1065 | 0 | 25.5 | 0 | 0 | 0 | 178.9302
5963 | 273.8038 | 3.5 | 43.4 | 0 | 0 | 136.9019 | 0 | 35.2 | 1.7 | 0 | 0 | 103.0607
5964 | 250.3198 | 2.8 | 43.3 | 0 | 0 | 125.1599 | 0 | 58.2 | 11.9 | 0 | 0 | 138.1778
5965 | 235.3933 | 1.4 | 43.1 | 0 | 75.1 | 117.6966 | 11.6 | 50 | 24.7 | 0 | 0 | 159.1831
5966 | 238.6468 | 2.1 | 43.2 | 0 | 37.6 | 119.3234 | 9.8 | 50.1 | 39.4 | 0 | 0 | 117.4914
5967 | 227.2237 | 3.5 | 43.4 | 0 | 0 | 113.6119 | 0 | 59.7 | 48.8 | 0 | 0 | 88.2406
5968 | 195.6001 | 2.8 | 43.3 | 0 | 0 | 97.8001 | 0 | 54.8 | 51.4 | 0 | 0 | 169.5753
5969 | 151.2444 | 2.1 | 43.2 | 0 | 0 | 75.6222 | 0 | 60.7 | 51.5 | 0 | 0 | 181.2949
5970 | 127.2185 | 0.7 | 43 | 0 | 37.6 | 63.6093 | 14.5 | 51.5 | 40.8 | 0 | 0 | 128.2342
5971 | 103.8832 | 0 | 42.9 | 0 | 75.1 | 51.9416 | 20.1 | 0 | 1.8 | 0 | 0 | 279.1005
5972 | 79.4861 | 0 | 42.9 | 0 | 75.1 | 39.7431 | 1.3 | 0 | 0 | 0 | 0 | 253.5689
5973 | 60.2998 | 0 | 42.9 | 0 | 75.1 | 30.1499 | 0 | 0 | 0 | 0 | 0 | 261.5607
5974 | 62.2179 | 0 | 42.9 | 0 | 93.9 | 31.1089 | 0 | 0 | 0 | 0 | 0 | 187.22
5975 | 63.151 | 0 | 0 | 0 | 0 | 31.5755 | 0 | 0 | 0 | 0 | 0 | 103.54
5976 | 61.947 | 0 | 0 | 0 | 0 | 30.9735 | 0 | 0 | 0 | 0 | 0 | 77.0905
5977 | 60.248 | 0 | 0 | 0 | 0 | 30.124 | 0 | 0 | 0 | 0 | 0 | 57.7075
5978 | 62.3552 | 0 | 0 | 0 | 0 | 31.1776 | 0 | 0 | 0 | 0 | 0 | 60.2415
5979 | 58.0138 | 0 | 0 | 0 | 0 | 29.0069 | 0 | 0 | 0 | 0 | 0 | 47.4789
5980 | 62.1522 | 0 | 0 | 0 | 0 | 31.0761 | 0 | 0 | 0 | 0 | 0 | 49.4345
5981 | 61.5859 | 0 | 0 | 0 | 0 | 30.793 | 0 | 0 | 0 | 0 | 0 | 57.5933
5982 | 77.1723 | 0 | 0 | 0 | 0 | 38.5861 | 0 | 0 | 0 | 0 | 0 | 84.2058
5983 | 113.7893 | 0 | 42.9 | 0 | 56.3 | 56.8946 | 0 | 0 | 0 | 0 | 0 | 95.3943
5984 | 191.6812 | 0.7 | 43 | 0.2 | 37.6 | 95.8406 | 0 | 0 | 0 | 0 | 0 | 129.3158
5985 | 288.0882 | 2.1 | 43.2 | 0 | 0 | 144.0441 | 0 | 0 | 0 | 0 | 0 | 106.5495
5986 | 331.7835 | 3.5 | 43.4 | 0 | 0 | 165.8918 | 0 | 0 | 0 | 0 | 0 | 125.5852
5987 | 308.5963 | 3.5 | 43.4 | 0 | 0 | 154.2982 | 0 | 0 | 0 | 0 | 0 | 108.6081
5988 | 304.7536 | 2.8 | 43.3 | 0 | 0 | 152.3768 | 0 | 0 | 0 | 0 | 0 | 132.6077
5989 | 287.5545 | 1.4 | 43.1 | 0 | 75.1 | 143.7772 | 0 | 0 | 4.6 | 0 | 0 | 127.4983
5990 | 265.5193 | 2.1 | 43.2 | 0 | 37.6 | 132.7596 | 0 | 0 | 19.3 | 0 | 0 | 156.4539
5991 | 255.2872 | 3.5 | 43.4 | 0 | 0 | 127.6436 | 0 | 0 | 31.3 | 0 | 0 | 189.0014
5992 | 221.5422 | 2.8 | 43.3 | 0 | 0 | 110.7711 | 0 | 0 | 39.2 | 0 | 0 | 107.3983
5993 | 161.1547 | 2.1 | 43.2 | 0 | 0 | 80.5774 | 0 | 0 | 46.2 | 0 | 0 | 123.4953
5994 | 153.1141 | 0.7 | 43 | 0 | 37.6 | 76.5571 | 0 | 0 | 34.1 | 0 | 0 | 193.911
5995 | 136.7127 | 0 | 42.9 | 0 | 75.1 | 68.3564 | 0 | 0 | 0 | 0 | 0 | 256.0959
5996 | 80.4391 | 0 | 42.9 | 0 | 75.1 | 40.2196 | 0 | 0 | 0 | 0 | 0 | 206.6573
5997 | 61.382 | 0 | 42.9 | 0 | 75.1 | 30.691 | 0 | 0 | 0 | 0 | 0 | 220.3169
5998 | 58.712 | 0 | 42.9 | 0 | 93.9 | 29.356 | 0 | 0 | 0 | 0 | 0 | 162.216
5999 | 58.2809 | 0 | 0 | 0 | 0 | 29.1405 | 0 | 0 | 0 | 0 | 0 | 143.6811
6000 | 58.8162 | 0 | 0 | 0 | 0 | 29.4081 | 0 | 0 | 0 | 0 | 0 | 111.8758
6001 | 57.6828 | 0 | 0 | 0 | 0 | 28.8414 | 0 | 0 | 0 | 0 | 0 | 98.518
6002 | 57.428 | 0 | 0 | 0 | 0 | 28.714 | 0 | 0 | 0 | 0 | 0 | 81.136
6003 | 58.1297 | 0 | 0 | 0 | 0 | 29.0648 | 0 | 0 | 0 | 0 | 0 | 69.5547
6004 | 60.2136 | 0 | 0 | 0 | 0 | 30.1068 | 0 | 0 | 0 | 0 | 0 | 62.1999
6005 | 58.1985 | 0 | 0 | 0 | 0 | 29.0992 | 0 | 0 | 0 | 0 | 0 | 73.4703
6006 | 64.3793 | 0 | 0 | 0 | 0 | 32.1896 | 0 | 0 | 0 | 0 | 0 | 74.9732
6007 | 82.5754 | 0 | 42.9 | 0 | 56.3 | 41.2877 | 0 | 0 | 0 | 0 | 0 | 74.5099
6008 | 94.5009 | 0 | 42.9 | 0 | 37.6 | 47.2505 | 0 | 0 | 0 | 0 | 0 | 60.5878
6009 | 96.9063 | 0 | 42.9 | 0 | 0 | 48.4531 | 0 | 0 | 0 | 0 | 0 | 76.8533
6010 | 95.8987 | 0 | 42.9 | 0 | 0 | 47.9493 | 0 | 0 | 0 | 0 | 0 | 69.7837
6011 | 91.5759 | 0 | 42.9 | 0 | 0 | 45.788 | 0 | 0 | 0 | 0 | 0 | 65.0694
6012 | 93.9558 | 0 | 42.9 | 0 | 0 | 46.9779 | 0 | 0 | 0 | 0 | 0 | 115.6367
6013 | 92.6572 | 0 | 42.9 | 0 | 75.1 | 46.3286 | 0 | 0 | 0 | 0 | 0 | 68.0576
6014 | 93.5619 | 0 | 42.9 | 0 | 37.6 | 46.7809 | 0 | 0 | 0 | 0 | 0 | 96.109
6015 | 93.1292 | 0 | 42.9 | 0 | 0 | 46.5646 | 0 | 0 | 0 | 0 | 0 | 79.7143
6016 | 95.2122 | 0 | 42.9 | 0 | 0 | 47.6061 | 0 | 0 | 0 | 0 | 0 | 84.9251
6017 | 92.6262 | 0 | 42.9 | 0 | 0 | 46.3131 | 0 | 0 | 0 | 0 | 0 | 70.9361
6018 | 89.2236 | 0 | 42.9 | 0 | 37.6 | 44.6118 | 0 | 0 | 0 | 0 | 0 | 150.8099
6019 | 84.0349 | 0 | 42.9 | 0 | 75.1 | 42.0174 | 0 | 0 | 0 | 0 | 0 | 270.1336
6020 | 70.0443 | 0 | 42.9 | 0 | 75.1 | 35.0222 | 0 | 0 | 0 | 0 | 0 | 255.7959
6021 | 60.1625 | 0 | 42.9 | 0 | 75.1 | 30.0812 | 0 | 0 | 0 | 0 | 0 | 131.0619
6022 | 57.225 | 0 | 42.9 | 0 | 93.9 | 28.6125 | 0 | 0 | 0 | 0 | 0 | 154.3344
6023 | 56.6346 | 0 | 0 | 0 | 0 | 28.3173 | 0 | 0 | 0 | 0 | 0 | 107.1539
6024 | 57.1289 | 0 | 0 | 0 | 0 | 28.5645 | 0 | 0 | 0 | 0 | 0 | 94.3236
6025 | 57.4875 | 0 | 0 | 0 | 0 | 28.7438 | 0 | 0 | 0 | 0 | 0 | 66.6776
6026 | 59.4515 | 0 | 0 | 0 | 0 | 29.7258 | 0 | 0 | 0 | 0 | 0 | 59.0937
6027 | 55.8657 | 0 | 0 | 0 | 0 | 27.9329 | 0 | 0 | 0 | 0 | 0 | 48.7443
6028 | 56.6591 | 0 | 0 | 0 | 0 | 28.3296 | 0 | 0 | 0 | 0 | 0 | 52.6501
6029 | 55.9171 | 0 | 0 | 0 | 0 | 27.9586 | 0 | 0 | 0 | 0 | 0 | 60.3584
6030 | 55.9736 | 0 | 0 | 0 | 0 | 27.9868 | 0 | 0 | 0 | 0 | 0 | 99.592
6031 | 79.7657 | 0 | 42.9 | 23.9 | 56.3 | 39.8828 | 0 | 0 | 0 | 0 | 84.3 | 118.159
6032 | 87.7852 | 0 | 42.9 | 9 | 37.6 | 43.8926 | 0 | 0 | 0 | 0 | 54.1 | 148.6022
6033 | 88.2043 | 0 | 42.9 | 0 | 0 | 44.1021 | 0 | 0 | 0 | 0 | 0 | 111.6316
6034 | 85.3303 | 0 | 42.9 | 0 | 0 | 42.6652 | 0 | 0 | 0 | 0 | 0 | 119.9657
6035 | 81.5403 | 0 | 42.9 | 0 | 0 | 40.7702 | 0 | 0 | 0 | 0 | 0 | 126.043
6036 | 83.1088 | 0 | 42.9 | 0 | 0 | 41.5544 | 0 | 0 | 0 | 0 | 0 | 135.8087
6037 | 86.1879 | 0 | 42.9 | 0 | 75.1 | 43.0939 | 0 | 0 | 0 | 0 | 0 | 135.2739
6038 | 84.6008 | 0 | 42.9 | 0 | 37.6 | 42.3004 | 0 | 0 | 0 | 0 | 0 | 115.2591
6039 | 88.3518 | 0 | 42.9 | 0 | 0 | 44.1759 | 0 | 0 | 0 | 0 | 0 | 124.5193
6040 | 85.4407 | 0 | 42.9 | 0 | 0 | 42.7203 | 0 | 0 | 0 | 0 | 0 | 89.5491
6041 | 85.4596 | 0 | 42.9 | 0 | 0 | 42.7298 | 0 | 0 | 0 | 0 | 0 | 84.5681
6042 | 80.0787 | 0 | 42.9 | 0 | 37.6 | 40.0394 | 0 | 0 | 0 | 0 | 0 | 120.4129
6043 | 66.616 | 0 | 42.9 | 0 | 75.1 | 33.308 | 0 | 0 | 0 | 0 | 0 | 177.0275
6044 | 63.7988 | 0 | 42.9 | 0 | 75.1 | 31.8994 | 0 | 0 | 0 | 0 | 0 | 333.2472
6045 | 61.8401 | 0 | 42.9 | 0 | 75.1 | 30.92 | 0 | 0 | 0 | 0 | 0 | 369.4706
6046 | 59.8888 | 0 | 42.9 | 0 | 93.9 | 29.9444 | 0 | 0 | 0 | 0 | 0 | 199.2562
6047 | 57.737 | 0 | 0 | 0 | 0 | 28.8685 | 0 | 0 | 0 | 0 | 0 | 143.0515
6048 | 59.665 | 0 | 0 | 0 | 0 | 29.8325 | 0 | 0 | 0 | 0 | 0 | 77.0868
6049 | 60.0679 | 0 | 0 | 0 | 0 | 30.034 | 0 | 0 | 0 | 0 | 0 | 57.2463
6050 | 58.2499 | 0 | 0 | 0 | 0 | 29.125 | 0 | 0 | 0 | 0 | 0 | 48.0537
6051 | 57.0583 | 0 | 0 | 0 | 0 | 28.5291 | 0 | 0 | 0 | 0 | 0 | 47.9407
6052 | 45.9215 | 0 | 0 | 0 | 0 | 22.9608 | 0 | 0 | 0 | 0 | 0 | 46.9063
6053 | 41.2203 | 0 | 0 | 0 | 0 | 20.6102 | 0 | 0 | 0 | 0 | 0 | 56.4356
6054 | 53.422 | 0 | 0 | 0 | 0 | 26.711 | 0 | 0 | 0 | 0 | 0 | 70.2432
6055 | 93.2411 | 0 | 42.9 | 7.7 | 56.3 | 46.6206 | 0 | 0 | 0 | 0 | 53.6 | 82.674
6056 | 157.5457 | 0.7 | 43 | 21.8 | 37.6 | 78.7728 | 0 | 0 | 0 | 0 | 50.8 | 121.5588
6057 | 278.8996 | 2.1 | 43.2 | 9.6 | 0 | 139.4498 | 0 | 0 | 0 | 0 | 0 | 135.8754
6058 | 371.5608 | 3.5 | 43.4 | 0.8 | 0 | 185.7804 | 0 | 0 | 0 | 0 | 0 | 97.7959
6059 | 370.6125 | 3.5 | 43.4 | 0 | 0 | 185.3062 | 0 | 0 | 0 | 0 | 0 | 118.8866
6060 | 316.8592 | 2.8 | 43.3 | 0 | 0 | 158.4296 | 0 | 0 | 0 | 0 | 0 | 186.2195
6061 | 287.8817 | 1.4 | 43.1 | 0 | 75.1 | 143.9409 | 0 | 0 | 0 | 0 | 1.2 | 125.6995
6062 | 307.1871 | 2.1 | 43.2 | 0 | 37.6 | 153.5936 | 0 | 0 | 0 | 0 | 0 | 159.0107
6063 | 278.3312 | 3.5 | 43.4 | 0 | 0 | 139.1656 | 0 | 0.7 | 0 | 0 | 0 | 147.1652
6064 | 235.9266 | 2.8 | 43.3 | 0 | 0 | 117.9633 | 0 | 6.3 | 0 | 0 | 0 | 119.4816
6065 | 167.9318 | 2.1 | 43.2 | 0 | 0 | 83.9659 | 0 | 19 | 0 | 0 | 0 | 268.5734
6066 | 116.5882 | 0.7 | 43 | 0 | 37.6 | 58.2941 | 0 | 15.9 | 0 | 0 | 0.6 | 205.5907
6067 | 88.1971 | 0 | 42.9 | 0 | 75.1 | 44.0986 | 0 | 0 | 0 | 0 | 0.3 | 275.2772
6068 | 66.0522 | 0 | 42.9 | 0 | 75.1 | 33.0261 | 0 | 0 | 0 | 0 | 0 | 206.235
6069 | 57.8994 | 0 | 42.9 | 0 | 75.1 | 28.9497 | 0 | 0 | 0 | 0 | 5.3 | 201.6991
6070 | 62.159 | 0 | 42.9 | 0 | 93.9 | 31.0795 | 0 | 0 | 0 | 0 | 12.6 | 119.4793
6071 | 59.4906 | 0 | 0 | 0 | 0 | 29.7453 | 0 | 0 | 0 | 0 | 0 | 124.7941
6072 | 59.2934 | 0 | 0 | 0 | 0 | 29.6467 | 0 | 0 | 0 | 0 | 0 | 98.6342
6073 | 60.0376 | 0 | 0 | 0 | 0 | 30.0188 | 0 | 0 | 0 | 0 | 0 | 82.9087
6074 | 57.0533 | 0 | 0 | 0 | 0 | 28.5267 | 0 | 0 | 0 | 0 | 0 | 74.9746
6075 | 58.9491 | 0 | 0 | 0 | 0 | 29.4746 | 0 | 0 | 0 | 0 | 0 | 65.069
6076 | 58.5134 | 0 | 0 | 0 | 0 | 29.2567 | 0 | 0 | 0 | 0 | 0 | 65.5253
6077 | 57.8167 | 0 | 0 | 0 | 0 | 28.9083 | 0 | 0 | 0 | 0 | 0 | 66.5607
6078 | 80.9555 | 0 | 0 | 0 | 0 | 40.4777 | 0 | 0 | 0 | 0 | 0.1 | 68.6316
6079 | 119.7596 | 0 | 42.9 | 75 | 56.3 | 59.8798 | 0 | 0 | 0 | 0 | 373.3 | 59.6673
6080 | 180.5007 | 0.7 | 43 | 88.9 | 37.6 | 90.2504 | 0 | 0 | 0 | 0 | 277.5 | 53.7975
6081 | 280.9736 | 2.1 | 43.2 | 32.4 | 0 | 140.4868 | 0 | 0 | 0 | 0 | 0 | 63.8068
6082 | 335.1158 | 3.5 | 43.4 | 5.3 | 0 | 167.5579 | 0 | 0 | 0 | 0 | 0 | 58.1719
6083 | 326.6345 | 3.5 | 43.4 | 0 | 0 | 163.3172 | 0 | 0 | 0 | 0 | 0 | 137.611
6084 | 318.3846 | 2.8 | 43.3 | 0 | 0 | 159.1923 | 0 | 0 | 0 | 0 | 0 | 217.3219
6085 | 300.9347 | 1.4 | 43.1 | 0 | 75.1 | 150.4674 | 0 | 0 | 0 | 0 | 36.4 | 212.7308
6086 | 305.7398 | 2.1 | 43.2 | 0 | 37.6 | 152.8699 | 0 | 0 | 0 | 0 | 14.1 | 190.6792
6087 | 272.6466 | 3.5 | 43.4 | 0 | 0 | 136.3233 | 0 | 0 | 0 | 0 | 0 | 105.1038
6088 | 204.6483 | 2.8 | 43.3 | 0 | 0 | 102.3242 | 0 | 0 | 0 | 0 | 0 | 270.6588
6089 | 138.364 | 2.1 | 43.2 | 0 | 0 | 69.182 | 0 | 0 | 0 | 0 | 0 | 90.9774
6090 | 105.8286 | 0.7 | 43 | 0 | 37.6 | 52.9143 | 0 | 0 | 0 | 0 | 1.5 | 146.9744
6091 | 86.933 | 0 | 42.9 | 0 | 75.1 | 43.4665 | 0 | 0 | 0 | 0 | 6.8 | 310.3915
6092 | 66.2211 | 0 | 42.9 | 0 | 75.1 | 33.1106 | 0 | 0 | 0 | 0 | 3.7 | 277.6027
6093 | 62.8033 | 0 | 42.9 | 0 | 75.1 | 31.4017 | 0 | 0 | 0 | 0 | 29 | 239.2485
6094 | 60.8874 | 0 | 42.9 | 0 | 93.9 | 30.4437 | 0 | 0 | 0 | 0 | 68.3 | 190.1713
6095 | 60.6828 | 0 | 0 | 0 | 0 | 30.3414 | 0 | 0 | 0 | 0 | 0 | 214.5791
6096 | 61.051 | 0 | 0 | 0 | 0 | 30.5255 | 0 | 0 | 0 | 0 | 0 | 138.5391
6097 | 61.7911 | 0 | 0 | 0 | 0 | 30.8956 | 0 | 0 | 0 | 0 | 0 | 64.8394
6098 | 60.5071 | 0 | 0 | 0 | 0 | 30.2535 | 0 | 0 | 0 | 0 | 0 | 54.0261
6099 | 59.8649 | 0 | 0 | 0 | 0 | 29.9325 | 0 | 0 | 0 | 0 | 0 | 49.893
6100 | 58.9184 | 0 | 0 | 0 | 0 | 29.4592 | 0 | 0 | 0 | 0 | 0 | 74.5108
6101 | 58.9175 | 0 | 0 | 0 | 0 | 29.4588 | 0 | 0 | 0 | 0 | 0.9 | 70.7049
6102 | 78.9577 | 0 | 0 | 0 | 0 | 39.4789 | 0 | 0 | 0 | 0 | 5.6 | 68.7468
6103 | 124.4897 | 0 | 42.9 | 80.3 | 56.3 | 62.2448 | 0 | 0 | 0 | 0 | 433.9 | 88.5982
6104 | 202.597 | 0.7 | 43 | 86.9 | 37.6 | 101.2985 | 0 | 0 | 0 | 0 | 312 | 75.3251
6105 | 275.6519 | 2.1 | 43.2 | 22.7 | 0 | 137.8259 | 0 | 0 | 0 | 0 | 0 | 97.4314
6106 | 344.5681 | 3.5 | 43.4 | 0.9 | 0 | 172.2841 | 0 | 0 | 0 | 0 | 0 | 204.6202
6107 | 342.0193 | 3.5 | 43.4 | 0 | 0 | 171.0097 | 0 | 0 | 0 | 0 | 0 | 251.1007
6108 | 304.6315 | 2.8 | 43.3 | 0 | 0 | 152.3158 | 0 | 0 | 0 | 0 | 0 | 54.3704
6109 | 289.8265 | 1.4 | 43.1 | 0 | 75.1 | 144.9133 | 0 | 0 | 0 | 0 | 7.7 | 96.7133
6110 | 257.4505 | 2.1 | 43.2 | 0 | 37.6 | 128.7252 | 0 | 0 | 0 | 0 | 0 | 127.4096
6111 | 245.4955 | 3.5 | 43.4 | 0 | 0 | 122.7478 | 0 | 0 | 0 | 0 | 0 | 205.9221
6112 | 198.2711 | 2.8 | 43.3 | 0 | 0 | 99.1355 | 0 | 0 | 0 | 0 | 0 | 181.5411
6113 | 151.1086 | 2.1 | 43.2 | 0 | 0 | 75.5543 | 0 | 0 | 0 | 0 | 0 | 125.3305
6114 | 129.5327 | 0.7 | 43 | 0 | 37.6 | 64.7664 | 0 | 0 | 0 | 0 | 0 | 162.6197
6115 | 110.7282 | 0 | 42.9 | 0 | 75.1 | 55.3641 | 0 | 0 | 0 | 0 | 0 | 205.2841
6116 | 85.7943 | 0 | 42.9 | 0 | 75.1 | 42.8971 | 0 | 0 | 0 | 0 | 0 | 207.8682
6117 | 67.6471 | 0 | 42.9 | 0 | 75.1 | 33.8235 | 0 | 0 | 0 | 0 | 0 | 206.7081
6118 | 64.9173 | 0 | 42.9 | 0 | 93.9 | 32.4586 | 0 | 0 | 0 | 0 | 3.8 | 251.1599
6119 | 62.0936 | 0 | 0 | 0 | 0 | 31.0468 | 0 | 0 | 0 | 0 | 0 | 193.0253
6120 | 62.0328 | 0 | 0 | 0 | 0 | 31.0164 | 0 | 0 | 0 | 0 | 0 | 109.4493
6121 | 60.8703 | 0 | 0 | 0 | 0 | 30.4352 | 0 | 0 | 0 | 0 | 0 | 76.3814
6122 | 61.4719 | 0 | 0 | 0 | 0 | 30.7359 | 0 | 0 | 0 | 0 | 0 | 56.3213
6123 | 59.762 | 0 | 0 | 0 | 0 | 29.881 | 0 | 0 | 0 | 0 | 0 | 51.5001
6124 | 60.1532 | 0 | 0 | 0 | 0 | 30.0766 | 0 | 0 | 0 | 0 | 0 | 49.3207
6125 | 61.0891 | 0 | 0 | 0 | 0 | 30.5446 | 0 | 0 | 0 | 0 | 0 | 52.1925
6126 | 87.3269 | 0 | 0 | 0 | 0 | 43.6634 | 0 | 0 | 0 | 0 | 0 | 77.8071
6127 | 127.7944 | 0 | 42.9 | 31.8 | 56.3 | 63.8972 | 0 | 0 | 0 | 0 | 336.6 | 82.1974
6128 | 193.9882 | 0.7 | 43 | 44.8 | 37.6 | 96.9941 | 0 | 0 | 0 | 0 | 244.4 | 96.4662
6129 | 324.6804 | 2.1 | 43.2 | 8.5 | 0 | 162.3402 | 0 | 0 | 0 | 0 | 0 | 107.8856
6130 | 372.176 | 3.5 | 43.4 | 0 | 0 | 186.088 | 0 | 0 | 0 | 0 | 0 | 141.726
6131 | 375.0084 | 3.5 | 43.4 | 0 | 0 | 187.5042 | 0 | 0 | 0 | 0 | 0 | 202.1964
6132 | 310.4906 | 2.8 | 43.3 | 0 | 0 | 155.2453 | 0 | 0 | 0 | 0 | 0 | 185.3947
6133 | 273.8596 | 1.4 | 43.1 | 0 | 75.1 | 136.9298 | 0 | 0 | 0 | 0 | 2.2 | 157.8862
6134 | 267.2852 | 2.1 | 43.2 | 0 | 37.6 | 133.6426 | 0 | 0 | 0 | 0 | 0 | 276.5026
6135 | 266.1881 | 3.5 | 43.4 | 0 | 0 | 133.094 | 0 | 0 | 0 | 0 | 0 | 246.126
6136 | 222.591 | 2.8 | 43.3 | 0 | 0 | 111.2955 | 0 | 0 | 0 | 0 | 0 | 124.1458
6137 | 183.453 | 2.1 | 43.2 | 0 | 0 | 91.7265 | 0 | 0 | 0 | 0 | 0 | 144.235
6138 | 188.1236 | 0.7 | 43 | 0 | 37.6 | 94.0618 | 0 | 0 | 0 | 0 | 0 | 247.5299
6139 | 119.4916 | 0 | 42.9 | 0 | 75.1 | 59.7458 | 0 | 0 | 0 | 0 | 0 | 202.2309
6140 | 78.3261 | 0 | 42.9 | 0 | 75.1 | 39.163 | 0 | 0 | 0 | 0 | 0 | 207.0215
6141 | 64.4453 | 0 | 42.9 | 0 | 75.1 | 32.2226 | 0 | 0 | 0 | 0 | 0 | 265.0651
6142 | 61.85 | 0 | 42.9 | 0 | 93.9 | 30.925 | 0 | 0 | 0 | 0 | 0 | 211.6362
6143 | 63.8292 | 0 | 0 | 0 | 0 | 31.9146 | 0 | 0 | 0 | 0 | 0 | 135.2964
6144 | 59.5522 | 0 | 0 | 0 | 0 | 29.7761 | 0 | 0 | 0 | 0 | 0 | 141.0865
6145 | 62.0223 | 0 | 0 | 0 | 0 | 31.0112 | 0 | 0 | 0 | 0 | 0 | 67.3709
6146 | 61.2205 | 0 | 0 | 0 | 0 | 30.6103 | 0 | 0 | 0 | 0 | 0 | 61.1657
6147 | 61.6523 | 0 | 0 | 0 | 0 | 30.8261 | 0 | 0 | 0 | 0 | 0 | 50.6964
6148 | 61.7009 | 0 | 0 | 0 | 0 | 30.8505 | 0 | 0 | 0 | 0 | 0 | 49.0879
6149 | 62.4832 | 0 | 0 | 0 | 0 | 31.2416 | 0 | 0 | 0 | 0 | 0 | 55.8633
6150 | 73.2982 | 0 | 0 | 0 | 0 | 36.6491 | 0 | 0 | 0 | 0 | 0 | 74.5095
6151 | 112.5552 | 0 | 42.9 | 0 | 56.3 | 56.2776 | 0 | 0 | 0 | 0 | 84.6 | 81.2534
6152 | 175.7555 | 0.7 | 43 | 0.9 | 37.6 | 87.8778 | 0 | 0 | 0 | 0 | 37.5 | 85.5121
6153 | 303.1761 | 2.1 | 43.2 | 0 | 0 | 151.5881 | 0 | 0 | 0 | 0 | 0 | 84.6888
6154 | 353.439 | 3.5 | 43.4 | 0 | 0 | 176.7195 | 0 | 0 | 0 | 0 | 0 | 88.0039
6155 | 338.5442 | 3.5 | 43.4 | 0 | 0 | 169.2721 | 0 | 0 | 0 | 0 | 0 | 107.6383
6156 | 302.2333 | 2.8 | 43.3 | 0 | 0 | 151.1167 | 0 | 0 | 0 | 0 | 0 | 162.5021
6157 | 295.3614 | 1.4 | 43.1 | 0 | 75.1 | 147.6807 | 0 | 0 | 0 | 0 | 0 | 192.5498
6158 | 297.8197 | 2.1 | 43.2 | 0 | 37.6 | 148.9099 | 0 | 0 | 0 | 0 | 0 | 123.0467
6159 | 263.2383 | 3.5 | 43.4 | 0 | 0 | 131.6191 | 0 | 3.4 | 1.2 | 0 | 0 | 85.2807
6160 | 208.4319 | 2.8 | 43.3 | 0 | 0 | 104.2159 | 0 | 5.7 | 19.3 | 0 | 0 | 84.805
6161 | 146.925 | 2.1 | 43.2 | 0 | 0 | 73.4625 | 0 | 4.7 | 43.2 | 0 | 0 | 242.6619
6162 | 110.8962 | 0.7 | 43 | 0 | 37.6 | 55.4481 | 0 | 0 | 42.5 | 0 | 0 | 225.7823
6163 | 82.5643 | 0 | 42.9 | 0 | 75.1 | 41.2821 | 0 | 0 | 0 | 0 | 0 | 254.6688
6164 | 57.874 | 0 | 42.9 | 0 | 75.1 | 28.937 | 0 | 0 | 0 | 0 | 0 | 190.3
6165 | 42.8951 | 0 | 42.9 | 0 | 75.1 | 21.4476 | 0 | 0 | 0 | 0 | 0 | 221.6952
6166 | 41.4571 | 0 | 42.9 | 0 | 93.9 | 20.7285 | 0 | 0 | 0 | 0 | 0 | 227.8016
6167 | 41.3756 | 0 | 0 | 0 | 0 | 20.6878 | 0 | 0 | 0 | 0 | 0 | 123.364
6168 | 40.7926 | 0 | 0 | 0 | 0 | 20.3963 | 0 | 0 | 0 | 0 | 0 | 73.3565
6169 | 41.8907 | 0 | 0 | 0 | 0 | 20.9453 | 0 | 0 | 0 | 0 | 0 | 62.6609
6170 | 41.6505 | 0 | 0 | 0 | 0 | 20.8252 | 0 | 0 | 0 | 0 | 0 | 52.536
6171 | 42.2093 | 0 | 0 | 0 | 0 | 21.1046 | 0 | 0 | 0 | 0 | 0 | 47.365
6172 | 40.3937 | 0 | 0 | 0 | 0 | 20.1969 | 0 | 0 | 0 | 0 | 0 | 46.4491
6173 | 43.9033 | 0 | 0 | 0 | 0 | 21.9517 | 0 | 0 | 0 | 0 | 0 | 52.4203
6174 | 44.785 | 0 | 0 | 0 | 0 | 22.3925 | 0 | 0 | 0 | 0 | 0 | 59.6683
6175 | 62.6384 | 0 | 42.9 | 0 | 56.3 | 31.3192 | 0 | 0 | 0 | 0 | 0 | 74.8572
6176 | 67.7475 | 0 | 42.9 | 0 | 37.6 | 33.8738 | 0 | 0 | 0 | 0 | 0.2 | 99.5936
6177 | 63.6618 | 0 | 42.9 | 0 | 0 | 31.8309 | 0 | 0 | 0 | 0 | 0 | 94.4415
6178 | 55.8945 | 0 | 42.9 | 0 | 0 | 27.9473 | 0 | 0 | 0 | 0 | 0 | 183.6313
6179 | 58.589 | 0 | 42.9 | 0 | 0 | 29.2945 | 0 | 0 | 0 | 0 | 0 | 85.5132
6180 | 54.0096 | 0 | 42.9 | 0 | 0 | 27.0048 | 0 | 0 | 0 | 0 | 0 | 258.9054
6181 | 53.8205 | 0 | 42.9 | 0 | 75.1 | 26.9103 | 0 | 0 | 0 | 0 | 0 | 173.8969
6182 | 55.976 | 0 | 42.9 | 0 | 37.6 | 27.988 | 0 | 0 | 0 | 0 | 0 | 113.7996
6183 | 61.0836 | 0 | 42.9 | 0 | 0 | 30.5418 | 0 | 0 | 0 | 0 | 0 | 61.0476
6184 | 63.6073 | 0 | 42.9 | 0 | 0 | 31.8036 | 0 | 0 | 0 | 0 | 0 | 73.2397
6185 | 62.2799 | 0 | 42.9 | 0 | 0 | 31.1399 | 0 | 0 | 0 | 0 | 0 | 193.7487
6186 | 68.7507 | 0 | 42.9 | 0 | 37.6 | 34.3754 | 0 | 0 | 0 | 0 | 0 | 210.4029
6187 | 69.2438 | 0 | 42.9 | 0 | 75.1 | 34.6219 | 0 | 0 | 0 | 0 | 0 | 296.6036
6188 | 50.5942 | 0 | 42.9 | 0 | 75.1 | 25.2971 | 0 | 0 | 0 | 0 | 0 | 212.7217
6189 | 42.2431 | 0 | 42.9 | 0 | 75.1 | 21.1215 | 0 | 0 | 0 | 0 | 0 | 170.1731
6190 | 41.0681 | 0 | 42.9 | 0 | 93.9 | 20.5341 | 0 | 0 | 0 | 0 | 0 | 185.551
6191 | 42.6974 | 0 | 0 | 0 | 0 | 21.3487 | 0 | 0 | 0 | 0 | 0 | 135.8242
6192 | 41.9406 | 0 | 0 | 0 | 0 | 20.9703 | 0 | 0 | 0 | 0 | 0 | 107.8865
6193 | 42.3184 | 0 | 0 | 0 | 0 | 21.1592 | 0 | 0 | 0 | 0 | 0 | 71.2797
6194 | 43.2859 | 0 | 0 | 0 | 0 | 21.643 | 0 | 0 | 0 | 0 | 0 | 86.9354
6195 | 44.4587 | 0 | 0 | 0 | 0 | 22.2293 | 0 | 0 | 0 | 0 | 0 | 169.4169
6196 | 40.3578 | 0 | 0 | 0 | 0 | 20.1789 | 0 | 0 | 0 | 0 | 0 | 48.7441
6197 | 44.4165 | 0 | 0 | 0 | 0 | 22.2083 | 0 | 0 | 0 | 0 | 0 | 54.1425
6198 | 45.337 | 0 | 0 | 0 | 0 | 22.6685 | 0 | 0 | 0 | 0 | 0 | 67.1395
6199 | 45.6234 | 0 | 42.9 | 0 | 56.3 | 22.8117 | 0 | 0 | 0 | 0 | 7.4 | 71.5113
6200 | 46.5299 | 0 | 42.9 | 0 | 37.6 | 23.265 | 0 | 0 | 0 | 0 | 11.6 | 92.8863
6201 | 45.7024 | 0 | 42.9 | 0 | 0 | 22.8512 | 0 | 0 | 0 | 0 | 0 | 64.6092
6202 | 46.2305 | 0 | 42.9 | 0 | 0 | 23.1153 | 0 | 0 | 0 | 0 | 0 | 104.3802
6203 | 45.6764 | 0 | 42.9 | 0 | 0 | 22.8382 | 0 | 0 | 0 | 0 | 0 | 62.6616
6204 | 48.7725 | 0 | 42.9 | 0 | 0 | 24.3863 | 0 | 0 | 0 | 0 | 0 | 150.6156
6205 | 51.3765 | 0 | 42.9 | 0 | 75.1 | 25.6882 | 0 | 0 | 0 | 0 | 14 | 128.1583
6206 | 55.7597 | 0 | 42.9 | 0 | 37.6 | 27.8799 | 0 | 0 | 0 | 0 | 5.6 | 157.8968
6207 | 59.1698 | 0 | 42.9 | 0 | 0 | 29.5849 | 0 | 0 | 0 | 0 | 0 | 65.2975
6208 | 57.2613 | 0 | 42.9 | 0 | 0 | 28.6306 | 0 | 0 | 0 | 0 | 0 | 54.1417
6209 | 59.0278 | 0 | 42.9 | 0 | 0 | 29.5139 | 0 | 0 | 0 | 0 | 0 | 104.1311
6210 | 57.3914 | 0 | 42.9 | 0 | 37.6 | 28.6957 | 0 | 0 | 0 | 0 | 0 | 176.753
6211 | 47.1457 | 0 | 42.9 | 0 | 75.1 | 23.5729 | 0 | 0 | 0 | 0 | 0 | 466.2938
6212 | 40.99 | 0 | 42.9 | 0 | 75.1 | 20.495 | 0 | 0 | 0 | 0 | 0 | 237.4145
6213 | 43.0752 | 0 | 42.9 | 0 | 75.1 | 21.5376 | 0 | 0 | 0 | 0 | 0 | 303.7963
6214 | 41.1103 | 0 | 42.9 | 0 | 93.9 | 20.5551 | 0 | 0 | 0 | 0 | 0 | 160.4924
6215 | 41.0681 | 0 | 0 | 0 | 0 | 20.5341 | 0 | 0 | 0 | 0 | 0 | 116.1201
6216 | 41.4329 | 0 | 0 | 0 | 0 | 20.7165 | 0 | 0 | 0 | 0 | 0 | 127.2308
6217 | 42.3825 | 0 | 0 | 0 | 0 | 21.1913 | 0 | 0 | 0 | 0 | 0 | 57.2466
6218 | 42.0215 | 0 | 0 | 0 | 0 | 21.0107 | 0 | 0 | 0 | 0 | 0 | 47.0199
6219 | 38.9458 | 0 | 0 | 0 | 0 | 19.4729 | 0 | 0 | 0 | 0 | 0 | 46.6772
6220 | 43.9033 | 0 | 0 | 0 | 0 | 21.9517 | 0 | 0 | 0 | 0 | 0 | 48.284
6221 | 45.0073 | 0 | 0 | 0 | 0 | 22.5036 | 0 | 0 | 0 | 0 | 0 | 49.6637
6222 | 60.3679 | 0 | 0 | 0 | 0 | 30.184 | 0 | 0 | 0 | 0 | 0 | 83.1505
6223 | 111.8272 | 0 | 42.9 | 62.8 | 56.3 | 55.9136 | 0 | 0 | 0 | 0 | 310.7 | 133.2926
6224 | 182.4591 | 0.7 | 43 | 88 | 37.6 | 91.2296 | 0 | 0 | 0 | 0 | 244.1 | 105.9405
6225 | 237.9582 | 2.1 | 43.2 | 36.3 | 0 | 118.9791 | 0 | 0 | 0 | 0 | 0 | 126.9667
6226 | 259.4008 | 3.5 | 43.4 | 9.9 | 0 | 129.7004 | 0 | 0 | 0 | 0 | 0 | 83.7336
6227 | 264.6524 | 3.5 | 43.4 | 0 | 0 | 132.3262 | 0 | 0 | 0 | 0 | 0 | 123.9188
6228 | 264.191 | 2.8 | 43.3 | 0 | 0 | 132.0955 | 0 | 0 | 0 | 0 | 0 | 116.8642
6229 | 249.4703 | 1.4 | 43.1 | 0 | 75.1 | 124.7351 | 0 | 0 | 0 | 0 | 19.1 | 205.55
6230 | 243.2895 | 2.1 | 43.2 | 0 | 37.6 | 121.6447 | 0 | 0 | 0 | 0 | 7.1 | 88.597
6231 | 239.4312 | 3.5 | 43.4 | 0 | 0 | 119.7156 | 0 | 0 | 0 | 0 | 0 | 98.1539
6232 | 214.5364 | 2.8 | 43.3 | 0 | 0 | 107.2682 | 0 | 0 | 0 | 0 | 0 | 124.3179
6233 | 182.2041 | 2.1 | 43.2 | 0 | 0 | 91.102 | 0 | 0 | 0 | 0 | 0 | 224.9525
6234 | 153.0366 | 0.7 | 43 | 0 | 37.6 | 76.5183 | 0 | 0 | 0 | 0 | 4.2 | 109.8126
6235 | 123.9114 | 0 | 42.9 | 0 | 75.1 | 61.9557 | 0 | 0 | 0 | 0 | 7.2 | 153.1516
6236 | 82.6207 | 0 | 42.9 | 0 | 75.1 | 41.3103 | 0 | 0 | 0 | 0 | 2.8 | 211.9003
6237 | 64.2658 | 0 | 42.9 | 0 | 75.1 | 32.1329 | 0 | 0 | 0 | 0 | 20 | 196.4193
6238 | 62.7751 | 0 | 42.9 | 0 | 93.9 | 31.3876 | 0 | 0 | 0 | 0 | 43.4 | 191.5009
6239 | 60.6221 | 0 | 0 | 0 | 0 | 30.311 | 0 | 0 | 0 | 0 | 0 | 156.6098
6240 | 60.2179 | 0 | 0 | 0 | 0 | 30.109 | 0 | 0 | 0 | 0 | 0 | 102.7022
6241 | 61.2236 | 0 | 0 | 0 | 0 | 30.6118 | 0 | 0 | 0 | 0 | 0 | 73.3561
6242 | 59.6855 | 0 | 0 | 0 | 0 | 29.8427 | 0 | 0 | 0 | 0 | 0 | 60.4731
6243 | 59.4183 | 0 | 0 | 0 | 0 | 29.7092 | 0 | 0 | 0 | 0 | 0 | 55.6344
6244 | 61.5193 | 0 | 0 | 0 | 0 | 30.7597 | 0 | 0 | 0 | 0 | 0 | 56.8988
6245 | 61.5364 | 0 | 0 | 0 | 0 | 30.7682 | 0 | 0 | 0 | 0 | 0 | 67.3705
6246 | 81.7142 | 0 | 0 | 0 | 0 | 40.8571 | 0 | 0 | 0 | 0 | 0 | 77.3255
6247 | 126.4626 | 0 | 42.9 | 46.4 | 56.3 | 63.2313 | 0 | 0 | 0 | 0 | 329.7 | 70.2436
6248 | 190.6318 | 0.7 | 43 | 43.9 | 37.6 | 95.3159 | 0 | 0 | 0 | 0 | 219.3 | 92.6522
6249 | 256.0149 | 2.1 | 43.2 | 2.2 | 0 | 128.0074 | 0 | 0 | 0 | 0 | 0 | 71.9725
6250 | 326.3558 | 3.5 | 43.4 | 0 | 0 | 163.1779 | 0 | 0 | 0 | 0 | 0 | 121.2704
6251 | 298.2304 | 3.5 | 43.4 | 0 | 0 | 149.1152 | 0 | 0 | 0 | 0 | 0 | 89.1862
6252 | 250.0988 | 2.8 | 43.3 | 0 | 0 | 125.0494 | 0 | 0 | 0 | 0 | 0 | 72.203
6253 | 232.4704 | 1.4 | 43.1 | 0 | 75.1 | 116.2352 | 0 | 0 | 0 | 0 | 0 | 121.3271
6254 | 226.0392 | 2.1 | 43.2 | 0 | 37.6 | 113.0196 | 0 | 0 | 14.6 | 0 | 0 | 170.9909
6255 | 206.9718 | 3.5 | 43.4 | 0 | 0 | 103.4859 | 0 | 0 | 40.8 | 0 | 0 | 127.6468
6256 | 175.1363 | 2.8 | 43.3 | 0 | 0 | 87.5681 | 0 | 0 | 56.3 | 0 | 0 | 77.9263
6257 | 130.7659 | 2.1 | 43.2 | 0 | 0 | 65.383 | 0 | 0 | 62 | 0 | 0 | 88.8393
6258 | 117.4736 | 0.7 | 43 | 0 | 37.6 | 58.7368 | 0 | 0 | 41.4 | 0 | 0 | 102.2201
6259 | 80.1525 | 0 | 42.9 | 0 | 75.1 | 40.0762 | 0 | 0 | 0 | 0 | 0 | 181.7098
6260 | 65.8381 | 0 | 42.9 | 0 | 75.1 | 32.919 | 0 | 0 | 0 | 0 | 0 | 351.6581
6261 | 61.66 | 0 | 42.9 | 0 | 75.1 | 30.83 | 0 | 0 | 0 | 0 | 0 | 577.2989
6262 | 60.6924 | 0 | 42.9 | 0 | 93.9 | 30.3462 | 0 | 0 | 0 | 0 | 0 | 204.5419
6263 | 62.569 | 0 | 0 | 0 | 0 | 31.2845 | 0 | 0 | 0 | 0 | 0 | 113.924
6264 | 59.9939 | 0 | 0 | 0 | 0 | 29.9969 | 0 | 0 | 0 | 0 | 0 | 100.0687
6265 | 61.065 | 0 | 0 | 0 | 0 | 30.5325 | 0 | 0 | 0 | 0 | 0 | 62.4299
6266 | 59.1335 | 0 | 0 | 0 | 0 | 29.5668 | 0 | 0 | 0 | 0 | 0 | 49.0901
6267 | 47.7842 | 0 | 0 | 0 | 0 | 23.8921 | 0 | 0 | 0 | 0 | 0 | 48.6294
6268 | 45.4932 | 0 | 0 | 0 | 0 | 22.7466 | 0 | 0 | 0 | 0 | 0 | 50.123
6269 | 42.8499 | 0 | 0 | 0 | 0 | 21.4249 | 0 | 0 | 0 | 0 | 0 | 56.5545
6270 | 67.2724 | 0 | 0 | 0 | 0 | 33.6362 | 0 | 0 | 0 | 0 | 0 | 74.6255
6271 | 104.6549 | 0 | 42.9 | 0 | 56.3 | 52.3275 | 0 | 0 | 0 | 0 | 21.4 | 103.2995
6272 | 158.0131 | 0.7 | 43 | 0.1 | 37.6 | 79.0065 | 0 | 0 | 0 | 0 | 16.9 | 67.7152
6273 | 258.1955 | 2.1 | 43.2 | 0 | 0 | 129.0978 | 0 | 0 | 0 | 0 | 0 | 68.7464
6274 | 301.0764 | 3.5 | 43.4 | 0 | 0 | 150.5382 | 0 | 0 | 0 | 0 | 0 | 162.2624
6275 | 316.4591 | 3.5 | 43.4 | 0 | 0 | 158.2295 | 0 | 0 | 0 | 0 | 0 | 88.5994
6276 | 306.5806 | 2.8 | 43.3 | 0 | 0 | 153.2903 | 0 | 0 | 0 | 0 | 0 | 149.3122
6277 | 314.7344 | 1.4 | 43.1 | 0 | 75.1 | 157.3672 | 0 | 0 | 0 | 0 | 0 | 201.2048
6278 | 328.0753 | 2.1 | 43.2 | 0 | 37.6 | 164.0376 | 0 | 0 | 0 | 0 | 0 | 83.4998
6279 | 321.8809 | 3.5 | 43.4 | 0 | 0 | 160.9404 | 0 | 0 | 0 | 0 | 0 | 114.168
6280 | 252.1266 | 2.8 | 43.3 | 0 | 0 | 126.0633 | 0 | 0 | 0 | 0 | 0 | 121.4198
6281 | 171.6748 | 2.1 | 43.2 | 0 | 0 | 85.8374 | 0 | 0 | 0 | 0 | 0 | 188.4893
6282 | 125.7225 | 0.7 | 43 | 0 | 37.6 | 62.8613 | 0 | 0 | 0 | 0 | 0 | 124.0118
6283 | 83.8291 | 0 | 42.9 | 0 | 75.1 | 41.9145 | 0 | 0 | 0 | 0 | 0 | 117.1773
6284 | 66.7778 | 0 | 42.9 | 0 | 75.1 | 33.3889 | 0 | 0 | 0 | 0 | 0 | 164.2046
6285 | 61.5205 | 0 | 42.9 | 0 | 75.1 | 30.7603 | 0 | 0 | 0 | 0 | 0 | 213.8281
6286 | 59.7862 | 0 | 42.9 | 0 | 93.9 | 29.8931 | 0 | 0 | 0 | 0 | 0 | 156.6226
6287 | 64.2947 | 0 | 0 | 0 | 0 | 32.1473 | 0 | 0 | 0 | 0 | 0 | 100.7852
6288 | 64.9647 | 0 | 0 | 0 | 0 | 32.4824 | 0 | 0 | 0 | 0 | 0 | 87.5271
6289 | 60.4305 | 0 | 0 | 0 | 0 | 30.2153 | 0 | 0 | 0 | 0 | 0 | 86.3418
6290 | 62.5678 | 0 | 0 | 0 | 0 | 31.2839 | 0 | 0 | 0 | 0 | 0 | 69.7845
6291 | 61.9566 | 0 | 0 | 0 | 0 | 30.9783 | 0 | 0 | 0 | 0 | 0 | 47.8256
6292 | 60.5709 | 0 | 0 | 0 | 0 | 30.2855 | 0 | 0 | 0 | 0 | 0 | 49.6622
6293 | 60.5737 | 0 | 0 | 0 | 0 | 30.2869 | 0 | 0 | 0 | 0 | 0 | 57.9398
6294 | 76.1009 | 0 | 0 | 0 | 0 | 38.0504 | 0 | 0 | 0 | 0 | 0 | 73.8161
6295 | 124.4481 | 0 | 42.9 | 5.6 | 56.3 | 62.2241 | 0 | 0 | 0 | 0 | 76.7 | 110.176
6296 | 207.4355 | 0.7 | 43 | 16.1 | 37.6 | 103.7177 | 0 | 0 | 0 | 0 | 60.3 | 74.7402
6297 | 300.9255 | 2.1 | 43.2 | 0.6 | 0 | 150.4627 | 0 | 0 | 0 | 0 | 0 | 50.6953
6298 | 276.9591 | 3.5 | 43.4 | 0 | 0 | 138.4796 | 0 | 0 | 0 | 0 | 0 | 50.8111
6299 | 269.3267 | 3.5 | 43.4 | 0 | 0 | 134.6633 | 0 | 0 | 0 | 0 | 0 | 55.1721
6300 | 254.9261 | 2.8 | 43.3 | 0 | 0 | 127.4631 | 0 | 0 | 0 | 0 | 0 | 109.9334
6301 | 244.6686 | 1.4 | 43.1 | 0 | 75.1 | 122.3343 | 0 | 0 | 0 | 0 | 0 | 292.9093
6302 | 256.9481 | 2.1 | 43.2 | 0 | 37.6 | 128.474 | 0 | 0.3 | 0 | 0 | 0 | 91.8215
6303 | 235.1221 | 3.5 | 43.4 | 0 | 0 | 117.561 | 0 | 8.9 | 0 | 0 | 0 | 162.5839
6304 | 184.0214 | 2.8 | 43.3 | 0 | 0 | 92.0107 | 0 | 16 | 0 | 0 | 0 | 146.2169
6305 | 151.1907 | 2.1 | 43.2 | 0 | 0 | 75.5954 | 0 | 28.7 | 1.2 | 0 | 0 | 193.0112
6306 | 133.8958 | 0.7 | 43 | 0 | 37.6 | 66.9479 | 0 | 19.4 | 0 | 0 | 0 | 209.2904
6307 | 102.0411 | 0 | 42.9 | 0 | 75.1 | 51.0205 | 0 | 0 | 0 | 0 | 0 | 290.6288
6308 | 79.7781 | 0 | 42.9 | 0 | 75.1 | 39.889 | 0 | 0 | 0 | 0 | 0 | 229.8718
6309 | 63.8499 | 0 | 42.9 | 0 | 75.1 | 31.925 | 0 | 0 | 0 | 0 | 0 | 207.5393
6310 | 61.7319 | 0 | 42.9 | 0 | 93.9 | 30.866 | 0 | 0 | 0 | 0 | 0 | 262.1106
6311 | 62.9326 | 0 | 0 | 0 | 0 | 31.4663 | 0 | 0 | 0 | 0 | 0 | 180.3795
6312 | 62.3679 | 0 | 0 | 0 | 0 | 31.1839 | 0 | 0 | 0 | 0 | 0 | 101.9784
6313 | 60.6803 | 0 | 0 | 0 | 0 | 30.3402 | 0 | 0 | 0 | 0 | 0 | 78.7664
6314 | 61.6052 | 0 | 0 | 0 | 0 | 30.8026 | 0 | 0 | 0 | 0 | 0 | 61.7404
6315 | 58.9175 | 0 | 0 | 0 | 0 | 29.4588 | 0 | 0 | 0 | 0 | 0 | 50.4672
6316 | 58.624 | 0 | 0 | 0 | 0 | 29.312 | 0 | 0 | 0 | 0 | 0 | 47.7093
6317 | 58.3646 | 0 | 0 | 0 | 0 | 29.1823 | 0 | 0 | 0 | 0 | 0 | 55.1732
6318 | 76.8096 | 0 | 0 | 0 | 0 | 38.4048 | 0 | 0 | 0 | 0 | 0 | 68.1728
6319 | 119.1063 | 0 | 42.9 | 0 | 56.3 | 59.5532 | 0 | 0 | 0 | 0 | 5.9 | 95.395
6320 | 201.3914 | 0.7 | 43 | 0 | 37.6 | 100.6957 | 0 | 0 | 0 | 0 | 8.6 | 85.5138
6321 | 302.0412 | 2.1 | 43.2 | 0 | 0 | 151.0206 | 0 | 0 | 0 | 0 | 0 | 87.1754
6322 | 348.2863 | 3.5 | 43.4 | 0 | 0 | 174.1431 | 0 | 0 | 0 | 0 | 0 | 103.059
6323 | 292.3623 | 3.5 | 43.4 | 0 | 0 | 146.1811 | 0 | 0 | 0 | 0 | 0 | 101.4969
6324 | 277.7157 | 2.8 | 43.3 | 0 | 0 | 138.8578 | 0 | 0 | 0 | 0 | 0 | 74.6259
6325 | 235.922 | 1.4 | 43.1 | 0 | 75.1 | 117.961 | 0 | 0 | 0 | 0 | 0 | 95.6317
6326 | 224.8038 | 2.1 | 43.2 | 0 | 37.6 | 112.4019 | 0 | 0 | 0 | 0 | 0 | 127.8839
6327 | 219.7856 | 3.5 | 43.4 | 0 | 0 | 109.8928 | 0 | 0 | 0 | 0 | 0 | 187.3705
6328 | 181.8833 | 2.8 | 43.3 | 0 | 0 | 90.9416 | 0 | 0 | 0 | 0 | 0 | 106.3012
6329 | 143.6165 | 2.1 | 43.2 | 0 | 0 | 71.8083 | 0 | 0 | 0 | 0 | 0 | 132.5992
6330 | 128.2115 | 0.7 | 43 | 0 | 37.6 | 64.1058 | 0 | 0 | 0 | 0 | 0 | 190.3054
6331 | 82.9089 | 0 | 42.9 | 0 | 75.1 | 41.4545 | 0 | 0 | 0 | 0 | 0 | 291.9219
6332 | 62.8176 | 0 | 42.9 | 0 | 75.1 | 31.4088 | 0 | 0 | 0 | 0 | 0 | 166.7406
6333 | 57.1637 | 0 | 42.9 | 0 | 75.1 | 28.5818 | 0 | 0 | 0 | 0 | 0 | 246.2269
6334 | 62.2371 | 0 | 42.9 | 0 | 93.9 | 31.1185 | 0 | 0 | 0 | 0 | 0 | 252.7548
6335 | 57.3787 | 0 | 0 | 0 | 0 | 28.6894 | 0 | 0 | 0 | 0 | 0 | 147.1586
6336 | 55.9577 | 0 | 0 | 0 | 0 | 27.9789 | 0 | 0 | 0 | 0 | 0 | 98.5143
6337 | 43.6272 | 0 | 0 | 0 | 0 | 21.8136 | 0 | 0 | 0 | 0 | 0 | 72.6644
6338 | 41.0396 | 0 | 0 | 0 | 0 | 20.5198 | 0 | 0 | 0 | 0 | 0 | 53.1084
6339 | 40.9758 | 0 | 0 | 0 | 0 | 20.4879 | 0 | 0 | 0 | 0 | 0 | 51.7297
6340 | 42.9999 | 0 | 0 | 0 | 0 | 21.4999 | 0 | 0 | 0 | 0 | 0 | 48.6277
6341 | 43.792 | 0 | 0 | 0 | 0 | 21.896 | 0 | 0 | 0 | 0 | 0 | 46.5643
6342 | 51.2891 | 0 | 0 | 0 | 0 | 25.6445 | 0 | 0 | 0 | 0 | 0 | 88.362
6343 | 68.0298 | 0 | 42.9 | 1.2 | 56.3 | 34.0149 | 0 | 0 | 0 | 0 | 59.2 | 77.2087
6344 | 68.2217 | 0 | 42.9 | 8.8 | 37.6 | 34.1108 | 0 | 0 | 0 | 0 | 71.8 | 60.1252
6345 | 68.9184 | 0 | 42.9 | 2.4 | 0 | 34.4592 | 0 | 0 | 0 | 0 | 0 | 80.5446
6346 | 62.2225 | 0 | 42.9 | 0 | 0 | 31.1113 | 0 | 0 | 0 | 0 | 0 | 182.0317
6347 | 56.9755 | 0 | 42.9 | 0 | 0 | 28.4878 | 0 | 0 | 0 | 0 | 0 | 77.3274
6348 | 55.3391 | 0 | 42.9 | 0 | 0 | 27.6696 | 0 | 0 | 0 | 0 | 0 | 230.8887
6349 | 56.9275 | 0 | 42.9 | 0 | 75.1 | 28.4637 | 0 | 0 | 0 | 0 | 6 | 219.0832
6350 | 58.5887 | 0 | 42.9 | 0 | 37.6 | 29.2943 | 0 | 0 | 0 | 0 | 4.7 | 124.1061
6351 | 62.6338 | 0 | 42.9 | 0 | 0 | 31.3169 | 0 | 0 | 0 | 0 | 0 | 122.4536
6352 | 63.7306 | 0 | 42.9 | 0 | 0 | 31.8653 | 0 | 0 | 0 | 0 | 0 | 92.5319
6353 | 62.1153 | 0 | 42.9 | 0 | 0 | 31.0576 | 0 | 0 | 0 | 0 | 0 | 115.0148
6354 | 62.7258 | 0 | 42.9 | 0 | 37.6 | 31.3629 | 0 | 0 | 0 | 0 | 5.5 | 257.6578
6355 | 45.6751 | 0 | 42.9 | 0 | 75.1 | 22.8376 | 0 | 0 | 0 | 0 | 4.1 | 216.4088
6356 | 43.7614 | 0 | 42.9 | 0 | 75.1 | 21.8807 | 0 | 0 | 0 | 0 | 0 | 306.3983
6357 | 42.2034 | 0 | 42.9 | 0 | 75.1 | 21.1017 | 0 | 0 | 0 | 0 | 4.6 | 381.9244
6358 | 43.7589 | 0 | 42.9 | 0 | 93.9 | 21.8794 | 0 | 0 | 0 | 0 | 7.7 | 242.8853
6359 | 42.8548 | 0 | 0 | 0 | 0 | 21.4274 | 0 | 0 | 0 | 0 | 0 | 158.5485
6360 | 42.9261 | 0 | 0 | 0 | 0 | 21.4631 | 0 | 0 | 0 | 0 | 0 | 111.7556
6361 | 39.4975 | 0 | 0 | 0 | 0 | 19.7487 | 0 | 0 | 0 | 0 | 0 | 80.4253
6362 | 43.5171 | 0 | 0 | 0 | 0 | 21.7586 | 0 | 0 | 0 | 0 | 0 | 76.6171
6363 | 41.1063 | 0 | 0 | 0 | 0 | 20.5531 | 0 | 0 | 0 | 0 | 0 | 69.4398
6364 | 45.0138 | 0 | 0 | 0 | 0 | 22.5069 | 0 | 0 | 0 | 0 | 0 | 68.0584
6365 | 42.2877 | 0 | 0 | 0 | 0 | 21.1438 | 0 | 0 | 0 | 0 | 0 | 64.8402
6366 | 47.1135 | 0 | 0 | 0 | 0 | 23.5567 | 0 | 0 | 0 | 0 | 0 | 58.171
6367 | 56.3309 | 0 | 42.9 | 4.7 | 56.3 | 28.1654 | 0 | 0 | 0 | 0 | 110.1 | 77.3283
6368 | 60.42 | 0 | 42.9 | 0.8 | 37.6 | 30.21 | 0 | 0 | 0 | 0 | 96 | 66.4471
6369 | 60.8542 | 0 | 42.9 | 0 | 0 | 30.4271 | 0 | 0 | 0 | 0 | 0 | 70.9352
6370 | 57.9518 | 0 | 42.9 | 0 | 0 | 28.9759 | 0 | 0 | 0 | 0 | 0 | 150.6282
6371 | 64.6154 | 0 | 42.9 | 0 | 0 | 32.3077 | 0 | 0 | 0 | 0 | 0 | 176.5546
6372 | 67.9945 | 0 | 42.9 | 0 | 0 | 33.9973 | 0 | 0 | 0 | 0 | 0 | 163.0253
6373 | 73.7445 | 0 | 42.9 | 0 | 75.1 | 36.8723 | 0 | 0 | 0 | 0 | 0 | 76.9705
6374 | 81.1448 | 0 | 42.9 | 0 | 37.6 | 40.5724 | 0 | 0 | 0 | 0 | 0 | 132.1958
6375 | 84.4923 | 0 | 42.9 | 0 | 0 | 42.2462 | 0 | 0 | 0 | 0 | 0 | 95.513
6376 | 84.0116 | 0 | 42.9 | 0 | 0 | 42.0058 | 0 | 0 | 0 | 0 | 0 | 120.0801
6377 | 82.3966 | 0 | 42.9 | 0 | 0 | 41.1983 | 0 | 0 | 0 | 0 | 0 | 111.6336
6378 | 82.3492 | 0 | 42.9 | 0 | 37.6 | 41.1746 | 0 | 0 | 0 | 0 | 0 | 205.0068
6379 | 66.8676 | 0 | 42.9 | 0 | 75.1 | 33.4338 | 0 | 0 | 0 | 0 | 0 | 326.2135
6380 | 54.9803 | 0 | 42.9 | 0 | 75.1 | 27.4901 | 0 | 0 | 0 | 0 | 0 | 234.9659
6381 | 45.8289 | 0 | 42.9 | 0 | 75.1 | 22.9144 | 0 | 0 | 0 | 0 | 0 | 238.3836
6382 | 45.6206 | 0 | 42.9 | 0 | 93.9 | 22.8103 | 0 | 0 | 0 | 0 | 0 | 355.7943
6383 | 42.1473 | 0 | 0 | 0 | 0 | 21.0736 | 0 | 0 | 0 | 0 | 0 | 189.6866
6384 | 39.9137 | 0 | 0 | 0 | 0 | 19.9568 | 0 | 0 | 0 | 0 | 0 | 109.5719
6385 | 41.5154 | 0 | 0 | 0 | 0 | 20.7577 | 0 | 0 | 0 | 0 | 0 | 68.978
6386 | 39.9924 | 0 | 0 | 0 | 0 | 19.9962 | 0 | 0 | 0 | 0 | 0 | 57.2454
6387 | 42.9525 | 0 | 0 | 0 | 0 | 21.4762 | 0 | 0 | 0 | 0 | 0 | 61.2797
6388 | 43.0709 | 0 | 0 | 0 | 0 | 21.5354 | 0 | 0 | 0 | 0 | 0 | 61.2791
6389 | 42.9723 | 0 | 0 | 0 | 0 | 21.4862 | 0 | 0 | 0 | 0 | 0 | 86.1028
6390 | 60.6906 | 0 | 0 | 0 | 0 | 30.3453 | 0 | 0 | 0 | 0 | 0 | 92.0554
6391 | 88.3936 | 0 | 42.9 | 3.2 | 56.3 | 44.1968 | 0 | 0 | 0 | 0 | 95.3 | 151.8853
6392 | 165.948 | 0.7 | 43 | 6 | 37.6 | 82.974 | 0 | 0 | 0 | 0 | 55.8 | 167.8807
6393 | 274.2225 | 2.1 | 43.2 | 0 | 0 | 137.1113 | 0 | 0 | 0 | 0 | 0 | 96.5937
6394 | 342.2951 | 3.5 | 43.4 | 0 | 0 | 171.1476 | 0 | 0 | 0 | 0 | 0 | 84.2085
6395 | 325.1276 | 3.5 | 43.4 | 0 | 0 | 162.5638 | 0 | 0 | 0 | 0 | 0 | 106.5513
6396 | 277.9571 | 2.8 | 43.3 | 0 | 0 | 138.9785 | 0 | 0 | 0 | 0 | 0 | 139.7059
6397 | 240.0483 | 1.4 | 43.1 | 0 | 75.1 | 120.0242 | 0 | 0 | 4.1 | 0 | 0 | 147.5543
6398 | 206.1183 | 2.1 | 43.2 | 0 | 37.6 | 103.0591 | 0 | 0 | 41.4 | 0 | 0 | 52.8794
6399 | 176.6599 | 3.5 | 43.4 | 0 | 0 | 88.3299 | 0 | 0 | 75.9 | 0 | 0 | 91.5772
6400 | 152.8882 | 2.8 | 43.3 | 0 | 0 | 76.4441 | 0 | 0 | 90.9 | 0 | 0 | 88.8381
6401 | 96.8505 | 2.1 | 43.2 | 0 | 0 | 48.4252 | 0 | 0 | 94.4 | 0 | 0 | 112.9639
6402 | 78.6354 | 0.7 | 43 | 0 | 37.6 | 39.3177 | 0 | 0 | 70 | 0 | 0 | 253.3699
6403 | 56.9421 | 0 | 42.9 | 0 | 75.1 | 28.471 | 0 | 0 | 0.1 | 0 | 0 | 140.0799
6404 | 43.8311 | 0 | 42.9 | 0 | 75.1 | 21.9155 | 0 | 0 | 0 | 0 | 0 | 222.6919
6405 | 39.7417 | 0 | 42.9 | 0 | 75.1 | 19.8708 | 0 | 0 | 0 | 0 | 0 | 185.4046
6406 | 41.1698 | 0 | 42.9 | 0 | 93.9 | 20.5849 | 0 | 0 | 0 | 0 | 0 | 146.4235
6407 | 41.0601 | 0 | 0 | 0 | 0 | 20.53 | 0 | 0 | 0 | 0 | 0 | 146.6958
6408 | 42.902 | 0 | 0 | 0 | 0 | 21.451 | 0 | 0 | 0 | 0 | 0 | 107.5205
6409 | 44.8839 | 0 | 0 | 0 | 0 | 22.442 | 0 | 0 | 0 | 0 | 0 | 109.571
6410 | 40.4635 | 0 | 0 | 0 | 0 | 20.2317 | 0 | 0 | 0 | 0 | 0 | 85.8661
6411 | 44.0484 | 0 | 0 | 0 | 0 | 22.0242 | 0 | 0 | 0 | 0 | 0 | 84.6882
6412 | 43.5779 | 0 | 0 | 0 | 0 | 21.7889 | 0 | 0 | 0 | 0 | 0 | 82.7911
6413 | 43.8791 | 0 | 0 | 0 | 0 | 21.9396 | 0 | 0 | 0 | 0 | 0 | 85.1588
6414 | 69.2745 | 0 | 0 | 0 | 0 | 34.6372 | 0 | 0 | 0 | 0 | 0 | 117.3534
6415 | 114.9472 | 0 | 42.9 | 0 | 56.3 | 57.4736 | 0 | 0 | 0 | 0 | 0 | 118.6573
6416 | 166.8397 | 0.7 | 43 | 0 | 37.6 | 83.4198 | 0 | 0 | 0 | 0 | 0 | 110.7796
6417 | 256.2365 | 2.1 | 43.2 | 0 | 0 | 128.1182 | 0 | 0 | 0 | 0 | 0 | 90.1459
6418 | 273.2531 | 3.5 | 43.4 | 0 | 0 | 136.6265 | 0 | 0 | 0 | 0 | 0 | 94.0831
6419 | 250.8826 | 3.5 | 43.4 | 0 | 0 | 125.4413 | 0 | 0 | 0 | 0 | 0 | 114.5295
6420 | 236.667 | 2.8 | 43.3 | 0 | 0 | 118.3335 | 0 | 0 | 0 | 0 | 0 | 139.3355
6421 | 234.3033 | 1.4 | 43.1 | 0 | 75.1 | 117.1516 | 0 | 0 | 0 | 0 | 0 | 201.538
6422 | 231.836 | 2.1 | 43.2 | 0 | 37.6 | 115.918 | 0 | 0 | 0 | 0 | 0 | 195.5017
6423 | 236.046 | 3.5 | 43.4 | 0 | 0 | 118.023 | 0 | 0 | 0 | 0 | 0 | 215.8497
6424 | 223.0267 | 2.8 | 43.3 | 0 | 0 | 111.5134 | 0 | 0 | 0 | 0 | 0 | 179.4103
6425 | 158.6658 | 2.1 | 43.2 | 0 | 0 | 79.3329 | 0 | 0 | 0 | 0 | 0 | 143.8774
6426 | 164.2794 | 0.7 | 43 | 0 | 37.6 | 82.1397 | 0 | 0 | 0 | 0 | 0 | 161.7191
6427 | 123.316 | 0 | 42.9 | 0 | 75.1 | 61.658 | 0 | 0 | 0 | 0 | 0 | 297.7837
6428 | 66.3064 | 0 | 42.9 | 0 | 75.1 | 33.1532 | 0 | 0 | 0 | 0 | 0 | 287.43
6429 | 41.5036 | 0 | 42.9 | 0 | 75.1 | 20.7518 | 0 | 0 | 0 | 0 | 0 | 243.2549
6430 | 41.974 | 0 | 42.9 | 0 | 93.9 | 20.987 | 0 | 0 | 0 | 0 | 0 | 223.8549
6431 | 42.4668 | 0 | 0 | 0 | 0 | 21.2334 | 0 | 0 | 0 | 0 | 0 | 155.0087
6432 | 43.0721 | 0 | 0 | 0 | 0 | 21.536 | 0 | 0 | 0 | 0 | 0 | 109.939
6433 | 42.5465 | 0 | 0 | 0 | 0 | 21.2732 | 0 | 0 | 0 | 0 | 0 | 84.4453
6434 | 42.1997 | 0 | 0 | 0 | 0 | 21.0998 | 0 | 0 | 0 | 0 | 0 | 48.9744
6435 | 39.9992 | 0 | 0 | 0 | 0 | 19.9996 | 0 | 0 | 0 | 0 | 0 | 48.5149
6436 | 42.685 | 0 | 0 | 0 | 0 | 21.3425 | 0 | 0 | 0 | 0 | 0 | 53.9125
6437 | 41.0322 | 0 | 0 | 0 | 0 | 20.5161 | 0 | 0 | 0 | 0 | 0 | 53.5691
6438 | 60.4981 | 0 | 0 | 0 | 0 | 30.2491 | 0 | 0 | 0 | 0 | 0 | 74.8559
6439 | 100.2959 | 0 | 42.9 | 7.4 | 56.3 | 50.1479 | 0 | 0 | 0 | 0 | 42 | 74.9715
6440 | 128.4158 | 0.7 | 43 | 12.6 | 37.6 | 64.2079 | 0 | 0 | 0 | 0 | 29.6 | 68.7472
6441 | 178.1617 | 2.1 | 43.2 | 0 | 0 | 89.0809 | 0 | 0 | 0 | 0 | 0 | 50.9261
6442 | 205.1439 | 3.5 | 43.4 | 0 | 0 | 102.572 | 0 | 0 | 0 | 0 | 0 | 90.8587
6443 | 198.1331 | 3.5 | 43.4 | 0 | 0 | 99.0666 | 0 | 0 | 0 | 0 | 0 | 131.6055
6444 | 184.19 | 2.8 | 43.3 | 0 | 0 | 92.095 | 0 | 0 | 0 | 0 | 0 | 146.3804
6445 | 158.4222 | 1.4 | 43.1 | 0 | 75.1 | 79.2111 | 0 | 0 | 0 | 0 | 0 | 177.9889
6446 | 159.7527 | 2.1 | 43.2 | 0 | 37.6 | 79.8763 | 0 | 0 | 0 | 0 | 0 | 130.0305
6447 | 155.1695 | 3.5 | 43.4 | 0 | 0 | 77.5848 | 0 | 0 | 0 | 0 | 0 | 117.9528
6448 | 119.7996 | 2.8 | 43.3 | 0 | 0 | 59.8998 | 0 | 0 | 1.8 | 0 | 0 | 99.3511
6449 | 89.7855 | 2.1 | 43.2 | 0 | 0 | 44.8927 | 0 | 0 | 4.9 | 0 | 0 | 97.9194
6450 | 91.8709 | 0.7 | 43 | 0 | 37.6 | 45.9355 | 0 | 0 | 0.9 | 0 | 0 | 107.5214
6451 | 52.6211 | 0 | 42.9 | 0 | 75.1 | 26.3106 | 0 | 0 | 0 | 0 | 0 | 156.4597
6452 | 44.2362 | 0 | 42.9 | 0 | 75.1 | 22.1181 | 0 | 0 | 0 | 0 | 0 | 247.499
6453 | 41.5656 | 0 | 42.9 | 0 | 75.1 | 20.7828 | 0 | 0 | 0 | 0 | 0 | 255.5701
6454 | 43.3771 | 0 | 42.9 | 0 | 93.9 | 21.6885 | 0 | 0 | 0 | 0 | 0 | 216.4842
6455 | 42.0224 | 0 | 0 | 0 | 0 | 21.0112 | 0 | 0 | 0 | 0 | 0 | 138.5067
6456 | 41.8668 | 0 | 0 | 0 | 0 | 20.9334 | 0 | 0 | 0 | 0 | 0 | 90.6212
6457 | 41.6368 | 0 | 0 | 0 | 0 | 20.8184 | 0 | 0 | 0 | 0 | 0 | 58.5186
6458 | 39.7324 | 0 | 0 | 0 | 0 | 19.8662 | 0 | 0 | 0 | 0 | 0 | 51.0408
6459 | 40.4774 | 0 | 0 | 0 | 0 | 20.2387 | 0 | 0 | 0 | 0 | 0 | 46.1072
6460 | 41.0124 | 0 | 0 | 0 | 0 | 20.5062 | 0 | 0 | 0 | 0 | 0 | 50.81
6461 | 40.0767 | 0 | 0 | 0 | 0 | 20.0383 | 0 | 0 | 0 | 0 | 0 | 84.6871
6462 | 65.4652 | 0 | 0 | 0 | 0 | 32.7326 | 0 | 0 | 0 | 0 | 0 | 74.3926
6463 | 110.5311 | 0 | 42.9 | 0 | 56.3 | 55.2655 | 0 | 0 | 0 | 0 | 9.9 | 89.546
6464 | 163.5253 | 0.7 | 43 | 0 | 37.6 | 81.7627 | 0 | 0 | 0 | 0 | 10 | 75.5591
6465 | 242.4301 | 2.1 | 43.2 | 0 | 0 | 121.215 | 0 | 0 | 0 | 0 | 0 | 83.2682
6466 | 296.0321 | 3.5 | 43.4 | 0 | 0 | 148.016 | 0 | 0 | 0 | 0 | 0 | 154.2365
6467 | 314.7675 | 3.5 | 43.4 | 0 | 0 | 157.3838 | 0 | 0 | 0 | 0 | 0 | 130.0413
6468 | 270.8568 | 2.8 | 43.3 | 0 | 0 | 135.4284 | 0 | 0 | 0 | 0 | 0 | 166.7516
6469 | 240.3396 | 1.4 | 43.1 | 0 | 75.1 | 120.1698 | 0 | 0 | 0 | 0 | 0 | 295.1498
6470 | 209.9179 | 2.1 | 43.2 | 0 | 37.6 | 104.959 | 0 | 0 | 0 | 0 | 0 | 143.2013
6471 | 206.0761 | 3.5 | 43.4 | 0 | 0 | 103.0381 | 0 | 0 | 0 | 0 | 0 | 166.558
6472 | 178.2842 | 2.8 | 43.3 | 0 | 0 | 89.1421 | 0 | 0 | 0 | 0 | 0 | 144.4896
6473 | 132.1863 | 2.1 | 43.2 | 0 | 0 | 66.0931 | 0 | 0 | 0 | 0 | 0 | 115.8798
6474 | 133.0203 | 0.7 | 43 | 0 | 37.6 | 66.5101 | 0 | 0 | 0 | 0 | 0 | 143.0006
6475 | 92.0055 | 0 | 42.9 | 0 | 75.1 | 46.0027 | 0 | 0 | 0 | 0 | 0 | 463.4536
6476 | 59.6136 | 0 | 42.9 | 0 | 75.1 | 29.8068 | 0 | 0 | 0 | 0 | 0 | 173.463
6477 | 44.5275 | 0 | 42.9 | 0 | 75.1 | 22.2637 | 0 | 0 | 0 | 0 | 0 | 295.5174
6478 | 42.981 | 0 | 42.9 | 0 | 93.9 | 21.4905 | 0 | 0 | 0 | 0 | 0 | 221.5971
6479 | 41.5628 | 0 | 0 | 0 | 0 | 20.7814 | 0 | 0 | 0 | 0 | 0 | 123.6219
6480 | 42.9943 | 0 | 0 | 0 | 0 | 21.4972 | 0 | 0 | 0 | 0 | 0 | 83.1494
6481 | 42.381 | 0 | 0 | 0 | 0 | 21.1905 | 0 | 0 | 0 | 0 | 0 | 67.5997
6482 | 43.0647 | 0 | 0 | 0 | 0 | 21.5323 | 0 | 0 | 0 | 0 | 0 | 58.7493
6483 | 40.5084 | 0 | 0 | 0 | 0 | 20.2542 | 0 | 0 | 0 | 0 | 0 | 47.7114
6484 | 44.0276 | 0 | 0 | 0 | 0 | 22.0138 | 0 | 0 | 0 | 0 | 0 | 51.0418
6485 | 42.0844 | 0 | 0 | 0 | 0 | 21.0422 | 0 | 0 | 0 | 0 | 0 | 63.8072
6486 | 54.891 | 0 | 0 | 0 | 0 | 27.4455 | 0 | 0 | 0 | 0 | 0 | 88.4804
6487 | 92.2193 | 0 | 42.9 | 11.9 | 56.3 | 46.1096 | 0 | 0 | 0 | 0 | 117.4 | 84.0902
6488 | 144.1307 | 0.7 | 43 | 19.1 | 37.6 | 72.0653 | 0 | 0 | 0 | 0 | 92.9 | 59.5521
6489 | 238.8697 | 2.1 | 43.2 | 2.5 | 0 | 119.4348 | 0 | 0 | 0 | 0 | 0 | 54.7148
6490 | 300.9022 | 3.5 | 43.4 | 0 | 0 | 150.4511 | 0 | 0 | 0 | 0 | 0 | 50.9271
6491 | 287.8449 | 3.5 | 43.4 | 0 | 0 | 143.9224 | 0 | 0 | 0 | 0 | 0 | 66.5629
6492 | 305.4677 | 2.8 | 43.3 | 0 | 0 | 152.7338 | 0 | 0 | 0 | 0 | 0 | 176.4379
6493 | 303.3562 | 1.4 | 43.1 | 0 | 75.1 | 151.6781 | 0 | 0 | 0 | 0 | 0 | 156.8385
6494 | 337.2124 | 2.1 | 43.2 | 0 | 37.6 | 168.6062 | 0 | 0 | 0 | 0 | 0 | 130.1904
6495 | 317.6603 | 3.5 | 43.4 | 0 | 0 | 158.8302 | 0 | 0 | 0 | 0 | 0 | 107.6392
6496 | 257.8605 | 2.8 | 43.3 | 0 | 0 | 128.9302 | 0 | 0 | 0 | 0 | 0 | 118.7218
6497 | 165.5761 | 2.1 | 43.2 | 0 | 0 | 82.788 | 0 | 0 | 0 | 0 | 0 | 127.8935
6498 | 113.983 | 0.7 | 43 | 0 | 37.6 | 56.9915 | 0 | 0 | 0 | 0 | 0 | 107.2717
6499 | 74.8395 | 0 | 42.9 | 0 | 75.1 | 37.4197 | 0 | 0 | 0 | 0 | 0 | 221.9988
6500 | 57.5746 | 0 | 42.9 | 0 | 75.1 | 28.7873 | 0 | 0 | 0 | 0 | 0 | 176.3724
6501 | 43.9086 | 0 | 42.9 | 0 | 75.1 | 21.9543 | 0 | 0 | 0 | 0 | 0 | 190.0943
6502 | 44.2486 | 0 | 42.9 | 0 | 93.9 | 22.1243 | 0 | 0 | 0 | 0 | 0 | 170.3878
6503 | 43.77 | 0 | 0 | 0 | 0 | 21.885 | 0 | 0 | 0 | 0 | 0 | 136.6485
6504 | 39.4414 | 0 | 0 | 0 | 0 | 19.7207 | 0 | 0 | 0 | 0 | 0 | 111.1445
6505 | 41.4819 | 0 | 0 | 0 | 0 | 20.7409 | 0 | 0 | 0 | 0 | 0 | 70.5884
6506 | 41.1239 | 0 | 0 | 0 | 0 | 20.562 | 0 | 0 | 0 | 0 | 0 | 57.246
6507 | 40.2602 | 0 | 0 | 0 | 0 | 20.1301 | 0 | 0 | 0 | 0 | 0 | 51.845
6508 | 42.4284 | 0 | 0 | 0 | 0 | 21.2142 | 0 | 0 | 0 | 0 | 0 | 46.1077
6509 | 41.9396 | 0 | 0 | 0 | 0 | 20.9698 | 0 | 0 | 0 | 0 | 0 | 47.0194
6510 | 45.4102 | 0 | 0 | 0 | 0 | 22.7051 | 0 | 0 | 0 | 0 | 0 | 85.2784
6511 | 62.9629 | 0 | 42.9 | 6.4 | 56.3 | 31.4815 | 0 | 0 | 0 | 0 | 130.7 | 108.8485
6512 | 70.0533 | 0 | 42.9 | 2.8 | 37.6 | 35.0267 | 0 | 0 | 0 | 0 | 82.2 | 93.368
6513 | 64.224 | 0 | 42.9 | 0 | 0 | 32.112 | 0 | 0 | 0 | 0 | 0 | 88.7184
6514 | 62.5151 | 0 | 42.9 | 0 | 0 | 31.2575 | 0 | 0 | 0 | 0 | 0 | 71.8583
6515 | 62.092 | 0 | 42.9 | 0 | 0 | 31.046 | 0 | 0 | 0 | 0 | 0 | 194.1248
6516 | 62.8262 | 0 | 42.9 | 0 | 0 | 31.4131 | 0 | 0 | 0 | 0 | 0 | 108.9683
6517 | 58.1176 | 0 | 42.9 | 0 | 75.1 | 29.0588 | 0 | 0 | 0 | 0 | 0 | 126.3958
6518 | 54.5615 | 0 | 42.9 | 0 | 37.6 | 27.2808 | 0 | 0 | 1.9 | 0 | 0 | 202.5764
6519 | 50.377 | 0 | 42.9 | 0 | 0 | 25.1885 | 0 | 0 | 18 | 0 | 0 | 228.535
6520 | 53.7957 | 0 | 42.9 | 0 | 0 | 26.8979 | 0 | 0 | 32.1 | 0 | 0 | 133.3509
6521 | 54.856 | 0 | 42.9 | 0 | 0 | 27.428 | 0 | 0 | 34.3 | 0 | 0 | 198.5296
6522 | 60.2644 | 0 | 42.9 | 0 | 37.6 | 30.1322 | 0 | 0 | 15.7 | 0 | 0 | 139.7216
6523 | 43.0864 | 0 | 42.9 | 0 | 75.1 | 21.5432 | 0 | 0 | 0 | 0 | 0 | 183.1416
6524 | 45.0612 | 0 | 42.9 | 0 | 75.1 | 22.5306 | 0 | 0 | 0 | 0 | 0 | 233.4528
6525 | 40.408 | 0 | 42.9 | 0 | 75.1 | 20.204 | 0 | 0 | 0 | 0 | 0 | 170.2453
6526 | 43.2971 | 0 | 42.9 | 0 | 93.9 | 21.6486 | 0 | 0 | 0 | 0 | 0 | 156.5324
6527 | 44.3539 | 0 | 0 | 0 | 0 | 22.177 | 0 | 0 | 0 | 0 | 0 | 163.1517
6528 | 43.8516 | 0 | 0 | 0 | 0 | 21.9258 | 0 | 0 | 0 | 0 | 0 | 194.1796
6529 | 40.7638 | 0 | 0 | 0 | 0 | 20.3819 | 0 | 0 | 0 | 0 | 0 | 70.1275
6530 | 41.4016 | 0 | 0 | 0 | 0 | 20.7008 | 0 | 0 | 0 | 0 | 0 | 57.0169
6531 | 44.6601 | 0 | 0 | 0 | 0 | 22.3301 | 0 | 0 | 0 | 0 | 0 | 47.5949
6532 | 42.2223 | 0 | 0 | 0 | 0 | 21.1111 | 0 | 0 | 0 | 0 | 0 | 47.4798
6533 | 40.871 | 0 | 0 | 0 | 0 | 20.4355 | 0 | 0 | 0 | 0 | 0 | 56.4377
6534 | 55.279 | 0 | 0 | 0 | 0 | 27.6395 | 0 | 0 | 0 | 0 | 0 | 128.4647
6535 | 76.5022 | 0 | 42.9 | 0 | 56.3 | 38.2511 | 0 | 0 | 0 | 0 | 0 | 86.1045
6536 | 72.0371 | 0 | 42.9 | 0 | 37.6 | 36.0186 | 0 | 0 | 0 | 0 | 1.4 | 54.0264
6537 | 68.0872 | 0 | 42.9 | 0 | 0 | 34.0436 | 0 | 0 | 0 | 0 | 0 | 151.3222
6538 | 63.6968 | 0 | 42.9 | 0 | 0 | 31.8484 | 0 | 0 | 0 | 0 | 0 | 99.8322
6539 | 61.903 | 0 | 42.9 | 0 | 0 | 30.9515 | 0 | 0 | 0 | 0 | 0 | 286.0215
6540 | 58.1021 | 0 | 42.9 | 0 | 0 | 29.0511 | 0 | 0 | 0 | 0 | 0 | 164.5217
6541 | 59.9028 | 0 | 42.9 | 0 | 75.1 | 29.9514 | 0 | 0 | 0 | 0 | 0 | 136.3246
6542 | 58.6364 | 0 | 42.9 | 0 | 37.6 | 29.3182 | 0 | 0 | 0 | 0 | 0 | 149.6596
6543 | 59.0471 | 0 | 42.9 | 0 | 0 | 29.5235 | 0 | 0 | 0 | 0 | 0 | 183.5133
6544 | 61.828 | 0 | 42.9 | 0 | 0 | 30.914 | 0 | 0 | 0 | 0 | 0 | 190.1959
6545 | 60.7522 | 0 | 42.9 | 0 | 0 | 30.3761 | 0 | 0 | 0 | 0 | 0 | 218.3573
6546 | 69.5866 | 0 | 42.9 | 0 | 37.6 | 34.7933 | 0 | 0 | 0 | 0 | 0 | 150.8178
6547 | 62.1407 | 0 | 42.9 | 0 | 75.1 | 31.0704 | 0 | 0 | 0 | 0 | 0 | 230.3689
6548 | 49.8988 | 0 | 42.9 | 0 | 75.1 | 24.9494 | 0 | 0 | 0 | 0 | 0 | 350.846
6549 | 40.951 | 0 | 42.9 | 0 | 75.1 | 20.4755 | 0 | 0 | 0 | 0 | 0 | 153.6913
6550 | 41.7614 | 0 | 42.9 | 0 | 93.9 | 20.8807 | 0 | 0 | 0 | 0 | 0 | 154.6076
6551 | 42.605 | 0 | 0 | 0 | 0 | 21.3025 | 0 | 0 | 0 | 0 | 0 | 165.2659
6552 | 43.6941 | 0 | 0 | 0 | 0 | 21.8471 | 0 | 0 | 0 | 0 | 0 | 214.8253
6553 | 39.7658 | 0 | 0 | 0 | 0 | 19.8829 | 0 | 0 | 0 | 0 | 0 | 80.4243
6554 | 43.5925 | 0 | 0 | 0 | 0 | 21.7962 | 0 | 0 | 0 | 0 | 0 | 74.2774
6555 | 44.1677 | 0 | 0 | 0 | 0 | 22.0838 | 0 | 0 | 0 | 0 | 0 | 75.0906
6556 | 40.3215 | 0 | 0 | 0 | 0 | 20.1608 | 0 | 0 | 0 | 0 | 0 | 75.7932
6557 | 42.2226 | 0 | 0 | 0 | 0 | 21.1113 | 0 | 0 | 0 | 0 | 0 | 75.4416
6558 | 57.3106 | 0 | 0 | 0 | 0 | 28.6553 | 0 | 0 | 0 | 0 | 0 | 82.9109
6559 | 99.0568 | 0 | 42.9 | 27.8 | 56.3 | 49.5284 | 0 | 0 | 0 | 0 | 200.9 | 96.4676
6560 | 193.8345 | 0.7 | 43 | 66.3 | 37.6 | 96.9173 | 0 | 0 | 0 | 0.9 | 200 | 117.3556
6561 | 313.2746 | 2.1 | 43.2 | 65.6 | 0 | 156.6373 | 0 | 0 | 0 | 3.2 | 0 | 221.0209
6562 | 329.5325 | 3.5 | 43.4 | 69.2 | 0 | 164.7663 | 0 | 0 | 0 | 23.4 | 0 | 82.7927
6563 | 336.8672 | 3.5 | 43.4 | 53.1 | 0 | 168.4336 | 0 | 0 | 0 | 19.5 | 0 | 86.1034
6564 | 299.1462 | 2.8 | 43.3 | 22.4 | 0 | 149.5731 | 0 | 0 | 0 | 2.4 | 0 | 131.8006
6565 | 294.5324 | 1.4 | 43.1 | 4 | 75.1 | 147.2662 | 0 | 0 | 0 | 0 | 128.8 | 151.3842
6566 | 275.8747 | 2.1 | 43.2 | 0 | 37.6 | 137.9374 | 0 | 0 | 0 | 0 | 67.3 | 114.2864
6567 | 230.9756 | 3.5 | 43.4 | 0 | 0 | 115.4878 | 0 | 0 | 0 | 0 | 0 | 122.5777
6568 | 197.7355 | 2.8 | 43.3 | 0 | 0 | 98.8678 | 0 | 0 | 0 | 0 | 0 | 139.4147
6569 | 183.961 | 2.1 | 43.2 | 0 | 0 | 91.9805 | 0 | 0 | 0 | 0 | 0 | 142.3294
6570 | 151.3866 | 0.7 | 43 | 0 | 37.6 | 75.6933 | 0 | 0 | 0 | 0 | 115.4 | 203.2633
6571 | 96.4717 | 0 | 42.9 | 0 | 75.1 | 48.2359 | 0 | 0 | 0 | 0 | 101.5 | 218.2042
6572 | 61.3699 | 0 | 42.9 | 0 | 75.1 | 30.685 | 0 | 0 | 0 | 0 | 58.8 | 393.8523
6573 | 40.7533 | 0 | 42.9 | 0 | 75.1 | 20.3766 | 0 | 0 | 0 | 0 | 126.7 | 225.3112
6574 | 43.2674 | 0 | 42.9 | 0 | 93.9 | 21.6337 | 0 | 0 | 0 | 0 | 155.1 | 244.751
6575 | 43.8984 | 0 | 0 | 0 | 0 | 21.9492 | 0 | 0 | 0 | 0 | 0 | 177.7553
6576 | 42.411 | 0 | 0 | 0 | 0 | 21.2055 | 0 | 0 | 0 | 0 | 0 | 117.5698
6577 | 42.2068 | 0 | 0 | 0 | 0 | 21.1034 | 0 | 0 | 0 | 0 | 0 | 81.9634
6578 | 40.5574 | 0 | 0 | 0 | 0 | 20.2787 | 0 | 0 | 0 | 0 | 0 | 75.6761
6579 | 40.7049 | 0 | 0 | 0 | 0 | 20.3525 | 0 | 0 | 0 | 0 | 0 | 75.9107
6580 | 41.5429 | 0 | 0 | 0 | 0 | 20.7715 | 0 | 0 | 0 | 0 | 0 | 79.1226
6581 | 41.3235 | 0 | 0 | 0 | 0 | 20.6618 | 0 | 0 | 0 | 0 | 1.3 | 100.9039
6582 | 65.3444 | 0 | 0 | 0 | 0 | 32.6722 | 0 | 0 | 0 | 0 | 4.2 | 129.9539
6583 | 114.3475 | 0 | 42.9 | 100.3 | 56.3 | 57.1737 | 0 | 0 | 0 | 0 | 420.5 | 96.9548
6584 | 193.3696 | 0.7 | 43 | 135.2 | 37.6 | 96.6848 | 0 | 0 | 0 | 37.4 | 358.2 | 126.8541
6585 | 277.1212 | 2.1 | 43.2 | 123.4 | 0 | 138.5606 | 0 | 0 | 0 | 31 | 7.1 | 107.6419
6586 | 269.0812 | 3.5 | 43.4 | 119.7 | 0 | 134.5406 | 0 | 0 | 0 | 46.1 | 12.4 | 134.4646
6587 | 269.8709 | 3.5 | 43.4 | 105.8 | 0 | 134.9355 | 0 | 0 | 0 | 27.6 | 11.6 | 202.5255
6588 | 261.9573 | 2.8 | 43.3 | 90.6 | 0 | 130.9787 | 0 | 0 | 0 | 1.1 | 10.4 | 298.3642
6589 | 253.4521 | 1.4 | 43.1 | 77.9 | 75.1 | 126.7261 | 0 | 0 | 0 | 0 | 398 | 260.896
6590 | 249.1352 | 2.1 | 43.2 | 72.3 | 37.6 | 124.5676 | 0 | 0 | 0 | 0 | 319.1 | 98.7519
6591 | 240.494 | 3.5 | 43.4 | 72.5 | 0 | 120.247 | 0 | 0 | 0 | 0 | 1.1 | 107.7606
6592 | 270.3268 | 2.8 | 43.3 | 70.3 | 0 | 135.1634 | 0 | 0 | 0 | 0 | 4.1 | 102.4563
6593 | 224.2289 | 2.1 | 43.2 | 66.7 | 0 | 112.1145 | 0 | 0 | 0 | 0 | 7.6 | 115.592
6594 | 129.5622 | 0.7 | 43 | 72.5 | 37.6 | 64.7811 | 0 | 0 | 0 | 0 | 423.3 | 190.2465
6595 | 74.5184 | 0 | 42.9 | 32.9 | 75.1 | 37.2592 | 0 | 0 | 0 | 0 | 347.1 | 174.9612
6596 | 47.2359 | 0 | 42.9 | 10.9 | 75.1 | 23.618 | 0 | 0 | 0 | 0 | 292.4 | 303.098
6597 | 40.5245 | 0 | 42.9 | 22.3 | 75.1 | 20.2623 | 0 | 0 | 0 | 0 | 349.8 | 227.6727
6598 | 42.4678 | 0 | 42.9 | 37 | 93.9 | 21.2339 | 0 | 0 | 0 | 0 | 383 | 185.96
6599 | 43.2156 | 0 | 0 | 0 | 0 | 21.6078 | 0 | 0 | 0 | 0 | 3.5 | 157.5306
6600 | 41.7862 | 0 | 0 | 0 | 0 | 20.8931 | 0 | 0 | 0 | 0 | 29.7 | 125.0172
6601 | 42.3599 | 0 | 0 | 2.8 | 0 | 21.1799 | 0 | 0 | 0 | 0 | 71.9 | 64.1501
6602 | 41.2017 | 0 | 0 | 9.7 | 0 | 20.6009 | 0 | 0 | 0 | 0 | 114 | 56.7841
6603 | 42.4011 | 0 | 0 | 17.9 | 0 | 21.2006 | 0 | 0 | 0 | 0 | 152.6 | 58.2852
6604 | 44.5926 | 0 | 0 | 29 | 0 | 22.2963 | 0 | 0 | 0 | 0 | 185.3 | 61.7415
6605 | 41.8907 | 0 | 0 | 41.1 | 0 | 20.9453 | 0 | 0 | 0 | 0 | 214.5 | 69.7841
6606 | 64.6889 | 0 | 0 | 53.9 | 0 | 32.3444 | 0 | 0 | 0 | 0 | 234.8 | 61.0499
6607 | 96.041 | 0 | 42.9 | 222.6 | 56.3 | 48.0205 | 0 | 0 | 0 | 0 | 737.5 | 105.3414
6608 | 124.3099 | 0.7 | 43 | 217.1 | 37.6 | 62.155 | 0 | 0 | 0 | 29.6 | 620.7 | 58.0559
6609 | 217.9136 | 2.1 | 43.2 | 155.7 | 0 | 108.9568 | 0 | 0 | 0 | 18.9 | 93.5 | 51.9585
6610 | 296.2825 | 3.5 | 43.4 | 98.7 | 0 | 148.1413 | 0 | 0 | 0 | 24.7 | 58.6 | 97.4336
6611 | 276.1186 | 3.5 | 43.4 | 45.2 | 0 | 138.0593 | 0 | 0 | 0 | 6.4 | 10.6 | 118.565
6612 | 263.1149 | 2.8 | 43.3 | 4.4 | 0 | 131.5575 | 0 | 0 | 0 | 0 | 0.6 | 107.8874
6613 | 257.7529 | 1.4 | 43.1 | 0 | 75.1 | 128.8765 | 0 | 0 | 0 | 0 | 283.4 | 63.1186
6614 | 234.4539 | 2.1 | 43.2 | 0 | 37.6 | 117.2269 | 0 | 0 | 0 | 0 | 172.7 | 72.2034
6615 | 221.156 | 3.5 | 43.4 | 0 | 0 | 110.578 | 0 | 0 | 0 | 0 | 0 | 133.8821
6616 | 180.8537 | 2.8 | 43.3 | 0 | 0 | 90.4269 | 0 | 0 | 0 | 0 | 0 | 177.5014
6617 | 123.2512 | 2.1 | 43.2 | 0 | 0 | 61.6256 | 0 | 0 | 0 | 0 | 0 | 82.4351
6618 | 84.9209 | 0.7 | 43 | 0 | 37.6 | 42.4605 | 0 | 0 | 0 | 0 | 146.5 | 161.2555
6619 | 51.6839 | 0 | 42.9 | 0 | 75.1 | 25.842 | 0 | 0 | 0 | 0 | 134.4 | 264.7942
6620 | 43.3188 | 0 | 42.9 | 0 | 75.1 | 21.6594 | 0 | 0 | 0 | 0 | 106.5 | 346.6079
6621 | 42.2592 | 0 | 42.9 | 0 | 75.1 | 21.1296 | 0 | 0 | 0 | 0 | 169.1 | 235.6385
6622 | 43.6482 | 0 | 42.9 | 0 | 93.9 | 21.8241 | 0 | 0 | 0 | 0 | 193.7 | 183.2513
6623 | 43.7276 | 0 | 0 | 0 | 0 | 21.8638 | 0 | 0 | 0 | 0 | 0 | 132.7138
6624 | 41.4283 | 0 | 0 | 0 | 0 | 20.7141 | 0 | 0 | 0 | 0 | 0 | 82.5553
6625 | 41.4357 | 0 | 0 | 0 | 0 | 20.7179 | 0 | 0 | 0 | 0 | 0 | 70.3577
6626 | 42.3388 | 0 | 0 | 0 | 0 | 21.1694 | 0 | 0 | 0 | 0 | 0 | 67.2539
6627 | 41.6198 | 0 | 0 | 0 | 0 | 20.8099 | 0 | 0 | 0 | 0 | 0 | 60.4721
6628 | 40.0792 | 0 | 0 | 0 | 0 | 20.0396 | 0 | 0 | 0 | 0 | 0 | 56.3216
6629 | 44.3031 | 0 | 0 | 0 | 0 | 22.1516 | 0 | 0 | 0 | 0 | 1.1 | 97.0759
6630 | 61.6678 | 0 | 0 | 0 | 0 | 30.8339 | 0 | 0 | 0 | 0 | 4.1 | 74.048
6631 | 101.7668 | 0 | 42.9 | 96.2 | 56.3 | 50.8834 | 0 | 0 | 0 | 0 | 465.1 | 92.4083
6632 | 184.085 | 0.7 | 43 | 129.5 | 37.6 | 92.0425 | 0 | 0 | 0 | 0 | 385.9 | 61.7411
6633 | 261.4237 | 2.1 | 43.2 | 117.8 | 0 | 130.7118 | 0 | 0 | 0 | 1.6 | 10.3 | 116.4643
6634 | 286.0693 | 3.5 | 43.4 | 120.8 | 0 | 143.0347 | 0 | 0 | 0 | 24 | 27.7 | 131.3999
6635 | 299.8237 | 3.5 | 43.4 | 114.4 | 0 | 149.9118 | 0 | 0 | 0 | 23.8 | 35.7 | 84.0863
6636 | 282.6267 | 2.8 | 43.3 | 92.8 | 0 | 141.3133 | 0 | 0 | 0 | 6.8 | 24.2 | 104.9845
6637 | 271.8637 | 1.4 | 43.1 | 52 | 75.1 | 135.9319 | 0 | 0 | 0 | 0 | 391.5 | 90.3844
6638 | 277.4203 | 2.1 | 43.2 | 10.6 | 37.6 | 138.7102 | 0 | 0 | 0 | 0 | 256.3 | 118.3737
6639 | 247.5881 | 3.5 | 43.4 | 0 | 0 | 123.794 | 0 | 0 | 0 | 0 | 0 | 63.3469
6640 | 181.9168 | 2.8 | 43.3 | 0 | 0 | 90.9584 | 0 | 0 | 0 | 0 | 0 | 63.3476
6641 | 111.6834 | 2.1 | 43.2 | 0 | 0 | 55.8417 | 0 | 0 | 0 | 0 | 0 | 64.8405
6642 | 96.8731 | 0.7 | 43 | 0 | 37.6 | 48.4365 | 0 | 0 | 0 | 0 | 203.6 | 77.808
6643 | 69.4003 | 0 | 42.9 | 0 | 75.1 | 34.7002 | 0 | 0 | 0 | 0 | 161.7 | 216.0279
6644 | 50.9234 | 0 | 42.9 | 0 | 75.1 | 25.4617 | 0 | 0 | 0 | 0 | 116.8 | 218.5036
6645 | 39.0186 | 0 | 42.9 | 0 | 75.1 | 19.5093 | 0 | 0 | 0 | 0 | 177.3 | 289.2107
6646 | 41.639 | 0 | 42.9 | 0 | 93.9 | 20.8195 | 0 | 0 | 0 | 0 | 197.9 | 143.0082
6647 | 40.1855 | 0 | 0 | 0 | 0 | 20.0927 | 0 | 0 | 0 | 0 | 0 | 136.9642
6648 | 42.654 | 0 | 0 | 0 | 0 | 21.327 | 0 | 0 | 0 | 0 | 0 | 95.152
6649 | 40.726 | 0 | 0 | 0 | 0 | 20.363 | 0 | 0 | 0 | 0 | 0 | 65.8715
6650 | 42.058 | 0 | 0 | 0 | 0 | 21.029 | 0 | 0 | 0 | 0 | 0 | 59.2076
6651 | 40.5726 | 0 | 0 | 0 | 0 | 20.2863 | 0 | 0 | 0 | 0 | 0 | 58.0543
6652 | 43.3095 | 0 | 0 | 0 | 0 | 21.6548 | 0 | 0 | 0 | 0 | 1.4 | 51.156
6653 | 41.8479 | 0 | 0 | 0 | 0 | 20.924 | 0 | 0 | 0 | 0 | 7.8 | 52.8786
6654 | 62.9713 | 0 | 0 | 0 | 0 | 31.4856 | 0 | 0 | 0 | 0 | 16.5 | 99.2341
6655 | 92.7725 | 0 | 42.9 | 120.8 | 56.3 | 46.3863 | 0 | 0 | 0 | 0 | 508.2 | 70.588
6656 | 155.8306 | 0.7 | 43 | 148.8 | 37.6 | 77.9153 | 0 | 0 | 0 | 27.6 | 437.1 | 77.6821
6657 | 252.2738 | 2.1 | 43.2 | 131.1 | 0 | 126.1369 | 0 | 0 | 0 | 17.6 | 32.2 | 159.7641
6658 | 308.2065 | 3.5 | 43.4 | 114.2 | 0 | 154.1032 | 0 | 0 | 0 | 21.4 | 36.8 | 132.975
6659 | 299.444 | 3.5 | 43.4 | 68.6 | 0 | 149.722 | 0 | 0 | 0 | 5.7 | 7.4 | 178.1921
6660 | 270.7892 | 2.8 | 43.3 | 5.7 | 0 | 135.3946 | 0 | 0 | 0 | 0 | 0 | 183.4963
6661 | 262.1873 | 1.4 | 43.1 | 0 | 75.1 | 131.0937 | 0 | 0 | 0 | 0 | 200.8 | 142.438
6662 | 215.0199 | 2.1 | 43.2 | 0 | 37.6 | 107.5099 | 0 | 0 | 0 | 0 | 139.2 | 185.3082
6663 | 219.2215 | 3.5 | 43.4 | 0 | 0 | 109.6108 | 0 | 0 | 0 | 0 | 0 | 126.1122
6664 | 209.0604 | 2.8 | 43.3 | 0 | 0 | 104.5302 | 0 | 0 | 0 | 0 | 0 | 69.0929
6665 | 169.068 | 2.1 | 43.2 | 0 | 0 | 84.534 | 0 | 0 | 0 | 0 | 0 | 132.1081
6666 | 160.8374 | 0.7 | 43 | 0 | 37.6 | 80.4187 | 0 | 0 | 0 | 0 | 126.1 | 188.3481
6667 | 89.5397 | 0 | 42.9 | 0 | 75.1 | 44.7699 | 0 | 0 | 0 | 0 | 92.1 | 255.7637
6668 | 54.4274 | 0 | 42.9 | 0 | 75.1 | 27.2137 | 0 | 0 | 0 | 0 | 66.2 | 244.8798
6669 | 40.2248 | 0 | 42.9 | 0 | 75.1 | 20.1124 | 0 | 0 | 0 | 0 | 141.3 | 270.3527
6670 | 41.793 | 0 | 42.9 | 0 | 93.9 | 20.8965 | 0 | 0 | 0 | 0 | 174.1 | 166.8115
6671 | 41.1342 | 0 | 0 | 0 | 0 | 20.5671 | 0 | 0 | 0 | 0 | 0 | 127.0428
6672 | 42.5424 | 0 | 0 | 0 | 0 | 21.2712 | 0 | 0 | 0 | 0 | 0 | 101.1445
6673 | 42.2821 | 0 | 0 | 0 | 0 | 21.1411 | 0 | 0 | 0 | 0 | 0 | 93.1258
6674 | 43.4397 | 0 | 0 | 0 | 0 | 21.7198 | 0 | 0 | 0 | 0 | 0 | 68.2864
6675 | 40.4582 | 0 | 0 | 0 | 0 | 20.2291 | 0 | 0 | 0 | 0 | 1.4 | 56.6688
6676 | 42.7628 | 0 | 0 | 0 | 0 | 21.3814 | 0 | 0 | 0 | 0 | 12.1 | 50.6969
6677 | 42.999 | 0 | 0 | 0 | 0 | 21.4995 | 0 | 0 | 0 | 0 | 43.1 | 60.2418
6678 | 48.457 | 0 | 0 | 1 | 0 | 24.2285 | 0 | 0 | 0 | 0 | 77.1 | 90.7412
6679 | 75.0635 | 0 | 42.9 | 152.1 | 56.3 | 37.5318 | 0 | 0 | 0 | 0 | 579.3 | 105.1012
6680 | 76.0159 | 0 | 42.9 | 117.9 | 37.6 | 38.008 | 0 | 0 | 0 | 0 | 434.7 | 60.2438
6681 | 71.5434 | 0 | 42.9 | 43.6 | 0 | 35.7717 | 0 | 0 | 0 | 0 | 0 | 82.6719
6682 | 67.7171 | 0 | 42.9 | 0.7 | 0 | 33.8586 | 0 | 0 | 0 | 0 | 0 | 88.3602
6683 | 69.0036 | 0 | 42.9 | 0 | 0 | 34.5018 | 0 | 0 | 0 | 0 | 0 | 151.4132
6684 | 66.8146 | 0 | 42.9 | 0 | 0 | 33.4073 | 0 | 0 | 0 | 0 | 0 | 137.8842
6685 | 57.1931 | 0 | 42.9 | 0 | 75.1 | 28.5965 | 0 | 0 | 0 | 0 | 24.4 | 252.7947
6686 | 54.6895 | 0 | 42.9 | 0 | 37.6 | 27.3448 | 0 | 0 | 0 | 0 | 2.1 | 99.4697
6687 | 57.1082 | 0 | 42.9 | 0 | 0 | 28.5541 | 0 | 0 | 0 | 0 | 0 | 147.3811
6688 | 60.1798 | 0 | 42.9 | 0 | 0 | 30.0899 | 0 | 0 | 0 | 0 | 0 | 142.1079
6689 | 67.9384 | 0 | 42.9 | 0 | 0 | 33.9692 | 0 | 0 | 0 | 0 | 0 | 139.2713
6690 | 81.3156 | 0 | 42.9 | 0 | 37.6 | 40.6578 | 0 | 0 | 0 | 0 | 0 | 260.1332
6691 | 64.0458 | 0 | 42.9 | 0 | 75.1 | 32.0229 | 0 | 0 | 0 | 0 | 0 | 247.7722
6692 | 48.3752 | 0 | 42.9 | 0 | 75.1 | 24.1876 | 0 | 0 | 0 | 0 | 0 | 250.4848
6693 | 44.1159 | 0 | 42.9 | 0 | 75.1 | 22.058 | 0 | 0 | 0 | 0 | 0.9 | 213.9703
6694 | 41.5581 | 0 | 42.9 | 0 | 93.9 | 20.7791 | 0 | 0 | 0 | 0 | 12.5 | 187.0666
6695 | 42.8741 | 0 | 0 | 0 | 0 | 21.437 | 0 | 0 | 0 | 0 | 0 | 139.3552
6696 | 42.3692 | 0 | 0 | 0 | 0 | 21.1846 | 0 | 0 | 0 | 0 | 0 | 79.836
6697 | 40.7898 | 0 | 0 | 0 | 0 | 20.3949 | 0 | 0 | 0 | 0 | 0 | 50.5824
6698 | 40.8131 | 0 | 0 | 0 | 0 | 20.4065 | 0 | 0 | 0 | 0 | 0 | 46.562
6699 | 43.2615 | 0 | 0 | 0 | 0 | 21.6307 | 0 | 0 | 0 | 0 | 0 | 47.4784
6700 | 40.5413 | 0 | 0 | 0 | 0 | 20.2706 | 0 | 0 | 0 | 0 | 0 | 57.2469
6701 | 41.0799 | 0 | 0 | 0 | 0 | 20.54 | 0 | 0 | 0 | 0 | 0 | 61.3935
6702 | 46.0839 | 0 | 0 | 0 | 0 | 23.042 | 0 | 0 | 0 | 0 | 0 | 81.9618
6703 | 55.6109 | 0 | 42.9 | 36.4 | 56.3 | 27.8055 | 0 | 0 | 0 | 0 | 378.2 | 120.546
6704 | 63.641 | 0 | 42.9 | 14.9 | 37.6 | 31.8205 | 0 | 0 | 0 | 0 | 279.7 | 69.2073
6705 | 59.2231 | 0 | 42.9 | 0 | 0 | 29.6115 | 0 | 0 | 0 | 0 | 0 | 47.7088
6706 | 56.961 | 0 | 42.9 | 0 | 0 | 28.4805 | 0 | 0 | 0 | 0 | 0 | 69.8993
6707 | 52.5684 | 0 | 42.9 | 0 | 0 | 26.2842 | 0 | 0 | 0 | 0 | 0 | 142.3387
6708 | 50.0478 | 0 | 42.9 | 0 | 0 | 25.0239 | 0 | 0 | 0 | 0 | 0 | 175.1349
6709 | 49.7429 | 0 | 42.9 | 0 | 75.1 | 24.8714 | 0 | 0 | 0 | 0 | 0 | 283.0642
6710 | 51.3529 | 0 | 42.9 | 0 | 37.6 | 25.6765 | 0 | 0 | 0 | 0 | 0 | 258.287
6711 | 50.456 | 0 | 42.9 | 0 | 0 | 25.228 | 0 | 0 | 0 | 0 | 0 | 124.2656
6712 | 51.8578 | 0 | 42.9 | 0 | 0 | 25.9289 | 0 | 0 | 0 | 0 | 0 | 104.0121
6713 | 58.549 | 0 | 42.9 | 0 | 0 | 29.2745 | 0 | 0 | 0 | 0 | 0 | 177.3529
6714 | 56.5203 | 0 | 42.9 | 0 | 37.6 | 28.2601 | 0 | 0 | 0 | 0 | 0 | 126.2035
6715 | 43.9557 | 0 | 42.9 | 0 | 75.1 | 21.9778 | 0 | 0 | 0 | 0 | 0 | 155.8376
6716 | 43.2512 | 0 | 42.9 | 0 | 75.1 | 21.6256 | 0 | 0 | 0 | 0 | 0 | 182.253
6717 | 42.0627 | 0 | 42.9 | 0 | 75.1 | 21.0313 | 0 | 0 | 0 | 0 | 0 | 132.5757
6718 | 42.8248 | 0 | 42.9 | 0 | 93.9 | 21.4124 | 0 | 0 | 0 | 0 | 0 | 152.6366
6719 | 43.0891 | 0 | 0 | 0 | 0 | 21.5446 | 0 | 0 | 0 | 0 | 0 | 212.8982
6720 | 43.4487 | 0 | 0 | 0 | 0 | 21.7243 | 0 | 0 | 0 | 0 | 0 | 336.3415
6721 | 41.6443 | 0 | 0 | 0 | 0 | 20.8221 | 0 | 0 | 0 | 0 | 0 | 78.6464
6722 | 43.3978 | 0 | 0 | 0 | 0 | 21.6989 | 0 | 0 | 0 | 0 | 0 | 90.7406
6723 | 44.4215 | 0 | 0 | 0 | 0 | 22.2108 | 0 | 0 | 0 | 0 | 0 | 50.2371
6724 | 43.0789 | 0 | 0 | 0 | 0 | 21.5395 | 0 | 0 | 0 | 0 | 0 | 49.32
6725 | 39.8811 | 0 | 0 | 0 | 0 | 19.9406 | 0 | 0 | 0 | 0 | 0 | 50.9263
6726 | 59.6641 | 0 | 0 | 0 | 0 | 29.8321 | 0 | 0 | 0 | 0 | 0 | 61.8556
6727 | 104.327 | 0 | 42.9 | 41.3 | 56.3 | 52.1635 | 0 | 0 | 0 | 0 | 371 | 81.3724
6728 | 183.2485 | 0.7 | 43 | 63.6 | 37.6 | 91.6242 | 0 | 0 | 0 | 23.4 | 280.2 | 88.7154
6729 | 306.7365 | 2.1 | 43.2 | 11.5 | 0 | 153.3682 | 0 | 0 | 0 | 21.1 | 0 | 119.8235
6730 | 370.3543 | 3.5 | 43.4 | 0 | 0 | 185.1771 | 0 | 0 | 0 | 33.6 | 0 | 178.3081
6731 | 394.0968 | 3.5 | 43.4 | 0 | 0 | 197.0484 | 0 | 0 | 0 | 30.6 | 0 | 105.1021
6732 | 341.3133 | 2.8 | 43.3 | 0 | 0 | 170.6567 | 0 | 0 | 0 | 20.6 | 0 | 87.4083
6733 | 315.6709 | 1.4 | 43.1 | 0 | 75.1 | 157.8355 | 0 | 0 | 0 | 5.5 | 0.3 | 83.7358
6734 | 313.0828 | 2.1 | 43.2 | 0 | 37.6 | 156.5414 | 0 | 0 | 0 | 4.6 | 0 | 77.0882
6735 | 252.2465 | 3.5 | 43.4 | 0 | 0 | 126.1233 | 0 | 0 | 0 | 15 | 0 | 89.1856
6736 | 182.5233 | 2.8 | 43.3 | 0 | 0 | 91.2616 | 0 | 0 | 0 | 15.2 | 0 | 237.4266
6737 | 141.5865 | 2.1 | 43.2 | 0 | 0 | 70.7933 | 0 | 0 | 0 | 12.7 | 0 | 119.7681
6738 | 112.191 | 0.7 | 43 | 0 | 37.6 | 56.0955 | 0 | 0 | 0 | 5 | 0 | 149.9688
6739 | 72.3096 | 0 | 42.9 | 0 | 75.1 | 36.1548 | 0 | 0 | 0 | 0 | 0 | 139.3105
6740 | 56.2705 | 0 | 42.9 | 0 | 75.1 | 28.1352 | 0 | 0 | 0 | 0 | 0 | 280.5391
6741 | 42.165 | 0 | 42.9 | 0 | 75.1 | 21.0825 | 0 | 0 | 0 | 0 | 0 | 212.0731
6742 | 44.3921 | 0 | 42.9 | 0 | 93.9 | 22.196 | 0 | 0 | 0 | 0 | 2.9 | 142.7655
6743 | 41.8885 | 0 | 0 | 0 | 0 | 20.9443 | 0 | 0 | 0 | 0 | 0 | 116.447
6744 | 42.5378 | 0 | 0 | 0 | 0 | 21.2689 | 0 | 0 | 0 | 0 | 0 | 85.9853
6745 | 41.097 | 0 | 0 | 0 | 0 | 20.5485 | 0 | 0 | 0 | 0 | 0 | 57.0144
6746 | 43.5996 | 0 | 0 | 0 | 0 | 21.7998 | 0 | 0 | 0 | 0 | 0 | 46.2217
6747 | 42.8911 | 0 | 0 | 0 | 0 | 21.4456 | 0 | 0 | 0 | 0 | 0 | 47.2488
6748 | 39.6577 | 0 | 0 | 0 | 0 | 19.8288 | 0 | 0 | 0 | 0 | 0 | 48.9748
6749 | 41.3421 | 0 | 0 | 0 | 0 | 20.6711 | 0 | 0 | 0 | 0 | 0 | 52.6509
6750 | 59.9204 | 0 | 0 | 0 | 0 | 29.9602 | 0 | 0 | 0 | 0 | 0 | 66.1019
6751 | 88.7014 | 0 | 42.9 | 28.9 | 56.3 | 44.3507 | 0 | 0 | 0 | 0 | 359.1 | 63.3487
6752 | 174.5862 | 0.7 | 43 | 39.8 | 37.6 | 87.2931 | 0 | 0 | 0 | 36.3 | 264.1 | 52.3057
6753 | 281.3219 | 2.1 | 43.2 | 3.6 | 0 | 140.661 | 0 | 0 | 0 | 20.6 | 0 | 81.7284
6754 | 361.0885 | 3.5 | 43.4 | 0 | 0 | 180.5443 | 0 | 0 | 0 | 17.5 | 0 | 70.1279
6755 | 381.2233 | 3.5 | 43.4 | 0 | 0 | 190.6116 | 0 | 0 | 0 | 0.9 | 0 | 45.6545
6756 | 362.6189 | 2.8 | 43.3 | 0 | 0 | 181.3095 | 0 | 0 | 0 | 0 | 0 | 152.0456
6757 | 332.541 | 1.4 | 43.1 | 0 | 75.1 | 166.2705 | 0 | 0 | 0 | 0 | 0 | 154.2214
6758 | 367.0902 | 2.1 | 43.2 | 0 | 37.6 | 183.5451 | 0 | 0 | 4.6 | 0 | 0 | 114.5305
6759 | 363.2236 | 3.5 | 43.4 | 0 | 0 | 181.6118 | 0 | 0 | 23.9 | 0 | 0 | 81.1381
6760 | 297.6307 | 2.8 | 43.3 | 0 | 0 | 148.8153 | 0 | 0 | 33.1 | 0 | 0 | 92.29
6761 | 201.1279 | 2.1 | 43.2 | 0 | 0 | 100.564 | 0 | 0 | 23.5 | 0 | 0 | 104.9837
6762 | 169.2921 | 0.7 | 43 | 0 | 37.6 | 84.646 | 0 | 0 | 2.4 | 0 | 0 | 163.9701
6763 | 97.6327 | 0 | 42.9 | 0 | 75.1 | 48.8164 | 0 | 0 | 0 | 0 | 0 | 159.5669
6764 | 62.7327 | 0 | 42.9 | 0 | 75.1 | 31.3663 | 0 | 0 | 0 | 0 | 0 | 255.0287
6765 | 44.1698 | 0 | 42.9 | 0 | 75.1 | 22.0849 | 0 | 0 | 0 | 0 | 0 | 159.8883
6766 | 42.7423 | 0 | 42.9 | 0 | 93.9 | 21.3712 | 0 | 0 | 0 | 0 | 0 | 193.7116
6767 | 42.9655 | 0 | 0 | 0 | 0 | 21.4827 | 0 | 0 | 0 | 0 | 0 | 164.2896
6768 | 40.8357 | 0 | 0 | 0 | 0 | 20.4178 | 0 | 0 | 0 | 0 | 0 | 88.243
6769 | 44.8706 | 0 | 0 | 0 | 0 | 22.4353 | 0 | 0 | 0 | 0 | 0 | 65.64
6770 | 43.2271 | 0 | 0 | 0 | 0 | 21.6135 | 0 | 0 | 0 | 0 | 0 | 58.1713
6771 | 39.9577 | 0 | 0 | 0 | 0 | 19.9788 | 0 | 0 | 0 | 0 | 0 | 57.2448
6772 | 40.818 | 0 | 0 | 0 | 0 | 20.409 | 0 | 0 | 0 | 0 | 0 | 52.8788
6773 | 41.3167 | 0 | 0 | 0 | 0 | 20.6583 | 0 | 0 | 0 | 0 | 0 | 53.9122
6774 | 53.4275 | 0 | 0 | 0 | 0 | 26.7138 | 0 | 0 | 0 | 0 | 0 | 70.59
6775 | 91.3571 | 0 | 42.9 | 0 | 56.3 | 45.6785 | 0 | 0 | 0 | 0 | 170.3 | 87.0571
6776 | 158.6639 | 0.7 | 43 | 3.6 | 37.6 | 79.3319 | 0 | 0 | 0 | 0 | 118.8 | 82.1979
6777 | 282.7587 | 2.1 | 43.2 | 0 | 0 | 141.3794 | 0 | 0 | 0 | 0 | 0 | 80.7783
6778 | 316.2195 | 3.5 | 43.4 | 0 | 0 | 158.1098 | 0 | 0 | 0 | 0 | 0 | 106.065
6779 | 301.2189 | 3.5 | 43.4 | 0 | 0 | 150.6095 | 0 | 0 | 0 | 0 | 0 | 88.3608
6780 | 280.9618 | 2.8 | 43.3 | 0 | 0 | 140.4809 | 0 | 0 | 0 | 0 | 0 | 162.7516
6781 | 272.1296 | 1.4 | 43.1 | 0 | 75.1 | 136.0648 | 0 | 0 | 36.8 | 0 | 0 | 239.9598
6782 | 279.9576 | 2.1 | 43.2 | 0 | 37.6 | 139.9788 | 0 | 0 | 87.8 | 0 | 0 | 255.4955
6783 | 263.9374 | 3.5 | 43.4 | 0 | 0 | 131.9687 | 0 | 0 | 116.8 | 0 | 0 | 143.5211
6784 | 214.0467 | 2.8 | 43.3 | 0 | 0 | 107.0234 | 0 | 0 | 133.8 | 0 | 0 | 126.4893
6785 | 182.8871 | 2.1 | 43.2 | 0 | 0 | 91.4436 | 0 | 0 | 124.7 | 0 | 0 | 178.3769
6786 | 125.893 | 0.7 | 43 | 0 | 37.6 | 62.9465 | 0 | 0 | 67.2 | 0 | 0 | 195.7013
6787 | 72.0585 | 0 | 42.9 | 0 | 75.1 | 36.0293 | 0 | 0 | 1.7 | 0 | 0 | 282.3799
6788 | 48.2404 | 0 | 42.9 | 0 | 75.1 | 24.1202 | 0 | 0 | 0 | 0 | 0 | 239.0206
6789 | 41.8876 | 0 | 42.9 | 0 | 75.1 | 20.9438 | 0 | 0 | 0 | 0 | 0 | 168.242
6790 | 42.5697 | 0 | 42.9 | 0 | 93.9 | 21.2849 | 0 | 0 | 0 | 0 | 0 | 186.888
6791 | 41.9028 | 0 | 0 | 0 | 0 | 20.9514 | 0 | 0 | 0 | 0 | 0 | 124.233
6792 | 40.3377 | 0 | 0 | 0 | 0 | 20.1688 | 0 | 0 | 0 | 0 | 0 | 77.8019
6793 | 39.927 | 0 | 0 | 0 | 0 | 19.9635 | 0 | 0 | 0 | 0 | 0 | 60.5891
6794 | 41.0901 | 0 | 0 | 0 | 0 | 20.5451 | 0 | 0 | 0 | 0 | 0 | 52.4209
6795 | 44.2365 | 0 | 0 | 0 | 0 | 22.1182 | 0 | 0 | 0 | 0 | 0 | 44.8641
6796 | 43.5912 | 0 | 0 | 0 | 0 | 21.7956 | 0 | 0 | 0 | 0 | 0 | 50.0081
6797 | 45.5608 | 0 | 0 | 0 | 0 | 22.7804 | 0 | 0 | 0 | 0 | 0 | 50.2374
6798 | 56.5884 | 0 | 0 | 0 | 0 | 28.2942 | 0 | 0 | 0 | 0 | 0 | 98.273
6799 | 82.7905 | 0 | 42.9 | 0 | 56.3 | 41.3953 | 0 | 0 | 0 | 0 | 7 | 89.4281
6800 | 165.0471 | 0.7 | 43 | 0 | 37.6 | 82.5235 | 0 | 0 | 0 | 0 | 3.5 | 112.8466
6801 | 257.4864 | 2.1 | 43.2 | 0 | 0 | 128.7432 | 0 | 0 | 0 | 0 | 0 | 142.6204
6802 | 297.4069 | 3.5 | 43.4 | 0 | 0 | 148.7035 | 0 | 0 | 0 | 0 | 0 | 216.5244
6803 | 271.3771 | 3.5 | 43.4 | 0 | 0 | 135.6886 | 0 | 0 | 0 | 0 | 0 | 75.4412
6804 | 224.709 | 2.8 | 43.3 | 0 | 0 | 112.3545 | 0 | 0 | 13.1 | 0 | 0 | 161.2947
6805 | 214.7298 | 1.4 | 43.1 | 0 | 75.1 | 107.3649 | 0 | 0 | 75.7 | 0 | 0 | 322.6049
6806 | 214.5398 | 2.1 | 43.2 | 0 | 37.6 | 107.2699 | 0 | 0 | 128.9 | 0 | 0 | 283.3321
6807 | 209.7348 | 3.5 | 43.4 | 0 | 0 | 104.8674 | 0 | 0.1 | 154.8 | 0 | 0 | 130.1395
6808 | 189.0797 | 2.8 | 43.3 | 0 | 0 | 94.5398 | 0 | 0 | 155.6 | 0 | 0 | 355.1924
6809 | 147.5051 | 2.1 | 43.2 | 0 | 0 | 73.7526 | 0 | 0 | 134.6 | 0 | 0 | 226.0217
6810 | 98.7822 | 0.7 | 43 | 0 | 37.6 | 49.3911 | 0 | 0 | 73.1 | 0 | 0 | 146.5033
6811 | 66.7576 | 0 | 42.9 | 0 | 75.1 | 33.3788 | 0 | 0 | 3.6 | 0 | 0 | 348.7946
6812 | 46.55 | 0 | 42.9 | 0 | 75.1 | 23.275 | 0 | 0 | 0 | 0 | 0 | 341.258
6813 | 42.6162 | 0 | 42.9 | 0 | 75.1 | 21.3081 | 0 | 0 | 0 | 0 | 0 | 277.2366
6814 | 43.259 | 0 | 42.9 | 0 | 93.9 | 21.6295 | 0 | 0 | 0 | 0 | 0 | 137.0911
6815 | 41.7397 | 0 | 0 | 0 | 0 | 20.8699 | 0 | 0 | 0 | 0 | 0 | 129.4255
6816 | 40.5106 | 0 | 0 | 0 | 0 | 20.2553 | 0 | 0 | 0 | 0 | 0 | 112.4818
6817 | 42.6844 | 0 | 0 | 0 | 0 | 21.3422 | 0 | 0 | 0 | 0 | 0 | 143.5943
6818 | 41.0117 | 0 | 0 | 0 | 0 | 20.5059 | 0 | 0 | 0 | 0 | 0 | 82.6729
6819 | 42.8496 | 0 | 0 | 0 | 0 | 21.4248 | 0 | 0 | 0 | 0 | 0 | 47.3643
6820 | 40.3346 | 0 | 0 | 0 | 0 | 20.1673 | 0 | 0 | 0 | 0 | 0 | 51.3864
6821 | 42.2747 | 0 | 0 | 0 | 0 | 21.1373 | 0 | 0 | 0 | 0 | 0 | 52.6506
6822 | 63.9221 | 0 | 0 | 0 | 0 | 31.9611 | 0 | 0 | 0 | 0 | 0 | 104.7402
6823 | 104.6596 | 0 | 42.9 | 0 | 56.3 | 52.3298 | 0 | 0 | 0 | 0 | 0 | 95.1576
6824 | 156.3063 | 0.7 | 43 | 0 | 37.6 | 78.1532 | 0 | 0 | 0 | 0 | 0 | 75.3268
6825 | 257.368 | 2.1 | 43.2 | 0 | 0 | 128.684 | 0 | 0 | 0 | 0 | 0 | 57.2475
6826 | 317.0241 | 3.5 | 43.4 | 0 | 0 | 158.512 | 0 | 0 | 0 | 0 | 0 | 75.912
6827 | 301.7576 | 3.5 | 43.4 | 0 | 0 | 150.8788 | 0 | 0 | 0 | 0 | 0 | 53.109
6828 | 291.2989 | 2.8 | 43.3 | 0 | 0 | 145.6495 | 0 | 0 | 0 | 0 | 0 | 113.8006
6829 | 257.4663 | 1.4 | 43.1 | 0 | 75.1 | 128.7331 | 0 | 0 | 0 | 0 | 0 | 83.5025
6830 | 257.3711 | 2.1 | 43.2 | 0 | 37.6 | 128.6856 | 0 | 0 | 0 | 0 | 0 | 86.9343
6831 | 236.7885 | 3.5 | 43.4 | 0 | 0 | 118.3943 | 0 | 0 | 0 | 0 | 0 | 154.9413
6832 | 198.3476 | 2.8 | 43.3 | 0 | 0 | 99.1738 | 0 | 0 | 0 | 0 | 0 | 101.0234
6833 | 153.8548 | 2.1 | 43.2 | 0 | 0 | 76.9274 | 0 | 0 | 0 | 0 | 0 | 101.2601
6834 | 126.528 | 0.7 | 43 | 0 | 37.6 | 63.264 | 0 | 0 | 0 | 0 | 0 | 190.6394
6835 | 71.1725 | 0 | 42.9 | 0 | 75.1 | 35.5862 | 0 | 0 | 0 | 0 | 0 | 324.076
6836 | 45.4399 | 0 | 42.9 | 0 | 75.1 | 22.72 | 0 | 0 | 0 | 0 | 0 | 261.8368
6837 | 41.5656 | 0 | 42.9 | 0 | 75.1 | 20.7828 | 0 | 0 | 0 | 0 | 0 | 175.4731
6838 | 41.5519 | 0 | 42.9 | 0 | 93.9 | 20.776 | 0 | 0 | 0 | 0 | 0 | 139.1917
6839 | 39.5833 | 0 | 0 | 0 | 0 | 19.7917 | 0 | 0 | 0 | 0 | 0 | 152.7918
6840 | 42.8335 | 0 | 0 | 0 | 0 | 21.4167 | 0 | 0 | 0 | 0 | 0 | 85.9824
6841 | 42.0878 | 0 | 0 | 0 | 0 | 21.0439 | 0 | 0 | 0 | 0 | 0 | 53.568
6842 | 44.274 | 0 | 0 | 0 | 0 | 22.137 | 0 | 0 | 0 | 0 | 0 | 52.4198
6843 | 44.0502 | 0 | 0 | 0 | 0 | 22.0251 | 0 | 0 | 0 | 0 | 0 | 69.7829
6844 | 40.527 | 0 | 0 | 0 | 0 | 20.2635 | 0 | 0 | 0 | 0 | 0 | 46.7915
6845 | 43.6749 | 0 | 0 | 0 | 0 | 21.8374 | 0 | 0 | 0 | 0 | 0 | 49.2047
6846 | 49.7017 | 0 | 0 | 0 | 0 | 24.8508 | 0 | 0 | 0 | 0 | 0 | 98.3974
6847 | 65.5393 | 0 | 42.9 | 0 | 56.3 | 32.7697 | 0 | 0 | 0 | 0 | 12.3 | 94.201
6848 | 69.1174 | 0 | 42.9 | 0 | 37.6 | 34.5587 | 0 | 0 | 0 | 0 | 20.7 | 133.3681
6849 | 61.8639 | 0 | 42.9 | 0 | 0 | 30.932 | 0 | 0 | 0 | 0 | 0 | 96.5858
6850 | 59.7001 | 0 | 42.9 | 0 | 0 | 29.85 | 0 | 0 | 0 | 0 | 0 | 82.5569
6851 | 59.1918 | 0 | 42.9 | 0 | 0 | 29.5959 | 0 | 0 | 0 | 0 | 0 | 76.0296
6852 | 63.4696 | 0 | 42.9 | 0 | 0 | 31.7348 | 0 | 0 | 0 | 0 | 0 | 152.6834
6853 | 63.9723 | 0 | 42.9 | 0 | 75.1 | 31.9862 | 0 | 0 | 0 | 0 | 15.4 | 166.1783
6854 | 69.8841 | 0 | 42.9 | 0 | 37.6 | 34.9421 | 0 | 0 | 0 | 0 | 21.7 | 114.0445
6855 | 78.4439 | 0 | 42.9 | 0 | 0 | 39.2219 | 0 | 0 | 0 | 0 | 0 | 126.7632
6856 | 77.7335 | 0 | 42.9 | 0 | 0 | 38.8668 | 0 | 0 | 0 | 0 | 0 | 94.6808
6857 | 75.3009 | 0 | 42.9 | 0 | 0 | 37.6505 | 0 | 0 | 0 | 0 | 0 | 131.6255
6858 | 73.8703 | 0 | 42.9 | 0 | 37.6 | 36.9352 | 0 | 0 | 0 | 0 | 66.6 | 261.0103
6859 | 62.1385 | 0 | 42.9 | 0 | 75.1 | 31.0693 | 0 | 0 | 0 | 0 | 26.2 | 189.9903
6860 | 45.4486 | 0 | 42.9 | 0 | 75.1 | 22.7243 | 0 | 0 | 0 | 0 | 6.1 | 187.8546
6861 | 44.7652 | 0 | 42.9 | 0 | 75.1 | 22.3826 | 0 | 0 | 0 | 0 | 28 | 243.3974
6862 | 43.718 | 0 | 42.9 | 0 | 93.9 | 21.859 | 0 | 0 | 0 | 0 | 70.7 | 172.8239
6863 | 44.102 | 0 | 0 | 0 | 0 | 22.051 | 0 | 0 | 0 | 0 | 0 | 174.3242
6864 | 42.9184 | 0 | 0 | 0 | 0 | 21.4592 | 0 | 0 | 0 | 0 | 0 | 126.4426
6865 | 42.2713 | 0 | 0 | 0 | 0 | 21.1356 | 0 | 0 | 0 | 0 | 0 | 71.2793
6866 | 43.9541 | 0 | 0 | 0 | 0 | 21.9771 | 0 | 0 | 0 | 0 | 0 | 72.7799
6867 | 44.6561 | 0 | 0 | 0 | 0 | 22.3281 | 0 | 0 | 0 | 0 | 0 | 57.3641
6868 | 40.7657 | 0 | 0 | 0 | 0 | 20.3828 | 0 | 0 | 0 | 0 | 0 | 54.829
6869 | 43.1462 | 0 | 0 | 0 | 0 | 21.5731 | 0 | 0 | 0 | 0 | 0 | 49.3205
6870 | 52.6264 | 0 | 0 | 0 | 0 | 26.3132 | 0 | 0 | 0 | 0 | 0 | 60.3575
6871 | 73.4346 | 0 | 42.9 | 15.6 | 56.3 | 36.7173 | 0 | 0 | 0 | 0 | 174.4 | 73.0083
6872 | 71.3181 | 0 | 42.9 | 13.9 | 37.6 | 35.6591 | 0 | 0 | 0 | 0 | 165.3 | 106.3098
6873 | 67.5051 | 0 | 42.9 | 12.1 | 0 | 33.7526 | 0 | 0 | 0 | 0 | 0 | 152.4312
6874 | 61.4589 | 0 | 42.9 | 10.7 | 0 | 30.7294 | 0 | 0 | 0 | 0 | 0 | 91.0981
6875 | 58.8806 | 0 | 42.9 | 9.3 | 0 | 29.4403 | 0 | 0 | 0 | 0 | 0 | 121.1037
6876 | 63.0698 | 0 | 42.9 | 8.2 | 0 | 31.5349 | 0 | 0 | 0 | 0 | 0 | 141.9584
6877 | 68.5468 | 0 | 42.9 | 7.7 | 75.1 | 34.2734 | 0 | 0 | 0 | 0 | 174.5 | 204.8271
6878 | 74.4679 | 0 | 42.9 | 6.8 | 37.6 | 37.2339 | 0 | 0 | 0 | 0 | 155.4 | 160.632
6879 | 78.9329 | 0 | 42.9 | 6.4 | 0 | 39.4665 | 0 | 0 | 0 | 0 | 0 | 105.6967
6880 | 80.4841 | 0 | 42.9 | 6.6 | 0 | 40.242 | 0 | 0 | 0 | 0 | 0 | 187.9412
6881 | 81.7154 | 0 | 42.9 | 7.3 | 0 | 40.8577 | 0 | 0 | 0 | 0 | 0 | 100.3082
6882 | 85.8656 | 0 | 42.9 | 8.4 | 37.6 | 42.9328 | 0 | 0 | 0 | 0 | 213.4 | 141.6484
6883 | 65.6865 | 0 | 42.9 | 11 | 75.1 | 32.8433 | 0 | 0 | 0 | 0 | 154.5 | 163.3951
6884 | 51.2234 | 0 | 42.9 | 2 | 75.1 | 25.6117 | 0 | 0 | 0 | 0 | 115.6 | 308.5014
6885 | 43.3761 | 0 | 42.9 | 4.5 | 75.1 | 21.6881 | 0 | 0 | 0 | 0 | 167.4 | 215.4037
6886 | 41.2538 | 0 | 42.9 | 4.4 | 93.9 | 20.6269 | 0 | 0 | 0 | 0 | 158.5 | 133.976
6887 | 43.3851 | 0 | 0 | 0 | 0 | 21.6926 | 0 | 0 | 0 | 0 | 0 | 126.432
6888 | 41.9744 | 0 | 0 | 0 | 0 | 20.9872 | 0 | 0 | 0 | 0 | 0 | 95.8735
6889 | 43.2407 | 0 | 0 | 0 | 0 | 21.6203 | 0 | 0 | 0 | 0 | 0 | 72.0863
6890 | 40.8394 | 0 | 0 | 0 | 0 | 20.4197 | 0 | 0 | 0 | 0 | 0 | 48.5134
6891 | 42.9469 | 0 | 0 | 0 | 0 | 21.4734 | 0 | 0 | 0 | 0 | 0 | 51.9598
6892 | 41.749 | 0 | 0 | 0 | 0 | 20.8745 | 0 | 0 | 0 | 0 | 0 | 54.4843
6893 | 41.3285 | 0 | 0 | 0 | 0 | 20.6642 | 0 | 0 | 0 | 0 | 0 | 70.4722
6894 | 58.6606 | 0 | 0 | 0 | 0 | 29.3303 | 0 | 0 | 0 | 0 | 0 | 83.1499
6895 | 122.4693 | 0 | 42.9 | 81.2 | 56.3 | 61.2346 | 0 | 0 | 0 | 0 | 339.9 | 89.3059
6896 | 227.2082 | 0.7 | 43 | 103 | 37.6 | 113.6041 | 0 | 0 | 0 | 0 | 294.8 | 89.5448
6897 | 363.7145 | 2.1 | 43.2 | 96.4 | 0 | 181.8573 | 0 | 0 | 0 | 0 | 0 | 81.0212
6898 | 406.6106 | 3.5 | 43.4 | 84 | 0 | 203.3053 | 0 | 0 | 0 | 0 | 0 | 74.3948
6899 | 417.1281 | 3.5 | 43.4 | 64.2 | 0 | 208.5641 | 0 | 0 | 0 | 0 | 0 | 141.7196
6900 | 381.8248 | 2.8 | 43.3 | 51.9 | 0 | 190.9124 | 0 | 0 | 0 | 0 | 0 | 178.7573
6901 | 334.738 | 1.4 | 43.1 | 41.4 | 75.1 | 167.369 | 0 | 0 | 0 | 0 | 285.8 | 62.0862
6902 | 343.6418 | 2.1 | 43.2 | 33.6 | 37.6 | 171.8209 | 0 | 0 | 0 | 0 | 226.1 | 78.0461
6903 | 334.01 | 3.5 | 43.4 | 27.1 | 0 | 167.005 | 0 | 0 | 0 | 0 | 0 | 115.1364
6904 | 275.8899 | 2.8 | 43.3 | 27.2 | 0 | 137.945 | 0 | 0 | 0 | 0 | 0 | 135.6323
6905 | 195.0054 | 2.1 | 43.2 | 28.4 | 0 | 97.5027 | 0 | 0 | 0 | 0 | 0 | 381.2725
6906 | 139.5305 | 0.7 | 43 | 34.6 | 37.6 | 69.7653 | 0 | 0 | 0 | 0 | 290 | 299.9732
6907 | 90.1741 | 0 | 42.9 | 6.8 | 75.1 | 45.0871 | 0 | 0 | 0 | 0 | 224.1 | 259.9636
6908 | 71.8121 | 0 | 42.9 | 0 | 75.1 | 35.9061 | 0 | 0 | 0 | 0 | 163 | 363.1088
6909 | 52.6388 | 0 | 42.9 | 2.5 | 75.1 | 26.3194 | 0 | 0 | 0 | 0 | 220 | 266.6954
6910 | 43.7893 | 0 | 42.9 | 6.4 | 93.9 | 21.8946 | 0 | 0 | 0 | 0 | 235.1 | 239.4649
6911 | 39.9028 | 0 | 0 | 0 | 0 | 19.9514 | 0 | 0 | 0 | 0 | 0 | 167.3783
6912 | 41.0886 | 0 | 0 | 0 | 0 | 20.5443 | 0 | 0 | 0 | 0 | 0 | 93.2476
6913 | 41.6282 | 0 | 0 | 0 | 0 | 20.8141 | 0 | 0 | 0 | 0 | 0 | 61.1637
6914 | 43.5968 | 0 | 0 | 0 | 0 | 21.7984 | 0 | 0 | 0 | 0 | 0 | 57.1316
6915 | 43.316 | 0 | 0 | 0 | 0 | 21.658 | 0 | 0 | 0 | 0 | 4.3 | 50.0086
6916 | 44.3511 | 0 | 0 | 0.3 | 0 | 22.1756 | 0 | 0 | 0 | 0 | 16 | 52.1917
6917 | 43.2116 | 0 | 0 | 4 | 0 | 21.6058 | 0 | 0 | 0 | 0 | 41.5 | 55.1726
6918 | 66.9665 | 0 | 0 | 7.7 | 0 | 33.4833 | 0 | 0 | 0 | 0 | 62 | 70.8203
6919 | 121.992 | 0 | 42.9 | 159.7 | 56.3 | 60.996 | 0 | 0 | 0 | 0 | 552.2 | 77.4456
6920 | 193.2026 | 0.7 | 43 | 172 | 37.6 | 96.6013 | 0 | 0 | 0 | 0 | 477.3 | 82.9103
6921 | 303.5173 | 2.1 | 43.2 | 145.5 | 0 | 151.7587 | 0 | 0 | 0 | 0 | 47 | 71.2785
6922 | 337.9798 | 3.5 | 43.4 | 122.9 | 0 | 168.9899 | 0 | 0 | 0 | 0.7 | 51.9 | 62.7758
6923 | 300.2306 | 3.5 | 43.4 | 95.4 | 0 | 150.1153 | 0 | 0 | 0 | 1.5 | 29.9 | 74.1627
6924 | 246.1776 | 2.8 | 43.3 | 71.2 | 0 | 123.0888 | 0 | 0 | 0 | 0 | 10.4 | 68.516
6925 | 258.3322 | 1.4 | 43.1 | 48.7 | 75.1 | 129.1661 | 0 | 0 | 0 | 0 | 377.4 | 95.1603
6926 | 261.4326 | 2.1 | 43.2 | 35.6 | 37.6 | 130.7163 | 0 | 0 | 0 | 0 | 287.8 | 84.8078
6927 | 257.6655 | 3.5 | 43.4 | 29.9 | 0 | 128.8328 | 0 | 0 | 0 | 0 | 0 | 187.1509
6928 | 244.6218 | 2.8 | 43.3 | 30.8 | 0 | 122.3109 | 0 | 0 | 0 | 0 | 0 | 71.2789
6929 | 216.1861 | 2.1 | 43.2 | 36 | 0 | 108.0931 | 0 | 0 | 0 | 0 | 0 | 108.9692
6930 | 176.0989 | 0.7 | 43 | 50.9 | 37.6 | 88.0494 | 0 | 0 | 0 | 0 | 375.5 | 228.0752
6931 | 96.8622 | 0 | 42.9 | 19.8 | 75.1 | 48.4311 | 0 | 0 | 0 | 0 | 307.4 | 385.5959
6932 | 60.0955 | 0 | 42.9 | 2.4 | 75.1 | 30.0478 | 0 | 0 | 0 | 0 | 252 | 410.5092
6933 | 41.3712 | 0 | 42.9 | 10.7 | 75.1 | 20.6856 | 0 | 0 | 0 | 0 | 307.6 | 200.6715
6934 | 42.3441 | 0 | 42.9 | 26.1 | 93.9 | 21.172 | 0 | 0 | 0 | 0 | 337.8 | 161.706
6935 | 42.8003 | 0 | 0 | 0 | 0 | 21.4001 | 0 | 0 | 0 | 0 | 0 | 134.6955
6936 | 40.5211 | 0 | 0 | 0 | 0 | 20.2606 | 0 | 0 | 0 | 0 | 4.5 | 90.3838
6937 | 43.7893 | 0 | 0 | 0 | 0 | 21.8946 | 0 | 0 | 0 | 0 | 22.4 | 63.2321
6938 | 39.3856 | 0 | 0 | 0.7 | 0 | 19.6928 | 0 | 0 | 0 | 0 | 56.7 | 51.5014
6939 | 42.4141 | 0 | 0 | 5.7 | 0 | 21.2071 | 0 | 0 | 0 | 0 | 89 | 48.6291
6940 | 42.2796 | 0 | 0 | 10.9 | 0 | 21.1398 | 0 | 0 | 0 | 0 | 116.5 | 53.2226
6941 | 41.26 | 0 | 0 | 19.6 | 0 | 20.63 | 0 | 0 | 0 | 0 | 139.2 | 57.1307
6942 | 53.7179 | 0 | 0 | 30.1 | 0 | 26.859 | 0 | 0 | 0 | 0 | 153.1 | 67.7148
6943 | 100.9476 | 0 | 42.9 | 194.2 | 56.3 | 50.4738 | 0 | 0 | 0 | 0 | 647.6 | 73.3556
6944 | 193.6058 | 0.7 | 43 | 194.6 | 37.6 | 96.8029 | 0 | 0 | 0 | 0.1 | 553.1 | 74.1632
6945 | 278.307 | 2.1 | 43.2 | 142.1 | 0 | 139.1535 | 0 | 0 | 0 | 0 | 62.3 | 171.9929
6946 | 307.2209 | 3.5 | 43.4 | 88.2 | 0 | 153.6105 | 0 | 0 | 0 | 0 | 31 | 63.3497
6947 | 295.9481 | 3.5 | 43.4 | 28.4 | 0 | 147.974 | 0 | 0 | 0 | 0 | 4.3 | 90.262
6948 | 251.7835 | 2.8 | 43.3 | 0.2 | 0 | 125.8918 | 0 | 0 | 0 | 0 | 0 | 90.0229
6949 | 244.3457 | 1.4 | 43.1 | 0 | 75.1 | 122.1728 | 0 | 0 | 0 | 0 | 211.8 | 127.7448
6950 | 230.5563 | 2.1 | 43.2 | 0 | 37.6 | 115.2782 | 0 | 0 | 0 | 0 | 131.9 | 96.593
6951 | 208.1622 | 3.5 | 43.4 | 0 | 0 | 104.0811 | 0 | 0 | 0 | 0 | 0 | 99.5974
6952 | 185.3169 | 2.8 | 43.3 | 0 | 0 | 92.6585 | 0 | 0 | 0 | 0 | 0 | 119.0723
6953 | 187.2189 | 2.1 | 43.2 | 0 | 0 | 93.6095 | 0 | 0 | 0 | 0 | 0 | 184.2284
6954 | 172.5032 | 0.7 | 43 | 0 | 37.6 | 86.2516 | 0 | 0 | 0 | 0 | 190.1 | 386.1178
6955 | 101.2291 | 0 | 42.9 | 0 | 75.1 | 50.6145 | 0 | 0 | 0 | 0 | 143.5 | 142.9725
6956 | 62.7438 | 0 | 42.9 | 0 | 75.1 | 31.3719 | 0 | 0 | 0 | 0 | 99.7 | 163.1243
6957 | 41.6722 | 0 | 42.9 | 0 | 75.1 | 20.8361 | 0 | 0 | 0 | 0 | 162.9 | 173.7965
6958 | 42.9457 | 0 | 42.9 | 0 | 93.9 | 21.4728 | 0 | 0 | 0 | 0 | 184.5 | 378.082
6959 | 43.2466 | 0 | 0 | 0 | 0 | 21.6233 | 0 | 0 | 0 | 0 | 0 | 112.8407
6960 | 43.925 | 0 | 0 | 0 | 0 | 21.9625 | 0 | 0 | 0 | 0 | 0 | 103.0623
6961 | 41.4949 | 0 | 0 | 0 | 0 | 20.7475 | 0 | 0 | 0 | 0 | 0 | 72.0888
6962 | 42.3611 | 0 | 0 | 0 | 0 | 21.1806 | 0 | 0 | 0 | 0 | 0 | 53.798
6963 | 41.6461 | 0 | 0 | 0 | 0 | 20.8231 | 0 | 0 | 0 | 0 | 0 | 46.107
6964 | 40.0702 | 0 | 0 | 0 | 0 | 20.0351 | 0 | 0 | 0 | 0 | 0 | 46.7917
6965 | 42.2483 | 0 | 0 | 0 | 0 | 21.1242 | 0 | 0 | 0 | 0 | 1.8 | 54.0275
6966 | 65.5427 | 0 | 0 | 0 | 0 | 32.7714 | 0 | 0 | 0 | 0 | 7.8 | 76.03
6967 | 109.9453 | 0 | 42.9 | 107.8 | 56.3 | 54.9727 | 0 | 0 | 0 | 0 | 482.7 | 84.8061
6968 | 183.8594 | 0.7 | 43 | 136.6 | 37.6 | 91.9297 | 0 | 0 | 0 | 0 | 404.4 | 112.603
6969 | 282.1724 | 2.1 | 43.2 | 111.2 | 0 | 141.0862 | 0 | 0 | 0 | 0 | 8.1 | 79.4774
6970 | 312.6449 | 3.5 | 43.4 | 92.3 | 0 | 156.3224 | 0 | 0 | 0 | 0 | 8.4 | 60.5868
6971 | 276.7165 | 3.5 | 43.4 | 60.5 | 0 | 138.3582 | 0 | 0 | 0 | 0 | 2.6 | 85.0436
6972 | 239.51 | 2.8 | 43.3 | 20.4 | 0 | 119.755 | 0 | 0 | 0 | 0 | 0 | 78.2838
6973 | 213.6699 | 1.4 | 43.1 | 0.4 | 75.1 | 106.8349 | 0 | 0 | 0 | 0 | 268.7 | 150.2671
6974 | 194.751 | 2.1 | 43.2 | 0 | 37.6 | 97.3755 | 0 | 0 | 0 | 0 | 193.6 | 92.173
6975 | 186.1884 | 3.5 | 43.4 | 0 | 0 | 93.0942 | 0 | 0 | 0 | 0 | 0 | 91.7006
6976 | 164.5698 | 2.8 | 43.3 | 0 | 0 | 82.2849 | 0 | 0 | 0 | 0 | 0 | 101.5024
6977 | 123.9656 | 2.1 | 43.2 | 0 | 0 | 61.9828 | 0 | 0 | 0 | 0 | 0 | 114.5275
6978 | 96.0549 | 0.7 | 43 | 0.2 | 37.6 | 48.0275 | 0 | 0 | 0 | 0 | 245.4 | 213.982
6979 | 53.5097 | 0 | 42.9 | 0 | 75.1 | 26.7548 | 0 | 0 | 0 | 0 | 195.6 | 224.1816
6980 | 43.9157 | 0 | 42.9 | 0 | 75.1 | 21.9579 | 0 | 0 | 0 | 0 | 149.8 | 215.0931
6981 | 43.5993 | 0 | 42.9 | 0 | 75.1 | 21.7996 | 0 | 0 | 0 | 0 | 217.3 | 173.2699
6982 | 40.862 | 0 | 42.9 | 0 | 93.9 | 20.431 | 0 | 0 | 0 | 0 | 245.8 | 169.9784
6983 | 42.4144 | 0 | 0 | 0 | 0 | 21.2072 | 0 | 0 | 0 | 0 | 0 | 132.0436
6984 | 41.8076 | 0 | 0 | 0 | 0 | 20.9038 | 0 | 0 | 0 | 0 | 0 | 75.6757
6985 | 41.4506 | 0 | 0 | 0 | 0 | 20.7253 | 0 | 0 | 0 | 0 | 0 | 59.6676
6986 | 42.8397 | 0 | 0 | 0 | 0 | 21.4198 | 0 | 0 | 0 | 0 | 1.5 | 54.1414
6987 | 42.2356 | 0 | 0 | 0 | 0 | 21.1178 | 0 | 0 | 0 | 0 | 13.7 | 47.3631
6988 | 39.1603 | 0 | 0 | 0 | 0 | 19.5801 | 0 | 0 | 0 | 0 | 41 | 46.906
6989 | 41.7794 | 0 | 0 | 3 | 0 | 20.8897 | 0 | 0 | 0 | 0 | 75.5 | 66.1016
6990 | 60.9422 | 0 | 0 | 8 | 0 | 30.4711 | 0 | 0 | 0 | 0 | 99.7 | 88.0027
6991 | 92.329 | 0 | 42.9 | 170.2 | 56.3 | 46.1645 | 0 | 0 | 0 | 0 | 598.3 | 129.5335
6992 | 184.142 | 0.7 | 43 | 185.4 | 37.6 | 92.071 | 0 | 0 | 0 | 0 | 517.2 | 99.9508
6993 | 293.8818 | 2.1 | 43.2 | 159 | 0 | 146.9409 | 0 | 0 | 0 | 0 | 72.7 | 194.9528
6994 | 330.0721 | 3.5 | 43.4 | 136.6 | 0 | 165.0361 | 0 | 0 | 0 | 0.1 | 77.3 | 91.8189
6995 | 258.8873 | 3.5 | 43.4 | 102 | 0 | 129.4436 | 0 | 0 | 0 | 0 | 44.4 | 156.8209
6996 | 237.722 | 2.8 | 43.3 | 65.5 | 0 | 118.861 | 0 | 0 | 0 | 0 | 14.6 | 111.1464
6997 | 208.3141 | 1.4 | 43.1 | 33.6 | 75.1 | 104.157 | 0 | 0 | 0 | 0 | 383.6 | 100.3067
6998 | 195.4037 | 2.1 | 43.2 | 14.7 | 37.6 | 97.7018 | 0 | 0 | 0 | 0 | 282.9 | 145.3018
6999 | 181.0828 | 3.5 | 43.4 | 3.2 | 0 | 90.5414 | 0 | 0 | 0 | 0 | 0 | 174.9449
7000 | 138.5698 | 2.8 | 43.3 | 0.1 | 0 | 69.2849 | 0 | 0 | 0 | 0 | 0 | 117.1024
7001 | 128.7434 | 2.1 | 43.2 | 5.5 | 0 | 64.3717 | 0 | 0 | 0 | 0 | 0 | 111.6259
7002 | 102.7588 | 0.7 | 43 | 25.8 | 37.6 | 51.3794 | 0 | 0 | 0 | 0 | 354 | 166.1869
7003 | 64.0514 | 0 | 42.9 | 3 | 75.1 | 32.0257 | 0 | 0 | 0 | 0 | 288.3 | 304.5388
7004 | 44.9763 | 0 | 42.9 | 0 | 75.1 | 22.4881 | 0 | 0 | 0 | 0 | 225.7 | 199.0876
7005 | 39.9382 | 0 | 42.9 | 0.1 | 75.1 | 19.9691 | 0 | 0 | 0 | 0 | 273.8 | 154.1453
7006 | 40.1291 | 0 | 42.9 | 4 | 93.9 | 20.0645 | 0 | 0 | 0 | 0 | 290.8 | 183.6155
7007 | 40.8723 | 0 | 0 | 0 | 0 | 20.4361 | 0 | 0 | 0 | 0 | 0 | 162.8418
7008 | 38.7443 | 0 | 0 | 0 | 0 | 19.3722 | 0 | 0 | 0 | 0 | 0 | 136.8234
7009 | 40.6677 | 0 | 0 | 0 | 0 | 20.3339 | 0 | 0 | 0 | 0 | 0 | 79.4804
7010 | 41.93 | 0 | 0 | 0 | 0 | 20.965 | 0 | 0 | 0 | 0 | 0 | 51.8448
7011 | 41.9142 | 0 | 0 | 0 | 0 | 20.9571 | 0 | 0 | 0 | 0 | 1.7 | 49.8917
7012 | 40.3479 | 0 | 0 | 0 | 0 | 20.1739 | 0 | 0 | 0 | 0 | 5.8 | 48.2852
7013 | 43.1053 | 0 | 0 | 0 | 0 | 21.5526 | 0 | 0 | 0 | 0 | 10 | 60.0099
7014 | 42.2012 | 0 | 0 | 0 | 0 | 21.1006 | 0 | 0 | 0 | 0 | 14.9 | 71.6271
7015 | 49.114 | 0 | 42.9 | 113.3 | 56.3 | 24.557 | 0 | 0 | 0 | 0 | 494.8 | 97.7988
7016 | 47.8861 | 0 | 42.9 | 111.2 | 37.6 | 23.9431 | 0 | 0 | 0 | 0 | 424.7 | 114.0455
7017 | 43.4372 | 0 | 42.9 | 85.3 | 0 | 21.7186 | 0 | 0 | 0 | 0 | 10.5 | 68.5156
7018 | 45.7278 | 0 | 42.9 | 60 | 0 | 22.8639 | 0 | 0 | 0 | 0 | 7.5 | 107.5179
7019 | 46.1772 | 0 | 42.9 | 34.2 | 0 | 23.0886 | 0 | 0 | 0 | 0 | 1.2 | 90.1421
7020 | 45.8391 | 0 | 42.9 | 10.5 | 0 | 22.9195 | 0 | 0 | 0 | 0 | 0 | 106.9105
7021 | 46.5637 | 0 | 42.9 | 0.5 | 75.1 | 23.2818 | 0 | 0 | 0 | 0 | 282.1 | 98.0348
7022 | 45.3014 | 0 | 42.9 | 0 | 37.6 | 22.6507 | 0 | 0 | 0 | 0 | 212.6 | 118.5454
7023 | 44.9124 | 0 | 42.9 | 0 | 0 | 22.4562 | 0 | 0 | 0 | 0 | 0 | 194.0891
7024 | 45.3131 | 0 | 42.9 | 0 | 0 | 22.6566 | 0 | 0 | 0 | 0 | 0 | 91.2227
7025 | 47.0763 | 0 | 42.9 | 0 | 0 | 23.5381 | 0 | 0 | 0 | 0 | 0 | 99.2334
7026 | 48.5202 | 0 | 42.9 | 2.2 | 37.6 | 24.2601 | 0 | 0 | 0 | 0 | 275.3 | 308.8329
7027 | 43.9988 | 0 | 42.9 | 0.9 | 75.1 | 21.9994 | 0 | 0 | 0 | 0 | 213.4 | 223.477
7028 | 39.7612 | 0 | 42.9 | 0 | 75.1 | 19.8806 | 0 | 0 | 0 | 0 | 150.3 | 142.3977
7029 | 42.2855 | 0 | 42.9 | 0 | 75.1 | 21.1428 | 0 | 0 | 0 | 0 | 207.2 | 143.8199
7030 | 41.2665 | 0 | 42.9 | 0.6 | 93.9 | 20.6332 | 0 | 0 | 0 | 0 | 223.3 | 142.5485
7031 | 40.9612 | 0 | 0 | 0 | 0 | 20.4806 | 0 | 0 | 0 | 0 | 0 | 137.7147
7032 | 42.1206 | 0 | 0 | 0 | 0 | 21.0603 | 0 | 0 | 0 | 0 | 0 | 87.2912
7033 | 44.3738 | 0 | 0 | 0 | 0 | 22.1869 | 0 | 0 | 0 | 0 | 0 | 89.6665
7034 | 43.2047 | 0 | 0 | 0 | 0 | 21.6024 | 0 | 0 | 0 | 0 | 0 | 76.618
7035 | 42.7727 | 0 | 0 | 0 | 0 | 21.3864 | 0 | 0 | 0 | 0 | 1.6 | 77.448
7036 | 39.7203 | 0 | 0 | 0 | 0 | 19.8601 | 0 | 0 | 0 | 0 | 10.6 | 81.0196
7037 | 43.7236 | 0 | 0 | 0 | 0 | 21.8618 | 0 | 0 | 0 | 0 | 28.9 | 98.5188
7038 | 50.7569 | 0 | 0 | 2.9 | 0 | 25.3785 | 0 | 0 | 0 | 0 | 49.8 | 158.2078
7039 | 63.8552 | 0 | 42.9 | 149.2 | 56.3 | 31.9276 | 0 | 0 | 0 | 0 | 544.7 | 117.6296
7040 | 70.0279 | 0 | 42.9 | 124.1 | 37.6 | 35.014 | 0 | 0 | 0 | 0 | 466.6 | 130.9784
7041 | 65.0307 | 0 | 42.9 | 77.8 | 0 | 32.5154 | 0 | 0 | 0 | 0 | 11.5 | 274.4934
7042 | 65.0645 | 0 | 42.9 | 33.2 | 0 | 32.5323 | 0 | 0 | 0 | 0 | 3 | 110.6568
7043 | 63.7052 | 0 | 42.9 | 1.4 | 0 | 31.8526 | 0 | 0 | 0 | 0 | 0 | 104.0145
7044 | 59.5745 | 0 | 42.9 | 0 | 0 | 29.7873 | 0 | 0 | 0 | 0 | 0 | 143.1686
7045 | 59.7524 | 0 | 42.9 | 0 | 75.1 | 29.8762 | 0 | 0 | 0 | 0 | 192.4 | 235.9383
7046 | 58.809 | 0 | 42.9 | 0 | 37.6 | 29.4045 | 0 | 0 | 0 | 0 | 128.6 | 171.9013
7047 | 57.653 | 0 | 42.9 | 0 | 0 | 28.8265 | 0 | 0 | 0 | 0 | 0 | 94.6774
7048 | 57.5759 | 0 | 42.9 | 0 | 0 | 28.7879 | 0 | 0 | 0 | 0 | 0 | 103.7756
7049 | 62.2104 | 0 | 42.9 | 0 | 0 | 31.1052 | 0 | 0 | 0 | 0 | 0 | 171.9768
7050 | 64.7112 | 0 | 42.9 | 0 | 37.6 | 32.3556 | 0 | 0 | 0 | 0 | 176.8 | 229.6418
7051 | 54.7822 | 0 | 42.9 | 0 | 75.1 | 27.3911 | 0 | 0 | 0 | 0 | 137.9 | 273.7092
7052 | 44.066 | 0 | 42.9 | 0 | 75.1 | 22.033 | 0 | 0 | 0 | 0 | 105 | 204.8737
7053 | 43.965 | 0 | 42.9 | 0 | 75.1 | 21.9825 | 0 | 0 | 0 | 0 | 176.9 | 191.4381
7054 | 39.3196 | 0 | 42.9 | 0 | 93.9 | 19.6598 | 0 | 0 | 0 | 0 | 210.3 | 252.2979
7055 | 43.7425 | 0 | 0 | 0 | 0 | 21.8712 | 0 | 0 | 0 | 0 | 0 | 252.4609
7056 | 43.7245 | 0 | 0 | 0 | 0 | 21.8622 | 0 | 0 | 0 | 0 | 0 | 225.1238
7057 | 42.442 | 0 | 0 | 0 | 0 | 21.221 | 0 | 0 | 0 | 0 | 0 | 95.0361
7058 | 42.5623 | 0 | 0 | 0 | 0 | 21.2811 | 0 | 0 | 0 | 0 | 0 | 88.719
7059 | 42.1774 | 0 | 0 | 0 | 0 | 21.0887 | 0 | 0 | 0 | 0 | 1.6 | 87.5236
7060 | 42.2864 | 0 | 0 | 0 | 0 | 21.1432 | 0 | 0 | 0 | 0 | 12.3 | 86.4617
7061 | 42.1606 | 0 | 0 | 0.2 | 0 | 21.0803 | 0 | 0 | 0 | 0 | 32.8 | 81.7258
7062 | 60.9525 | 0 | 0 | 4.7 | 0 | 30.4762 | 0 | 0 | 0 | 0 | 62 | 95.7498
7063 | 99.721 | 0 | 42.9 | 170.6 | 56.3 | 49.8605 | 0 | 0 | 0 | 0 | 576 | 144.8387
7064 | 177.0569 | 0.7 | 43 | 191.1 | 37.6 | 88.5284 | 0 | 0 | 0 | 40.2 | 493.6 | 112.9679
7065 | 252.434 | 2.1 | 43.2 | 143.5 | 0 | 126.217 | 0 | 0 | 0 | 36.5 | 31.9 | 131.5668
7066 | 284.3266 | 3.5 | 43.4 | 95.5 | 0 | 142.1633 | 0 | 0 | 0 | 47.1 | 11.5 | 166.4142
7067 | 229.9684 | 3.5 | 43.4 | 42.5 | 0 | 114.9842 | 0 | 0 | 0 | 44.1 | 1.6 | 245.7308
7068 | 195.6624 | 2.8 | 43.3 | 2.6 | 0 | 97.8312 | 0 | 0 | 0 | 35.5 | 0 | 120.7565
7069 | 189.2982 | 1.4 | 43.1 | 0 | 75.1 | 94.6491 | 0 | 0 | 0 | 19 | 254.7 | 152.1
7070 | 185.9603 | 2.1 | 43.2 | 0 | 37.6 | 92.9802 | 0 | 0 | 0 | 17.9 | 173.4 | 219.007
7071 | 173.1301 | 3.5 | 43.4 | 0 | 0 | 86.5651 | 0 | 0 | 0 | 25.1 | 0 | 295.7239
7072 | 155.8876 | 2.8 | 43.3 | 0 | 0 | 77.9438 | 0 | 0 | 0 | 20.3 | 0 | 133.786
7073 | 172.5605 | 2.1 | 43.2 | 0 | 0 | 86.2803 | 0 | 0 | 0 | 14.1 | 0 | 218.7251
7074 | 135.4724 | 0.7 | 43 | 0 | 37.6 | 67.7362 | 0 | 0 | 0 | 4.2 | 281.1 | 389.2128
7075 | 80.2643 | 0 | 42.9 | 0 | 75.1 | 40.1322 | 0 | 0 | 0 | 0 | 244.3 | 305.5191
7076 | 55.465 | 0 | 42.9 | 0 | 75.1 | 27.7325 | 0 | 0 | 0 | 0 | 205.2 | 289.3463
7077 | 40.095 | 0 | 42.9 | 0 | 75.1 | 20.0475 | 0 | 0 | 0 | 0 | 272 | 217.8251
7078 | 43.7666 | 0 | 42.9 | 0 | 93.9 | 21.8833 | 0 | 0 | 0 | 0 | 302.8 | 201.0075
7079 | 41.445 | 0 | 0 | 0 | 0 | 20.7225 | 0 | 0 | 0 | 0 | 0 | 175.4083
7080 | 40.6885 | 0 | 0 | 0 | 0 | 20.3442 | 0 | 0 | 0 | 0 | 0 | 139.4009
7081 | 40.8276 | 0 | 0 | 0 | 0 | 20.4138 | 0 | 0 | 0 | 0 | 1.9 | 106.6734
7082 | 42.5393 | 0 | 0 | 0 | 0 | 21.2697 | 0 | 0 | 0 | 0 | 12.7 | 87.6448
7083 | 40.6981 | 0 | 0 | 0 | 0 | 20.349 | 0 | 0 | 0 | 0 | 36.4 | 80.3055
7084 | 40.69 | 0 | 0 | 0 | 0 | 20.345 | 0 | 0 | 0 | 0 | 70.9 | 82.4356
7085 | 44.1147 | 0 | 0 | 3.4 | 0 | 22.0573 | 0 | 0 | 0 | 0 | 101 | 93.1245
7086 | 56.5643 | 0 | 0 | 8.4 | 0 | 28.2821 | 0 | 0 | 0 | 0 | 122.6 | 133.6991
7087 | 88.1881 | 0 | 42.9 | 175.5 | 56.3 | 44.0941 | 0 | 0 | 0 | 8.1 | 628.8 | 146.4726
7088 | 161.301 | 0.7 | 43 | 197.9 | 37.6 | 80.6505 | 0 | 0 | 0 | 63.1 | 560 | 118.595
7089 | 302.3133 | 2.1 | 43.2 | 166.2 | 0 | 151.1566 | 0 | 0 | 0 | 51.9 | 93.8 | 119.297
7090 | 366.7483 | 3.5 | 43.4 | 143.8 | 0 | 183.3742 | 0 | 0 | 0 | 55.9 | 103 | 193.0431
7091 | 373.7907 | 3.5 | 43.4 | 111.3 | 0 | 186.8954 | 0 | 0 | 0 | 36.7 | 73.2 | 117.237
7092 | 350.5515 | 2.8 | 43.3 | 77.7 | 0 | 175.2757 | 0 | 0 | 0 | 7.9 | 44.7 | 196.2951
7093 | 321.05 | 1.4 | 43.1 | 48.8 | 75.1 | 160.525 | 0 | 0 | 0 | 0 | 432.1 | 123.465
7094 | 308.8939 | 2.1 | 43.2 | 34.2 | 37.6 | 154.4469 | 0 | 0 | 0 | 0 | 336.6 | 136.4914
7095 | 257.6767 | 3.5 | 43.4 | 31.4 | 0 | 128.8383 | 0 | 0 | 0 | 0 | 0.5 | 166.2655
7096 | 193.8795 | 2.8 | 43.3 | 35.9 | 0 | 96.9397 | 0 | 0 | 0 | 0 | 3 | 203.581
7097 | 173.5981 | 2.1 | 43.2 | 45.8 | 0 | 86.7991 | 0 | 0 | 0 | 0 | 10.5 | 295.2815
7098 | 109.1934 | 0.7 | 43 | 65.5 | 37.6 | 54.5967 | 0 | 0 | 0 | 0 | 465.4 | 148.3487
7099 | 70.9425 | 0 | 42.9 | 30.3 | 75.1 | 35.4713 | 0 | 0 | 0 | 0 | 392 | 180.1021
7100 | 57.3598 | 0 | 42.9 | 6.8 | 75.1 | 28.6799 | 0 | 0 | 0 | 0 | 333.1 | 273.5766
7101 | 42.7991 | 0 | 42.9 | 21.9 | 75.1 | 21.3995 | 0 | 0 | 0 | 0 | 391 | 268.5273
7102 | 41.2498 | 0 | 42.9 | 39.9 | 93.9 | 20.6249 | 0 | 0 | 0 | 0 | 423.4 | 237.9905
7103 | 38.7279 | 0 | 0 | 0 | 0 | 19.364 | 0 | 0 | 0 | 0 | 18 | 183.357
7104 | 44.0753 | 0 | 0 | 0 | 0 | 22.0377 | 0 | 0 | 0 | 0 | 68.4 | 128.0868
7105 | 42.7281 | 0 | 0 | 1.3 | 0 | 21.364 | 0 | 0 | 0 | 0 | 105.5 | 66.1005
7106 | 41.2132 | 0 | 0 | 7.9 | 0 | 20.6066 | 0 | 0 | 0 | 0 | 142.2 | 62.2013
7107 | 43.4784 | 0 | 0 | 15.8 | 0 | 21.7392 | 0 | 0 | 0 | 0 | 177.2 | 62.5458
7108 | 41.6778 | 0 | 0 | 28.9 | 0 | 20.8389 | 0 | 0 | 0 | 0 | 206.5 | 51.041
7109 | 41.1627 | 0 | 0 | 43.5 | 0 | 20.5813 | 0 | 0 | 0 | 0 | 231.9 | 63.9224
7110 | 53.8363 | 0 | 0 | 55.9 | 0 | 26.9182 | 0 | 0 | 0 | 0 | 250.1 | 108.1231
7111 | 82.2661 | 0 | 42.9 | 227.3 | 56.3 | 41.1331 | 0 | 0 | 0 | 0 | 764.7 | 100.0733
7112 | 173.1949 | 0.7 | 43 | 245.2 | 37.6 | 86.5975 | 0 | 0 | 0 | 48.6 | 689.5 | 175.3706
7113 | 313.419 | 2.1 | 43.2 | 187.4 | 0 | 156.7095 | 0 | 0 | 0 | 38.3 | 150.8 | 92.6509
7114 | 342.1473 | 3.5 | 43.4 | 125.3 | 0 | 171.0737 | 0 | 0 | 0 | 43.8 | 121.5 | 60.5871
7115 | 308.9906 | 3.5 | 43.4 | 62.9 | 0 | 154.4953 | 0 | 0 | 0 | 23.7 | 62 | 122.8806
7116 | 325.5073 | 2.8 | 43.3 | 10.1 | 0 | 162.7536 | 0 | 0 | 0 | 1.1 | 14.8 | 357.4788
7117 | 291.1263 | 1.4 | 43.1 | 0 | 75.1 | 145.5632 | 0 | 0 | 0 | 0 | 364 | 280.6214
7118 | 276.3997 | 2.1 | 43.2 | 0 | 37.6 | 138.1999 | 0 | 0 | 0 | 0 | 253.4 | 197.4084
7119 | 294.7072 | 3.5 | 43.4 | 0 | 0 | 147.3536 | 0 | 0 | 0 | 0 | 0 | 404.3028
7120 | 291.5289 | 2.8 | 43.3 | 0 | 0 | 145.7645 | 0 | 0 | 0 | 0 | 0 | 167.4983
7121 | 199.711 | 2.1 | 43.2 | 0 | 0 | 99.8555 | 0 | 0 | 0 | 0 | 0 | 140.3531
7122 | 97.0135 | 0.7 | 43 | 0.8 | 37.6 | 48.5067 | 0 | 0 | 0 | 0 | 341.7 | 205.2747
7123 | 56.8884 | 0 | 42.9 | 0 | 75.1 | 28.4442 | 0 | 0 | 0 | 0 | 297.1 | 234.857
7124 | 41.33 | 0 | 42.9 | 0 | 75.1 | 20.665 | 0 | 0 | 0 | 0 | 253.5 | 226.9028
7125 | 40.8689 | 0 | 42.9 | 0 | 75.1 | 20.4344 | 0 | 0 | 0 | 0 | 317.1 | 163.8177
7126 | 41.6889 | 0 | 42.9 | 0 | 93.9 | 20.8445 | 0 | 0 | 0 | 0 | 357.2 | 114.409
7127 | 42.2152 | 0 | 0 | 0 | 0 | 21.1076 | 0 | 0 | 0 | 0 | 1.5 | 130.9926
7128 | 44.0787 | 0 | 0 | 0 | 0 | 22.0394 | 0 | 0 | 0 | 0 | 14.3 | 108.0034
7129 | 42.6196 | 0 | 0 | 0 | 0 | 21.3098 | 0 | 0 | 0 | 0 | 51.2 | 51.6162
7130 | 42.3103 | 0 | 0 | 0 | 0 | 21.1552 | 0 | 0 | 0 | 0 | 99.5 | 46.2226
7131 | 40.9563 | 0 | 0 | 1.5 | 0 | 20.4781 | 0 | 0 | 0 | 0 | 145.7 | 44.751
7132 | 42.8328 | 0 | 0 | 8.9 | 0 | 21.4164 | 0 | 0 | 0 | 0 | 184.7 | 46.5641
7133 | 41.0877 | 0 | 0 | 17.8 | 0 | 20.5438 | 0 | 0 | 0 | 0 | 217.5 | 56.8982
7134 | 59.0852 | 0 | 0 | 35.5 | 0 | 29.5426 | 0 | 0 | 0 | 0 | 241.9 | 86.2243
7135 | 95.9275 | 0 | 42.9 | 225.3 | 56.3 | 47.9638 | 0 | 0 | 0 | 0 | 759.2 | 79.4794
7136 | 169.8605 | 0.7 | 43 | 245.7 | 37.6 | 84.9302 | 0 | 0 | 0 | 33.6 | 687.2 | 78.6489
7137 | 266.1568 | 2.1 | 43.2 | 191.6 | 0 | 133.0784 | 0 | 0 | 0 | 28 | 154.9 | 88.5976
7138 | 310.8904 | 3.5 | 43.4 | 144.5 | 0 | 155.4452 | 0 | 0 | 0 | 41.2 | 138.7 | 90.6206
7139 | 316.0996 | 3.5 | 43.4 | 93.2 | 0 | 158.0498 | 0 | 0 | 0 | 31.7 | 93.5 | 109.5738
7140 | 271.119 | 2.8 | 43.3 | 36.7 | 0 | 135.5595 | 0 | 0 | 0 | 21.9 | 46.6 | 126.7877
7141 | 246.1646 | 1.4 | 43.1 | 3.2 | 75.1 | 123.0823 | 0 | 0 | 0 | 1.7 | 424.8 | 235.4773
7142 | 226.0249 | 2.1 | 43.2 | 0 | 37.6 | 113.0125 | 0 | 0 | 0 | 0.6 | 300.5 | 114.7747
7143 | 197.1584 | 3.5 | 43.4 | 0 | 0 | 98.5792 | 0 | 0 | 0 | 17 | 0 | 104.2569
7144 | 160.4624 | 2.8 | 43.3 | 0 | 0 | 80.2312 | 0 | 0 | 0 | 24.9 | 0 | 137.1879
7145 | 151.7474 | 2.1 | 43.2 | 0.2 | 0 | 75.8737 | 0 | 0 | 0 | 19.7 | 0.1 | 191.2684
7146 | 97.4399 | 0.7 | 43 | 11.5 | 37.6 | 48.72 | 0 | 0 | 0 | 4.4 | 412.8 | 191.0253
7147 | 61.5491 | 0 | 42.9 | 0.3 | 75.1 | 30.7745 | 0 | 0 | 0 | 0 | 357.9 | 169.4399
7148 | 41.9585 | 0 | 42.9 | 0 | 75.1 | 20.9793 | 0 | 0 | 0 | 0 | 311.6 | 215.9237
7149 | 40.9941 | 0 | 42.9 | 0.4 | 75.1 | 20.497 | 0 | 0 | 0 | 0 | 373.6 | 174.2711
7150 | 39.6462 | 0 | 42.9 | 10.7 | 93.9 | 19.8231 | 0 | 0 | 0 | 0 | 413.6 | 129.8209
7151 | 43.4378 | 0 | 0 | 0 | 0 | 21.7189 | 0 | 0 | 0 | 0 | 8.6 | 100.0718
7152 | 42.9196 | 0 | 0 | 0 | 0 | 21.4598 | 0 | 0 | 0 | 0 | 47.7 | 71.8563
7153 | 41.802 | 0 | 0 | 0 | 0 | 20.901 | 0 | 0 | 0 | 0 | 95.4 | 79.5966
7154 | 42.0624 | 0 | 0 | 1.1 | 0 | 21.0312 | 0 | 0 | 0 | 0 | 136.2 | 76.4972
7155 | 40.1102 | 0 | 0 | 8.3 | 0 | 20.0551 | 0 | 0 | 0 | 0 | 175.3 | 76.0305
7156 | 41.3629 | 0 | 0 | 16 | 0 | 20.6814 | 0 | 0 | 0 | 0 | 209.5 | 79.4784
7157 | 43.5931 | 0 | 0 | 31.4 | 0 | 21.7965 | 0 | 0 | 0 | 0 | 237.9 | 92.292
7158 | 56.9749 | 0 | 0 | 47.1 | 0 | 28.4875 | 0 | 0 | 0 | 0 | 258.6 | 121.9458
7159 | 106.9084 | 0 | 42.9 | 231.1 | 56.3 | 53.4542 | 0 | 0 | 0 | 9.2 | 774.9 | 109.4512
7160 | 208.209 | 0.7 | 43 | 262.9 | 37.6 | 104.1045 | 0 | 0 | 0 | 66.7 | 720.1 | 104.8619
7161 | 298.7916 | 2.1 | 43.2 | 259.2 | 0 | 149.3958 | 0 | 0 | 0 | 63 | 249 | 96.4698
7162 | 298.9079 | 3.5 | 43.4 | 268.7 | 0 | 149.4539 | 0 | 0 | 0 | 82.7 | 314 | 82.4383
7163 | 271.8361 | 3.5 | 43.4 | 263.2 | 0 | 135.9181 | 0 | 0 | 0 | 73.5 | 321.9 | 108.9665
7164 | 242.5618 | 2.8 | 43.3 | 251 | 0 | 121.2809 | 0 | 0 | 0 | 46.9 | 327.7 | 227.8478
7165 | 237.8482 | 1.4 | 43.1 | 230.3 | 75.1 | 118.9241 | 0 | 0 | 0 | 15.3 | 805.2 | 125.8543
7166 | 249.3088 | 2.1 | 43.2 | 181.5 | 37.6 | 124.6544 | 0 | 0 | 0 | 11.4 | 653.6 | 224.7313
7167 | 244.9234 | 3.5 | 43.4 | 159.7 | 0 | 122.4617 | 0 | 0 | 0 | 29.3 | 131.7 | 274.3977
7168 | 207.9664 | 2.8 | 43.3 | 139.5 | 0 | 103.9832 | 0 | 0 | 0 | 29.5 | 168.6 | 261.7735
7169 | 236.5775 | 2.1 | 43.2 | 129.5 | 0 | 118.2887 | 0 | 0 | 0 | 21.4 | 187.6 | 134.0673
7170 | 180.7592 | 0.7 | 43 | 147.7 | 37.6 | 90.3796 | 0 | 0 | 0 | 9.1 | 681.4 | 206.0162
7171 | 102.1796 | 0 | 42.9 | 103.8 | 75.1 | 51.0898 | 0 | 0 | 0 | 0 | 607.8 | 151.0704
7172 | 65.1051 | 0 | 42.9 | 70.1 | 75.1 | 32.5526 | 0 | 0 | 0 | 0 | 528 | 176.2153
7173 | 42.1863 | 0 | 42.9 | 88.4 | 75.1 | 21.0932 | 0 | 0 | 0 | 0 | 576.6 | 250.7428
7174 | 41.4875 | 0 | 42.9 | 101.1 | 93.9 | 20.7437 | 0 | 0 | 0 | 0 | 601.9 | 275.89
7175 | 43.2636 | 0 | 0 | 1.6 | 0 | 21.6318 | 0 | 0 | 0 | 0 | 132.4 | 135.1637
7176 | 40.6039 | 0 | 0 | 11.5 | 0 | 20.3019 | 0 | 0 | 0 | 0 | 206.2 | 124.1819
7177 | 41.9539 | 0 | 0 | 27.2 | 0 | 20.9769 | 0 | 0 | 0 | 0 | 232.4 | 104.1345
7178 | 42.9528 | 0 | 0 | 41.5 | 0 | 21.4764 | 0 | 0 | 0 | 0 | 254.3 | 81.8448
7179 | 42.0624 | 0 | 0 | 53.9 | 0 | 21.0312 | 0 | 0 | 0 | 0 | 274.6 | 78.1664
7180 | 43.974 | 0 | 0 | 64.1 | 0 | 21.987 | 0 | 0 | 0 | 0 | 291.7 | 78.8854
7181 | 42.1306 | 0 | 0 | 72.5 | 0 | 21.0653 | 0 | 0 | 0 | 0 | 306.3 | 111.5067
7182 | 53.2744 | 0 | 0 | 79.7 | 0 | 26.6372 | 0 | 0 | 0 | 0 | 314.9 | 122.3979
7183 | 67.7497 | 0 | 42.9 | 243.3 | 56.3 | 33.8748 | 0 | 0 | 0 | 11.9 | 840.9 | 113.919
7184 | 78.3376 | 0 | 42.9 | 252.8 | 37.6 | 39.1688 | 0 | 0 | 0 | 15.3 | 795 | 184.4119
7185 | 78.1702 | 0 | 42.9 | 242.8 | 0 | 39.0851 | 0 | 0 | 0 | 10.9 | 280.2 | 257.0346
7186 | 76.6789 | 0 | 42.9 | 244.5 | 0 | 38.3394 | 0 | 0 | 0 | 8.8 | 340.1 | 184.3935
7187 | 75.8895 | 0 | 42.9 | 233.9 | 0 | 37.9447 | 0 | 0 | 0 | 6.9 | 340.7 | 261.5138
7188 | 71.0299 | 0 | 42.9 | 218.6 | 0 | 35.5149 | 0 | 0 | 0 | 3.7 | 334.9 | 272.7333
7189 | 71.2899 | 0 | 42.9 | 206.9 | 75.1 | 35.645 | 0 | 0 | 0 | 0 | 811.3 | 349.3652
7190 | 72.3024 | 0 | 42.9 | 153.1 | 37.6 | 36.1512 | 0 | 0 | 0 | 0 | 680.4 | 248.0493
7191 | 71.3547 | 0 | 42.9 | 126.5 | 0 | 35.6773 | 0 | 0 | 0 | 0 | 141.3 | 184.4617
7192 | 80.092 | 0 | 42.9 | 112.3 | 0 | 40.046 | 0 | 0 | 0 | 0 | 176.5 | 162.0361
7193 | 77.683 | 0 | 42.9 | 111.3 | 0 | 38.8415 | 0 | 0 | 0 | 0 | 188.4 | 222.4931
7194 | 66.3154 | 0 | 42.9 | 129.1 | 37.6 | 33.1577 | 0 | 0 | 0 | 0 | 674.5 | 485.8971
7195 | 41.0114 | 0 | 42.9 | 111.7 | 75.1 | 20.5057 | 0 | 0 | 0 | 0 | 601.4 | 371.6789
7196 | 42.0177 | 0 | 42.9 | 80 | 75.1 | 21.0089 | 0 | 0 | 0 | 0 | 521.6 | 227.4573
7197 | 41.3446 | 0 | 42.9 | 96.6 | 75.1 | 20.6723 | 0 | 0 | 0 | 0 | 569.6 | 232.3798
7198 | 39.5591 | 0 | 42.9 | 108.3 | 93.9 | 19.7796 | 0 | 0 | 0 | 0 | 594.5 | 205.874
7199 | 40.275 | 0 | 0 | 7 | 0 | 20.1375 | 0 | 0 | 0 | 0 | 128.7 | 205.6617
7200 | 41.8711 | 0 | 0 | 26 | 0 | 20.9356 | 0 | 0 | 0 | 0 | 204 | 183.711
7201 | 41.6517 | 0 | 0 | 44.7 | 0 | 20.8259 | 0 | 0 | 0 | 1 | 238 | 102.3406
7202 | 43.4831 | 0 | 0 | 62.8 | 0 | 21.7415 | 0 | 0 | 0 | 6.1 | 273.6 | 97.6753
7203 | 43.59 | 0 | 0 | 80.8 | 0 | 21.795 | 0 | 0 | 0 | 11.4 | 311.4 | 89.5479
7204 | 41.7342 | 0 | 0 | 95.1 | 0 | 20.8671 | 0 | 0 | 0 | 14.9 | 341.5 | 88.3614
7205 | 41.5231 | 0 | 0 | 106.8 | 0 | 20.7616 | 0 | 0 | 0 | 18.3 | 366 | 82.2011
7206 | 42.8186 | 0 | 0 | 116.8 | 0 | 21.4093 | 0 | 0 | 0 | 21.6 | 383.6 | 79.8335
7207 | 54.3313 | 0 | 42.9 | 285.2 | 56.3 | 27.1656 | 0 | 0 | 0 | 37.8 | 928.3 | 135.0858
7208 | 67.6325 | 0 | 42.9 | 281.4 | 37.6 | 33.8163 | 0 | 0 | 0 | 38 | 887.4 | 117.9608
7209 | 74.1294 | 0 | 42.9 | 256.8 | 0 | 37.0647 | 0 | 0 | 0 | 33.7 | 344.2 | 135.5993
7210 | 70.7789 | 0 | 42.9 | 238.1 | 0 | 35.3894 | 0 | 0 | 0 | 28.4 | 385.8 | 257.8475
7211 | 71.0485 | 0 | 42.9 | 218.8 | 0 | 35.5242 | 0 | 0 | 0 | 24 | 372.9 | 166.8217
7212 | 70.6158 | 0 | 42.9 | 200.1 | 0 | 35.3079 | 0 | 0 | 0 | 13.9 | 358.2 | 139.0459
7213 | 69.7673 | 0 | 42.9 | 191.5 | 75.1 | 34.8836 | 0 | 0 | 0 | 9.7 | 830.8 | 167.3033
7214 | 66.6969 | 0 | 42.9 | 176 | 37.6 | 33.3484 | 0 | 0 | 0 | 11.2 | 743.8 | 128.0762
7215 | 62.7832 | 0 | 42.9 | 172.8 | 0 | 31.3916 | 0 | 0 | 0 | 12.7 | 238.1 | 157.172
7216 | 66.7908 | 0 | 42.9 | 176.1 | 0 | 33.3954 | 0 | 0 | 0 | 12.1 | 301.9 | 151.022
7217 | 71.5992 | 0 | 42.9 | 185.5 | 0 | 35.7996 | 0 | 0 | 0 | 11.2 | 324.4 | 155.0754
7218 | 71.6547 | 0 | 42.9 | 207.2 | 37.6 | 35.8274 | 0 | 0 | 0 | 19.5 | 833.5 | 237.3875
7219 | 68.8121 | 0 | 42.9 | 199.4 | 75.1 | 34.406 | 0 | 0 | 0 | 21.6 | 778.7 | 273.7603
7220 | 49.9629 | 0 | 42.9 | 162.8 | 75.1 | 24.9815 | 0 | 0 | 0 | 10.2 | 693.8 | 328.2716
7221 | 43.7211 | 0 | 42.9 | 176.3 | 75.1 | 21.8605 | 0 | 0 | 0 | 15.2 | 742.4 | 268.7463
7222 | 40.0507 | 0 | 42.9 | 183.8 | 93.9 | 20.0253 | 0 | 0 | 0 | 18.7 | 770.4 | 244.7975
7223 | 39.8145 | 0 | 0 | 74.7 | 0 | 19.9073 | 0 | 0 | 0 | 22.5 | 264.1 | 165.1421
7224 | 45.342 | 0 | 0 | 99.9 | 0 | 22.671 | 0 | 0 | 0 | 25.6 | 351.6 | 116.5742
7225 | 42.0639 | 0 | 0 | 109.4 | 0 | 21.032 | 0 | 0 | 0 | 27.5 | 371.2 | 94.6788
7226 | 41.361 | 0 | 0 | 115 | 0 | 20.6805 | 0 | 0 | 0 | 28.1 | 382.7 | 89.9067
7227 | 43.5209 | 0 | 0 | 118.7 | 0 | 21.7604 | 0 | 0 | 0 | 28.4 | 390.5 | 82.1984
7228 | 41.6015 | 0 | 0 | 122.8 | 0 | 20.8008 | 0 | 0 | 0 | 29 | 399.7 | 75.5586
7229 | 44.1872 | 0 | 0 | 127.1 | 0 | 22.0936 | 0 | 0 | 0 | 29.7 | 410.3 | 80.0684
7230 | 42.24 | 0 | 0 | 130.1 | 0 | 21.12 | 0 | 0 | 0 | 30.8 | 412.7 | 101.6236
7231 | 59.8318 | 0 | 42.9 | 294.1 | 56.3 | 29.9159 | 0 | 0 | 0 | 42.9 | 954.1 | 104.3769
7232 | 99.7492 | 0.7 | 43 | 331.2 | 37.6 | 49.8746 | 0 | 0 | 0 | 99.4 | 904.1 | 104.6185
7233 | 167.4998 | 2.1 | 43.2 | 273.2 | 0 | 83.7499 | 0 | 0 | 0 | 106.3 | 296.2 | 94.5581
7234 | 281.8159 | 3.5 | 43.4 | 213.3 | 0 | 140.908 | 0 | 0 | 0 | 120.1 | 282.6 | 102.703
7235 | 339.7556 | 3.5 | 43.4 | 149.7 | 0 | 169.8778 | 0 | 0 | 0 | 96.3 | 223.1 | 109.2069
7236 | 289.0269 | 2.8 | 43.3 | 93.9 | 0 | 144.5135 | 0 | 0 | 0 | 57.6 | 162.6 | 126.5683
7237 | 282.7838 | 1.4 | 43.1 | 46.7 | 75.1 | 141.3919 | 0 | 0 | 0 | 32.3 | 540 | 179.6388
7238 | 283.9107 | 2.1 | 43.2 | 19.5 | 37.6 | 141.9554 | 0 | 0 | 0 | 27.5 | 418.4 | 95.1534
7239 | 317.4139 | 3.5 | 43.4 | 12.2 | 0 | 158.707 | 0 | 0 | 0 | 34.3 | 9.1 | 157.9474
7240 | 348.4459 | 2.8 | 43.3 | 13.3 | 0 | 174.2229 | 0 | 0 | 0 | 27 | 12.5 | 101.025
7241 | 364.5482 | 2.1 | 43.2 | 20.1 | 0 | 182.2741 | 0 | 0 | 0 | 21.8 | 29.6 | 91.698
7242 | 254.3977 | 0.7 | 43 | 50.9 | 37.6 | 127.1989 | 0 | 0 | 0 | 20.5 | 505.9 | 112.1181
7243 | 129.0892 | 0 | 42.9 | 19.6 | 75.1 | 64.5446 | 0 | 0 | 0 | 0 | 420.5 | 174.3381
7244 | 78.6066 | 0 | 42.9 | 3.9 | 75.1 | 39.3033 | 0 | 0 | 0 | 0 | 339.2 | 165.8976
7245 | 57.0865 | 0 | 42.9 | 9.3 | 75.1 | 28.5432 | 0 | 0 | 0 | 0 | 378.5 | 145.1755
7246 | 41.4025 | 0 | 42.9 | 17.3 | 93.9 | 20.7013 | 0 | 0 | 0 | 0 | 390.2 | 130.557
7247 | 43.4437 | 0 | 0 | 0 | 0 | 21.7218 | 0 | 0 | 0 | 0 | 5.3 | 125.5876
7248 | 41.0396 | 0 | 0 | 0 | 0 | 20.5198 | 0 | 0 | 0 | 0 | 13.7 | 154.4879
7249 | 40.8909 | 0 | 0 | 0 | 0 | 20.4454 | 0 | 0 | 0 | 0 | 28.7 | 107.6428
7250 | 39.9174 | 0 | 0 | 0 | 0 | 19.9587 | 0 | 0 | 0 | 0 | 54.8 | 82.4362
7251 | 43.2711 | 0 | 0 | 0 | 0 | 21.6355 | 0 | 0 | 0 | 0 | 81.4 | 75.7936
7252 | 42.3227 | 0 | 0 | 0 | 0 | 21.1614 | 0 | 0 | 0 | 0 | 104.2 | 78.5309
7253 | 42.5896 | 0 | 0 | 2.9 | 0 | 21.2948 | 0 | 0 | 0 | 0 | 123.6 | 78.0475
7254 | 42.3444 | 0 | 0 | 8.4 | 0 | 21.1722 | 0 | 0 | 0 | 0.6 | 137 | 82.7932
7255 | 54.8817 | 0 | 42.9 | 173.6 | 56.3 | 27.4408 | 0 | 0 | 0 | 12.8 | 640.7 | 97.5511
7256 | 102.8521 | 0.7 | 43 | 197.9 | 37.6 | 51.4261 | 0 | 0 | 0 | 64.2 | 587.2 | 102.6981
7257 | 194.3338 | 2.1 | 43.2 | 187.7 | 0 | 97.1669 | 0 | 0 | 0 | 65.5 | 131.9 | 92.4129
7258 | 293.0822 | 3.5 | 43.4 | 185.3 | 0 | 146.5411 | 0 | 0 | 0 | 82.6 | 174.7 | 86.5798
7259 | 311.8688 | 3.5 | 43.4 | 176.1 | 0 | 155.9344 | 0 | 0 | 0 | 77.7 | 175.4 | 113.5608
7260 | 309.6932 | 2.8 | 43.3 | 164.6 | 0 | 154.8466 | 0 | 0 | 0 | 60.8 | 175.4 | 130.9251
7261 | 319.3243 | 1.4 | 43.1 | 152 | 75.1 | 159.6622 | 0 | 0 | 0 | 38.3 | 614.4 | 77.8094
7262 | 350.0246 | 2.1 | 43.2 | 149.4 | 37.6 | 175.0123 | 0 | 0 | 0 | 39.3 | 549.9 | 81.4883
7263 | 355.0934 | 3.5 | 43.4 | 152.9 | 0 | 177.5467 | 0 | 0 | 0 | 55.1 | 105.2 | 111.2694
7264 | 351.8745 | 2.8 | 43.3 | 150.5 | 0 | 175.9373 | 0 | 0 | 0 | 56.2 | 151.4 | 125.1418
7265 | 360.05 | 2.1 | 43.2 | 151.9 | 0 | 180.025 | 0 | 0 | 0 | 48.1 | 174.7 | 315.1441
7266 | 255.1245 | 0.7 | 43 | 151.8 | 37.6 | 127.5622 | 0 | 0 | 0 | 33.1 | 640.7 | 202.1645
7267 | 142.2591 | 0 | 42.9 | 110.8 | 75.1 | 71.1295 | 0 | 0 | 0 | 0 | 568.2 | 136.5567
7268 | 99.4538 | 0 | 42.9 | 82.1 | 75.1 | 49.7269 | 0 | 0 | 0 | 0 | 487.4 | 170.1547
7269 | 67.8795 | 0 | 42.9 | 94.3 | 75.1 | 33.9398 | 0 | 0 | 0 | 0 | 530.7 | 141.2399
7270 | 42.1445 | 0 | 42.9 | 104.5 | 93.9 | 21.0723 | 0 | 0 | 0 | 0 | 555.6 | 155.3261
7271 | 41.8773 | 0 | 0 | 12.5 | 0 | 20.9387 | 0 | 0 | 0 | 0 | 120.7 | 130.5981
7272 | 40.7818 | 0 | 0 | 26 | 0 | 20.3909 | 0 | 0 | 0 | 0 | 175.2 | 114.5315
7273 | 41.7323 | 0 | 0 | 34.5 | 0 | 20.8662 | 0 | 0 | 0 | 0 | 187.1 | 93.607
7274 | 41.3496 | 0 | 0 | 47.1 | 0 | 20.6748 | 0 | 0 | 0 | 0.6 | 211.8 | 78.5241
7275 | 44.7299 | 0 | 0 | 58.5 | 0 | 22.3649 | 0 | 0 | 0 | 1.3 | 235.3 | 78.409
7276 | 42.7916 | 0 | 0 | 68.1 | 0 | 21.3958 | 0 | 0 | 0 | 2.2 | 255.7 | 81.1375
7277 | 42.8217 | 0 | 0 | 75.8 | 0 | 21.4108 | 0 | 0 | 0 | 4.4 | 272 | 77.8089
7278 | 41.7255 | 0 | 0 | 83.1 | 0 | 20.8627 | 0 | 0 | 0 | 7.1 | 283.5 | 76.7347
7279 | 56.9049 | 0 | 42.9 | 243.5 | 56.3 | 28.4524 | 0 | 0 | 0 | 24 | 807.7 | 93.4871
7280 | 93.3766 | 0.7 | 43 | 280.4 | 37.6 | 46.6883 | 0 | 0 | 0 | 73.7 | 761.7 | 102.4571
7281 | 167.8264 | 2.1 | 43.2 | 264.4 | 0 | 83.9132 | 0 | 0 | 0 | 79.9 | 246.5 | 103.4168
7282 | 244.646 | 3.5 | 43.4 | 250.9 | 0 | 122.323 | 0 | 0 | 0 | 101.2 | 283.5 | 96.1104
7283 | 279.2876 | 3.5 | 43.4 | 223.4 | 0 | 139.6438 | 0 | 0 | 0 | 99 | 264.4 | 169.4751
7284 | 255.7924 | 2.8 | 43.3 | 191.9 | 0 | 127.8962 | 0 | 0 | 0 | 80.6 | 241.7 | 167.5548
7285 | 255.18 | 1.4 | 43.1 | 171.4 | 75.1 | 127.59 | 0 | 0 | 0 | 53.8 | 688.7 | 167.4
7286 | 245.6269 | 2.1 | 43.2 | 163.2 | 37.6 | 122.8135 | 0 | 0 | 0 | 55.9 | 620.3 | 118.0379
7287 | 246.5142 | 3.5 | 43.4 | 159.2 | 0 | 123.2571 | 0 | 0 | 0 | 76.4 | 136.5 | 160.0951
7288 | 287.8049 | 2.8 | 43.3 | 151.1 | 0 | 143.9024 | 0 | 0 | 0 | 75.6 | 180.6 | 91.2175
7289 | 322.5748 | 2.1 | 43.2 | 147.1 | 0 | 161.2874 | 0 | 0 | 0 | 62.9 | 195.9 | 160.075
7290 | 240.5219 | 0.7 | 43 | 157 | 37.6 | 120.2609 | 0 | 0 | 0 | 41.7 | 679.4 | 267.3799
7291 | 136.3771 | 0 | 42.9 | 119.4 | 75.1 | 68.1885 | 0 | 0 | 0 | 0.1 | 617.1 | 189.0829
7292 | 91.6339 | 0 | 42.9 | 93.7 | 75.1 | 45.8169 | 0 | 0 | 0 | 0 | 542.6 | 200.2117
7293 | 60.6212 | 0 | 42.9 | 111.6 | 75.1 | 30.3106 | 0 | 0 | 0 | 0 | 597.4 | 212.9566
7294 | 44.6781 | 0 | 42.9 | 124.5 | 93.9 | 22.3391 | 0 | 0 | 0 | 0 | 628.8 | 216.7535
7295 | 41.8172 | 0 | 0 | 21.8 | 0 | 20.9086 | 0 | 0 | 0 | 0.2 | 157.8 | 178.3282
7296 | 41.6071 | 0 | 0 | 49 | 0 | 20.8035 | 0 | 0 | 0 | 1.9 | 246.2 | 112.7223
7297 | 43.5175 | 0 | 0 | 68.8 | 0 | 21.7587 | 0 | 0 | 0 | 5.5 | 286.3 | 84.2091
7298 | 42.2954 | 0 | 0 | 88.3 | 0 | 21.1477 | 0 | 0 | 0 | 9.7 | 327.8 | 82.9135
7299 | 42.0373 | 0 | 0 | 107.6 | 0 | 21.0186 | 0 | 0 | 0 | 14.3 | 370.6 | 83.503
7300 | 41.3446 | 0 | 0 | 122.9 | 0 | 20.6723 | 0 | 0 | 0 | 19.1 | 404.6 | 75.5564
7301 | 41.3951 | 0 | 0 | 135.4 | 0 | 20.6976 | 0 | 0 | 0 | 23.1 | 433.4 | 96.5865
7302 | 41.4961 | 0 | 0 | 146.3 | 0 | 20.7481 | 0 | 0 | 0 | 27 | 455.3 | 122.3678
7303 | 61.1493 | 0 | 42.9 | 318 | 56.3 | 30.5746 | 0 | 0 | 0 | 44.1 | 1009.3 | 116.6271
7304 | 99.0041 | 0.7 | 43 | 371.1 | 37.6 | 49.5021 | 0 | 0 | 0 | 98.7 | 970.8 | 171.0615
7305 | 175.6972 | 2.1 | 43.2 | 368.9 | 0 | 87.8486 | 0 | 0 | 0 | 114.8 | 423.8 | 196.0191
7306 | 239.7344 | 3.5 | 43.4 | 366.3 | 0 | 119.8672 | 0 | 0 | 0 | 154 | 472.5 | 189.9729
7307 | 254.998 | 3.5 | 43.4 | 328.2 | 0 | 127.499 | 0 | 0 | 0 | 159.4 | 445.2 | 302.2458
7308 | 259.627 | 2.8 | 43.3 | 285.2 | 0 | 129.8135 | 0 | 0 | 0 | 135.3 | 415.8 | 194.0472
7309 | 227.9573 | 1.4 | 43.1 | 258.1 | 75.1 | 113.9786 | 0 | 0 | 0 | 98.7 | 906.7 | 238.6024
7310 | 199.0738 | 2.1 | 43.2 | 260.2 | 37.6 | 99.5369 | 0 | 0 | 0 | 104.1 | 843.6 | 186.4692
7311 | 197.1798 | 3.5 | 43.4 | 279.3 | 0 | 98.5899 | 0 | 0 | 0 | 137.4 | 330.1 | 155.8001
7312 | 201.771 | 2.8 | 43.3 | 284.9 | 0 | 100.8855 | 0 | 0 | 0 | 137 | 410.4 | 131.9921
7313 | 240.4503 | 2.1 | 43.2 | 279.9 | 0 | 120.2251 | 0 | 0 | 0 | 114.3 | 434.2 | 220.0385
7314 | 149.6839 | 0.7 | 43 | 284.6 | 37.6 | 74.8419 | 0 | 0 | 0 | 70.8 | 966 | 207.7128
7315 | 102.2574 | 0 | 42.9 | 225.7 | 75.1 | 51.1287 | 0 | 0 | 0 | 19.1 | 932.5 | 180.3486
7316 | 64.431 | 0 | 42.9 | 196 | 75.1 | 32.2155 | 0 | 0 | 0 | 13.4 | 847.2 | 291.5685
7317 | 48.0423 | 0 | 42.9 | 210.6 | 75.1 | 24.0212 | 0 | 0 | 0 | 21.1 | 897.1 | 281.0332
7318 | 42.3912 | 0 | 42.9 | 219.9 | 93.9 | 21.1956 | 0 | 0 | 0 | 26.3 | 932.5 | 198.4824
7319 | 42.0816 | 0 | 0 | 111 | 0 | 21.0408 | 0 | 0 | 0 | 30.1 | 393.7 | 289.7398
7320 | 43.2314 | 0 | 0 | 138.2 | 0 | 21.6157 | 0 | 0 | 0 | 33.8 | 488 | 139.9885
7321 | 43.4022 | 0 | 0 | 149.3 | 0 | 21.7011 | 0 | 0 | 0 | 37.2 | 511.6 | 104.1328
7322 | 39.5948 | 0 | 0 | 158 | 0 | 19.7974 | 0 | 0 | 0 | 39.1 | 530.6 | 87.8856
7323 | 40.6181 | 0 | 0 | 165.5 | 0 | 20.3091 | 0 | 0 | 0 | 40.4 | 546.4 | 81.016
7324 | 43.0247 | 0 | 0 | 172 | 0 | 21.5123 | 0 | 0 | 0 | 42.3 | 559.7 | 81.9613
7325 | 43.7493 | 0 | 0 | 177.7 | 0 | 21.8746 | 0 | 0 | 0 | 44.1 | 572.1 | 84.5665
7326 | 42.4867 | 0 | 0 | 183.7 | 0 | 21.2433 | 0 | 0 | 0 | 46.9 | 583.6 | 87.8844
7327 | 56.9312 | 0 | 42.9 | 357.9 | 56.3 | 28.4656 | 0 | 0 | 0 | 61.3 | 1180.5 | 129.8715
7328 | 95.7952 | 0.7 | 43 | 411.4 | 37.6 | 47.8976 | 0 | 0 | 0 | 123.1 | 1131.5 | 174.8962
7329 | 164.0727 | 2.1 | 43.2 | 402.5 | 0 | 82.0363 | 0 | 0 | 0 | 130.7 | 521.3 | 128.4587
7330 | 248.4441 | 3.5 | 43.4 | 409.1 | 0 | 124.2221 | 0 | 0 | 0 | 159.6 | 574.1 | 135.7473
7331 | 320.6365 | 3.5 | 43.4 | 394.4 | 0 | 160.3183 | 0 | 0 | 0 | 153.4 | 572.4 | 132.172
7332 | 314.5701 | 2.8 | 43.3 | 373.2 | 0 | 157.285 | 0 | 0 | 0 | 133 | 572.2 | 136.9148
7333 | 221.7189 | 1.4 | 43.1 | 343.6 | 75.1 | 110.8594 | 0 | 0 | 0 | 96.6 | 1147.8 | 158.2904
7334 | 196.9824 | 2.1 | 43.2 | 275.5 | 37.6 | 98.4912 | 0 | 0 | 0 | 88.1 | 963.1 | 196.6738
7335 | 198.1573 | 3.5 | 43.4 | 240.3 | 0 | 99.0787 | 0 | 0 | 0 | 107.2 | 330.4 | 244.0895
7336 | 257.2645 | 2.8 | 43.3 | 218.3 | 0 | 128.6322 | 0 | 0 | 0 | 103.7 | 368.9 | 184.2465
7337 | 283.408 | 2.1 | 43.2 | 209.4 | 0 | 141.704 | 0 | 0 | 0 | 89.2 | 380.4 | 120.664
7338 | 191.8411 | 0.7 | 43 | 226 | 37.6 | 95.9205 | 0 | 0 | 0 | 57.7 | 919.7 | 158.499
7339 | 101.4596 | 0 | 42.9 | 178.4 | 75.1 | 50.7298 | 0 | 0 | 0 | 8.9 | 873.4 | 328.1475
7340 | 75.6106 | 0 | 42.9 | 146.2 | 75.1 | 37.8053 | 0 | 0 | 0 | 3.4 | 776.5 | 364.3057
7341 | 55.9788 | 0 | 42.9 | 160.4 | 75.1 | 27.9894 | 0 | 0 | 0 | 8.5 | 815 | 216.9498
7342 | 41.3198 | 0 | 42.9 | 169.7 | 93.9 | 20.6599 | 0 | 0 | 0 | 13.6 | 834.2 | 177.8805
7343 | 40.8438 | 0 | 0 | 59 | 0 | 20.4219 | 0 | 0 | 0 | 18.2 | 298.9 | 143.0796
7344 | 42.7743 | 0 | 0 | 84.1 | 0 | 21.3871 | 0 | 0 | 0 | 23.4 | 381.3 | 142.659
7345 | 41.4794 | 0 | 0 | 99.8 | 0 | 20.7397 | 0 | 0 | 0 | 28.2 | 410.1 | 102.4603
7346 | 42.5189 | 0 | 0 | 114.7 | 0 | 21.2594 | 0 | 0 | 0 | 33.2 | 439.3 | 88.359
7347 | 42.742 | 0 | 0 | 127.7 | 0 | 21.371 | 0 | 0 | 0 | 38.6 | 464.7 | 82.4394
7348 | 42.7482 | 0 | 0 | 138.4 | 0 | 21.3741 | 0 | 0 | 0 | 41.5 | 485.2 | 79.5981
7349 | 39.5551 | 0 | 0 | 146.9 | 0 | 19.7775 | 0 | 0 | 0 | 43.8 | 502.5 | 79.2392
7350 | 44.3825 | 0 | 0 | 154.2 | 0 | 22.1912 | 0 | 0 | 0 | 45.3 | 515.1 | 91.1013
7351 | 44.9155 | 0 | 42.9 | 326.6 | 56.3 | 22.4578 | 0 | 0 | 0 | 59.1 | 1108.5 | 131.3563
7352 | 55.6828 | 0 | 42.9 | 351.6 | 37.6 | 27.8414 | 0 | 0 | 0 | 60 | 1065.8 | 145.7873
7353 | 66.1136 | 0 | 42.9 | 344 | 0 | 33.0568 | 0 | 0 | 0 | 54.3 | 471.6 | 123.3314
7354 | 63.3262 | 0 | 42.9 | 347.8 | 0 | 31.6631 | 0 | 0 | 0 | 45.7 | 529.6 | 132.9584
7355 | 61.7313 | 0 | 42.9 | 336.4 | 0 | 30.8656 | 0 | 0 | 0 | 38.3 | 533.7 | 123.6441
7356 | 57.6521 | 0 | 42.9 | 324.3 | 0 | 28.826 | 0 | 0 | 0 | 26.8 | 540.9 | 118.92
7357 | 55.2235 | 0 | 42.9 | 314.9 | 75.1 | 27.6118 | 0 | 0 | 0 | 18.6 | 1120.8 | 156.0161
7358 | 57.6595 | 0 | 42.9 | 253.8 | 37.6 | 28.8298 | 0 | 0 | 0 | 15.7 | 951.7 | 195.194
7359 | 54.5355 | 0 | 42.9 | 222.8 | 0 | 27.2678 | 0 | 0 | 0 | 13.5 | 332.7 | 90.7425
7360 | 56.0436 | 0 | 42.9 | 206.6 | 0 | 28.0218 | 0 | 0 | 0 | 10.9 | 376.6 | 135.9935
7361 | 67.1968 | 0 | 42.9 | 205.6 | 0 | 33.5984 | 0 | 0 | 0 | 15 | 388.4 | 122.2843
7362 | 67.137 | 0 | 42.9 | 223.8 | 37.6 | 33.5685 | 0 | 0 | 0 | 25.1 | 926.5 | 227.9219
7363 | 64.7502 | 0 | 42.9 | 197.7 | 75.1 | 32.3751 | 0 | 0 | 0 | 27 | 883.1 | 330.8228
7364 | 48.6684 | 0 | 42.9 | 165.3 | 75.1 | 24.3342 | 0 | 0 | 0 | 17.2 | 792.5 | 182.7591
7365 | 42.9742 | 0 | 42.9 | 181 | 75.1 | 21.4871 | 0 | 0 | 0 | 23.5 | 839.1 | 243.6281
7366 | 39.8901 | 0 | 42.9 | 191.3 | 93.9 | 19.9451 | 0 | 0 | 0 | 27.7 | 868.1 | 212.6493
7367 | 42.733 | 0 | 0 | 85.1 | 0 | 21.3665 | 0 | 0 | 0 | 31.8 | 334.3 | 229.1833
7368 | 41.5172 | 0 | 0 | 112 | 0 | 20.7586 | 0 | 0 | 0 | 35 | 425.6 | 185.7367
7369 | 44.0205 | 0 | 0 | 127.4 | 0 | 22.0102 | 0 | 0 | 0 | 37.6 | 457.8 | 117.045
7370 | 40.2397 | 0 | 0 | 140.4 | 0 | 20.1199 | 0 | 0 | 0 | 39.8 | 486.1 | 93.2442
7371 | 41.3263 | 0 | 0 | 152.7 | 0 | 20.6632 | 0 | 0 | 0 | 42.1 | 513 | 87.6454
7372 | 44.5287 | 0 | 0 | 162.4 | 0 | 22.2644 | 0 | 0 | 0 | 44.1 | 534.3 | 82.4388
7373 | 41.0303 | 0 | 0 | 170.9 | 0 | 20.5152 | 0 | 0 | 0 | 45.7 | 554.1 | 81.8464
7374 | 42.2152 | 0 | 0 | 178.7 | 0 | 21.1076 | 0 | 0 | 0 | 48.1 | 570.1 | 105.4581
7375 | 44.8067 | 0 | 42.9 | 356.3 | 56.3 | 22.4034 | 0 | 0 | 0 | 63.9 | 1173.2 | 120.0835
7376 | 60.1724 | 0 | 42.9 | 355.7 | 37.6 | 30.0862 | 0 | 0 | 0 | 64.1 | 1129.1 | 137.7552
7377 | 71.2202 | 0 | 42.9 | 315.9 | 0 | 35.6101 | 0 | 0 | 0 | 55.5 | 493.4 | 168.1531
7378 | 69.7515 | 0 | 42.9 | 283.4 | 0 | 34.8757 | 0 | 0 | 0 | 50.6 | 511.9 | 196.3023
7379 | 69.1233 | 0 | 42.9 | 247.6 | 0 | 34.5616 | 0 | 0 | 0 | 41.5 | 473.2 | 448.7079
7380 | 64.9638 | 0 | 42.9 | 211.7 | 0 | 32.4819 | 0 | 0 | 0 | 35.7 | 430.6 | 190.5911
7381 | 64.1428 | 0 | 42.9 | 189.3 | 75.1 | 32.0714 | 0 | 0 | 0 | 34.2 | 919.8 | 261.1298
7382 | 58.3104 | 0 | 42.9 | 163.3 | 37.6 | 29.1552 | 0 | 0 | 0 | 33.3 | 813.2 | 195.146
7383 | 57.9239 | 0 | 42.9 | 156.7 | 0 | 28.9619 | 0 | 0 | 0 | 33.9 | 264.5 | 132.5169
7384 | 64.4174 | 0 | 42.9 | 161.9 | 0 | 32.2087 | 0 | 0 | 0 | 36.9 | 326.6 | 200.1872
7385 | 73.3112 | 0 | 42.9 | 176.9 | 0 | 36.6556 | 0 | 0 | 0 | 36.4 | 355.7 | 244.7749
7386 | 74.8512 | 0 | 42.9 | 204.2 | 37.6 | 37.4256 | 0 | 0 | 0 | 42.9 | 893.8 | 231.0091
7387 | 62.8622 | 0 | 42.9 | 202.3 | 75.1 | 31.4311 | 0 | 0 | 0 | 42.8 | 860.8 | 374.6273
7388 | 47.2263 | 0 | 42.9 | 167 | 75.1 | 23.6132 | 0 | 0 | 0 | 32.2 | 771.6 | 468.5962
7389 | 42.7079 | 0 | 42.9 | 182.2 | 75.1 | 21.354 | 0 | 0 | 0 | 36 | 819.9 | 333.748
7390 | 42.2669 | 0 | 42.9 | 191.5 | 93.9 | 21.1335 | 0 | 0 | 0 | 37.1 | 848.1 | 307.0386
7391 | 44.4609 | 0 | 0 | 87.7 | 0 | 22.2304 | 0 | 0 | 0 | 38.4 | 319.8 | 203.2949
7392 | 41.8588 | 0 | 0 | 114.9 | 0 | 20.9294 | 0 | 0 | 0 | 39.8 | 412 | 233.8406
7393 | 42.5381 | 0 | 0 | 128.6 | 0 | 21.2691 | 0 | 0 | 0 | 41.7 | 443.2 | 133.9641
7394 | 40.779 | 0 | 0 | 140.5 | 0 | 20.3895 | 0 | 0 | 0 | 44.1 | 471.2 | 94.9153
7395 | 40.6485 | 0 | 0 | 151.4 | 0 | 20.3243 | 0 | 0 | 0 | 44.8 | 496.3 | 94.676
7396 | 41.0802 | 0 | 0 | 160.1 | 0 | 20.5401 | 0 | 0 | 0 | 44.7 | 516.5 | 87.8802
7397 | 41.2299 | 0 | 0 | 167.4 | 0 | 20.615 | 0 | 0 | 0 | 46.1 | 533.7 | 74.9719
7398 | 40.6098 | 0 | 0 | 174.6 | 0 | 20.3049 | 0 | 0 | 0 | 47.6 | 548.3 | 84.2096
7399 | 56.3808 | 0 | 42.9 | 351.1 | 56.3 | 28.1904 | 0 | 0 | 0 | 64 | 1144.3 | 104.3785
7400 | 100.334 | 0.7 | 43 | 403.7 | 37.6 | 50.167 | 0 | 0 | 0 | 130.1 | 1099.8 | 159.9391
7401 | 165.0244 | 2.1 | 43.2 | 370.3 | 0 | 82.5122 | 0 | 0 | 0 | 133.9 | 462.5 | 176.7074
7402 | 252.285 | 3.5 | 43.4 | 344.8 | 0 | 126.1425 | 0 | 0 | 0 | 163.6 | 478.1 | 137.8596
7403 | 310.1627 | 3.5 | 43.4 | 298.2 | 0 | 155.0813 | 0 | 0 | 0 | 157.1 | 438.4 | 92.4142
7404 | 273.5683 | 2.8 | 43.3 | 231.2 | 0 | 136.7841 | 0 | 0 | 0 | 130.9 | 377.2 | 129.8329
7405 | 207.7844 | 1.4 | 43.1 | 182 | 75.1 | 103.8922 | 0 | 0 | 0 | 94.4 | 827.2 | 164.0588
7406 | 197.6512 | 2.1 | 43.2 | 151.3 | 37.6 | 98.8256 | 0 | 0 | 0 | 96.1 | 713.1 | 170.4773
7407 | 200.619 | 3.5 | 43.4 | 143.3 | 0 | 100.3095 | 0 | 0 | 0 | 117.6 | 182 | 133.3343
7408 | 219.3442 | 2.8 | 43.3 | 135.1 | 0 | 109.6721 | 0 | 0 | 0 | 115 | 228.4 | 91.4571
7409 | 285.5663 | 2.1 | 43.2 | 137.5 | 0 | 142.7832 | 0 | 0 | 0 | 99.4 | 254.1 | 101.1414
7410 | 208.7412 | 0.7 | 43 | 166 | 37.6 | 104.3706 | 0 | 0 | 0 | 65.3 | 779.7 | 184.181
7411 | 121.9306 | 0 | 42.9 | 128.1 | 75.1 | 60.9653 | 0 | 0 | 0 | 14.7 | 728 | 256.483
7412 | 91.1566 | 0 | 42.9 | 98.9 | 75.1 | 45.5783 | 0 | 0 | 0 | 8.3 | 647.6 | 347.5526
7413 | 60.2499 | 0 | 42.9 | 119.9 | 75.1 | 30.1249 | 0 | 0 | 0 | 13.6 | 700.9 | 345.7391
7414 | 44.4919 | 0 | 42.9 | 135 | 93.9 | 22.2459 | 0 | 0 | 0 | 16.8 | 730.8 | 294.7182
7415 | 40.8983 | 0 | 0 | 28 | 0 | 20.4492 | 0 | 0 | 0 | 19.9 | 233.5 | 217.9547
7416 | 40.5565 | 0 | 0 | 57.5 | 0 | 20.2782 | 0 | 0 | 0 | 22.6 | 325 | 162.6981
7417 | 42.9147 | 0 | 0 | 77.2 | 0 | 21.4573 | 0 | 0 | 0 | 25.2 | 358.8 | 104.7411
7418 | 41.6489 | 0 | 0 | 95 | 0 | 20.8245 | 0 | 0 | 0 | 27.5 | 391 | 94.3229
7419 | 42.7287 | 0 | 0 | 111.7 | 0 | 21.3644 | 0 | 0 | 0 | 29.9 | 424.6 | 95.7505
7420 | 41.3468 | 0 | 0 | 125 | 0 | 20.6734 | 0 | 0 | 0 | 31.9 | 451.7 | 77.6831
7421 | 42.9735 | 0 | 0 | 135.8 | 0 | 21.4868 | 0 | 0 | 0 | 33.7 | 473.9 | 103.8946
7422 | 42.4185 | 0 | 0 | 144.8 | 0 | 21.2092 | 0 | 0 | 0 | 35.7 | 488.4 | 112.2413
7423 | 60.2561 | 0 | 42.9 | 316.7 | 56.3 | 30.128 | 0 | 0 | 0 | 49.2 | 1052.8 | 138.6886
7424 | 107.7182 | 0.7 | 43 | 361.9 | 37.6 | 53.8591 | 0 | 0 | 0 | 109.2 | 1012.8 | 118.6307
7425 | 165.8389 | 2.1 | 43.2 | 314.3 | 0 | 82.9195 | 0 | 0 | 0 | 117.6 | 387.6 | 203.2116
7426 | 243.923 | 3.5 | 43.4 | 241.3 | 0 | 121.9615 | 0 | 0 | 0 | 146.6 | 356 | 157.2131
7427 | 277.9264 | 3.5 | 43.4 | 192.5 | 0 | 138.9632 | 0 | 0 | 0 | 139.9 | 305.7 | 79.2416
7428 | 252.5779 | 2.8 | 43.3 | 175.9 | 0 | 126.2889 | 0 | 0 | 0 | 111.1 | 291.8 | 100.4308
7429 | 212.5771 | 1.4 | 43.1 | 153.2 | 75.1 | 106.2885 | 0 | 0 | 0 | 77.5 | 743.3 | 225.381
7430 | 192.4306 | 2.1 | 43.2 | 125.6 | 37.6 | 96.2153 | 0 | 0 | 0 | 78.2 | 636.2 | 226.1769
7431 | 197.8483 | 3.5 | 43.4 | 112.7 | 0 | 98.9242 | 0 | 0 | 0 | 101.9 | 128.9 | 235.12
7432 | 222.5467 | 2.8 | 43.3 | 117.4 | 0 | 111.2733 | 0 | 0 | 0 | 103.9 | 184.4 | 169.0007
7433 | 251.8994 | 2.1 | 43.2 | 140.2 | 0 | 125.9497 | 0 | 0 | 0 | 89.1 | 228.7 | 156.0972
7434 | 146.9907 | 0.7 | 43 | 163.6 | 37.6 | 73.4953 | 0 | 0 | 0 | 56.8 | 745.1 | 130.214
7435 | 100.0126 | 0 | 42.9 | 121.6 | 75.1 | 50.0063 | 0 | 0 | 0 | 8.5 | 687.9 | 317.9349
7436 | 67.9115 | 0 | 42.9 | 91 | 75.1 | 33.9557 | 0 | 0 | 0 | 3.7 | 608 | 182.4422
7437 | 49.9477 | 0 | 42.9 | 110.1 | 75.1 | 24.9739 | 0 | 0 | 0 | 7.9 | 657.5 | 204.883
7438 | 43.307 | 0 | 42.9 | 124.7 | 93.9 | 21.6535 | 0 | 0 | 0 | 13.2 | 687.8 | 205.3432
7439 | 40.8066 | 0 | 0 | 16.8 | 0 | 20.4033 | 0 | 0 | 0 | 17.9 | 200.5 | 169.4065
7440 | 42.7956 | 0 | 0 | 41.8 | 0 | 21.3978 | 0 | 0 | 0 | 22 | 284.7 | 125.1477
7441 | 43.9985 | 0 | 0 | 60.3 | 0 | 21.9992 | 0 | 0 | 0 | 25.5 | 314.2 | 104.0104
7442 | 43.4372 | 0 | 0 | 75.9 | 0 | 21.7186 | 0 | 0 | 0 | 28.6 | 339.9 | 81.8453
7443 | 41.0272 | 0 | 0 | 89.8 | 0 | 20.5136 | 0 | 0 | 0 | 31.9 | 364.2 | 76.7333
7444 | 41.3849 | 0 | 0 | 101.8 | 0 | 20.6924 | 0 | 0 | 0 | 35.2 | 386.7 | 78.164
7445 | 40.1557 | 0 | 0 | 111.3 | 0 | 20.0779 | 0 | 0 | 0 | 37.7 | 405.5 | 77.562
7446 | 44.2885 | 0 | 0 | 120.1 | 0 | 22.1443 | 0 | 0 | 0 | 40.1 | 419.4 | 90.0241
7447 | 59.5528 | 0 | 42.9 | 287.3 | 56.3 | 29.7764 | 0 | 0 | 0 | 54.5 | 970.3 | 105.7036
7448 | 87.1081 | 0.7 | 43 | 328.9 | 37.6 | 43.554 | 0 | 0 | 0 | 112.7 | 923.6 | 126.2815
7449 | 158.0859 | 2.1 | 43.2 | 267.6 | 0 | 79.0429 | 0 | 0 | 0 | 110.2 | 312.6 | 126.6536
7450 | 256.0257 | 3.5 | 43.4 | 207.9 | 0 | 128.0129 | 0 | 0 | 0 | 119.9 | 293 | 86.3401
7451 | 302.9613 | 3.5 | 43.4 | 182.5 | 0 | 151.4807 | 0 | 0 | 0 | 91 | 267.6 | 138.6433
7452 | 309.9495 | 2.8 | 43.3 | 164.7 | 0 | 154.9747 | 0 | 0 | 0 | 51.6 | 253.7 | 196.903
7453 | 286.4924 | 1.4 | 43.1 | 144.7 | 75.1 | 143.2462 | 0 | 0 | 0 | 17.6 | 698.5 | 146.7366
7454 | 267.0884 | 2.1 | 43.2 | 139.4 | 37.6 | 133.5442 | 0 | 0 | 0 | 9.6 | 623.8 | 170.8646
7455 | 266.8795 | 3.5 | 43.4 | 149 | 0 | 133.4398 | 0 | 0 | 0 | 18.3 | 150.8 | 194.3767
7456 | 271.7165 | 2.8 | 43.3 | 158.7 | 0 | 135.8582 | 0 | 0 | 0 | 22.1 | 216.7 | 146.6869
7457 | 313.5049 | 2.1 | 43.2 | 169.3 | 0 | 156.7524 | 0 | 0 | 0 | 25.5 | 251.3 | 237.4833
7458 | 248.5098 | 0.7 | 43 | 182.8 | 37.6 | 124.2549 | 0 | 0 | 0 | 20.1 | 762 | 241.0772
7459 | 187.4693 | 0 | 42.9 | 136.9 | 75.1 | 93.7347 | 0 | 0 | 0 | 0 | 697.9 | 323.9212
7460 | 106.4708 | 0 | 42.9 | 101.4 | 75.1 | 53.2354 | 0 | 0 | 0 | 0 | 603.4 | 283.8412
7461 | 56.9008 | 0 | 42.9 | 113.5 | 75.1 | 28.4504 | 0 | 0 | 0 | 0 | 641.1 | 203.5939
7462 | 41.5274 | 0 | 42.9 | 121 | 93.9 | 20.7637 | 0 | 0 | 0 | 0 | 656.4 | 216.0134
7463 | 42.5679 | 0 | 0 | 12.9 | 0 | 21.2839 | 0 | 0 | 0 | 0 | 163.3 | 191.9379
7464 | 41.4481 | 0 | 0 | 31.6 | 0 | 20.7241 | 0 | 0 | 0 | 0 | 233.4 | 167.2587
7465 | 41.2494 | 0 | 0 | 43.9 | 0 | 20.6247 | 0 | 0 | 0 | 0 | 251.3 | 106.669
7466 | 42.8133 | 0 | 0 | 53.8 | 0 | 21.4067 | 0 | 0 | 0 | 0.2 | 265.8 | 85.2801
7467 | 42.7758 | 0 | 0 | 61.5 | 0 | 21.3879 | 0 | 0 | 0 | 1.4 | 276.8 | 84.3252
7468 | 39.8694 | 0 | 0 | 67.6 | 0 | 19.9347 | 0 | 0 | 0 | 2.3 | 285.6 | 85.983
7469 | 43.387 | 0 | 0 | 72.7 | 0 | 21.6935 | 0 | 0 | 0 | 3.5 | 293.7 | 77.3288
7470 | 42.4535 | 0 | 0 | 77.7 | 0 | 21.2267 | 0 | 0 | 0 | 5.2 | 298.2 | 100.4261
7471 | 57.3967 | 0 | 42.9 | 236.7 | 56.3 | 28.6984 | 0 | 0 | 0 | 23 | 830.4 | 138.8133
7472 | 99.3649 | 0.7 | 43 | 272.4 | 37.6 | 49.6824 | 0 | 0 | 0 | 74 | 786.6 | 141.4912
7473 | 161.6767 | 2.1 | 43.2 | 253.8 | 0 | 80.8383 | 0 | 0 | 0 | 66 | 251.1 | 101.7408
7474 | 212.7404 | 3.5 | 43.4 | 243.9 | 0 | 106.3702 | 0 | 0 | 0 | 71.9 | 290.9 | 86.8167
7475 | 246.5945 | 3.5 | 43.4 | 217.7 | 0 | 123.2972 | 0 | 0 | 0 | 46.9 | 270.4 | 135.9345
7476 | 233.7801 | 2.8 | 43.3 | 180.1 | 0 | 116.8901 | 0 | 0 | 0 | 14.5 | 236.7 | 131.8826
7477 | 233.0664 | 1.4 | 43.1 | 151.5 | 75.1 | 116.5332 | 0 | 0 | 0 | 1.3 | 668.6 | 187.5326
7478 | 216.8484 | 2.1 | 43.2 | 133.9 | 37.6 | 108.4242 | 0 | 0 | 0 | 2.4 | 596.7 | 128.544
7479 | 230.4274 | 3.5 | 43.4 | 130.9 | 0 | 115.2137 | 0 | 0 | 0 | 12.4 | 115 | 132.6667
7480 | 252.4731 | 2.8 | 43.3 | 133.6 | 0 | 126.2365 | 0 | 0 | 0 | 20.1 | 164.4 | 255.3905
7481 | 267.4018 | 2.1 | 43.2 | 135.8 | 0 | 133.7009 | 0 | 0 | 0 | 22.6 | 182.5 | 237.7645
7482 | 182.1225 | 0.7 | 43 | 144 | 37.6 | 91.0613 | 0 | 0 | 0 | 10.5 | 671 | 264.3731
7483 | 102.6367 | 0 | 42.9 | 106.1 | 75.1 | 51.3184 | 0 | 0 | 0 | 0 | 604.9 | 265.9015
7484 | 50.3004 | 0 | 42.9 | 80.2 | 75.1 | 25.1502 | 0 | 0 | 0 | 0 | 520.6 | 267.1019
7485 | 44.4153 | 0 | 42.9 | 95.1 | 75.1 | 22.2077 | 0 | 0 | 0 | 0 | 567.6 | 293.6624
7486 | 42.8133 | 0 | 42.9 | 105.1 | 93.9 | 21.4067 | 0 | 0 | 0 | 0 | 587.2 | 266.0104
7487 | 39.3484 | 0 | 0 | 9.2 | 0 | 19.6742 | 0 | 0 | 0 | 0 | 118.9 | 212.5095
7488 | 41.4518 | 0 | 0 | 28.6 | 0 | 20.7259 | 0 | 0 | 0 | 0 | 190.3 | 133.5983
7489 | 40.9584 | 0 | 0 | 45.9 | 0 | 20.4792 | 0 | 0 | 0 | 0 | 224.4 | 93.006
7490 | 43.5909 | 0 | 0 | 62.7 | 0 | 21.7955 | 0 | 0 | 0 | 0 | 258.9 | 86.2237
7491 | 41.3254 | 0 | 0 | 78.4 | 0 | 20.6627 | 0 | 0 | 0 | 0 | 292.6 | 88.2418
7492 | 41.5938 | 0 | 0 | 91.2 | 0 | 20.7969 | 0 | 0 | 0 | 0 | 320.2 | 102.9425
7493 | 42.1116 | 0 | 0 | 101.1 | 0 | 21.0558 | 0 | 0 | 0 | 0 | 342 | 83.0296
7494 | 44.04 | 0 | 0 | 108.9 | 0 | 22.02 | 0 | 0 | 0 | 0 | 355.6 | 89.4269
7495 | 61.3978 | 0 | 42.9 | 274.3 | 56.3 | 30.6989 | 0 | 0 | 0 | 6.2 | 901.6 | 98.3921
7496 | 95.9095 | 0.7 | 43 | 313.1 | 37.6 | 47.9548 | 0 | 0 | 0 | 61.3 | 851.5 | 130.3905
7497 | 159.4939 | 2.1 | 43.2 | 242.9 | 0 | 79.7469 | 0 | 0 | 0 | 57.4 | 250.5 | 133.104
7498 | 237.9117 | 3.5 | 43.4 | 171.4 | 0 | 118.9558 | 0 | 0 | 0 | 66.8 | 219.6 | 98.3929
7499 | 282.3515 | 3.5 | 43.4 | 93 | 0 | 141.1757 | 0 | 0 | 0 | 53.9 | 143 | 145.189
7500 | 259.4978 | 2.8 | 43.3 | 26.1 | 0 | 129.7489 | 0 | 0 | 0 | 35.4 | 65.4 | 167.6507
7501 | 230.0468 | 1.4 | 43.1 | 2.1 | 75.1 | 115.0234 | 0 | 0 | 0 | 15.6 | 407.7 | 149.5985
7502 | 218.9193 | 2.1 | 43.2 | 0 | 37.6 | 109.4597 | 0 | 0 | 0 | 11.8 | 272.3 | 148.1927
7503 | 213.8081 | 3.5 | 43.4 | 0 | 0 | 106.904 | 0 | 0 | 0 | 18.6 | 0 | 129.5798
7504 | 221.0057 | 2.8 | 43.3 | 0 | 0 | 110.5029 | 0 | 0 | 0 | 19.1 | 0 | 84.5692
7505 | 240.3926 | 2.1 | 43.2 | 0 | 0 | 120.1963 | 0 | 0 | 0 | 21 | 0.3 | 105.7018
7506 | 186.0239 | 0.7 | 43 | 4.5 | 37.6 | 93.0119 | 0 | 0 | 0 | 11.5 | 363.7 | 187.3289
7507 | 120.6119 | 0 | 42.9 | 0 | 75.1 | 60.306 | 0 | 0 | 0 | 0 | 311.7 | 242.7766
7508 | 80.5213 | 0 | 42.9 | 0 | 75.1 | 40.2606 | 0 | 0 | 0 | 0 | 256.1 | 261.2206
7509 | 57.9983 | 0 | 42.9 | 0 | 75.1 | 28.9991 | 0 | 0 | 0 | 0 | 313.3 | 239.359
7510 | 42.8477 | 0 | 42.9 | 0.4 | 93.9 | 21.4239 | 0 | 0 | 0 | 0 | 345.8 | 214.3631
7511 | 43.4623 | 0 | 0 | 0 | 0 | 21.7311 | 0 | 0 | 0 | 0 | 4 | 190.0738
7512 | 41.0037 | 0 | 0 | 0 | 0 | 20.5018 | 0 | 0 | 0 | 0 | 12.6 | 144.0744
7513 | 42.3726 | 0 | 0 | 0 | 0 | 21.1863 | 0 | 0 | 0 | 0 | 29.8 | 88.4816
7514 | 40.4712 | 0 | 0 | 0 | 0 | 20.2356 | 0 | 0 | 0 | 0 | 67.4 | 82.2
7515 | 42.1476 | 0 | 0 | 0 | 0 | 21.0738 | 0 | 0 | 0 | 0 | 109.3 | 78.1635
7516 | 41.2476 | 0 | 0 | 0 | 0 | 20.6238 | 0 | 0 | 0 | 0 | 143.8 | 75.3219
7517 | 43.4105 | 0 | 0 | 5.6 | 0 | 21.7053 | 0 | 0 | 0 | 0 | 174.1 | 78.408
7518 | 42.1033 | 0 | 0 | 17.1 | 0 | 21.0516 | 0 | 0 | 0 | 0 | 195.7 | 91.3389
7519 | 57.2765 | 0 | 42.9 | 200.8 | 56.3 | 28.6382 | 0 | 0 | 0 | 0.6 | 712.4 | 128.9575
7520 | 66.563 | 0 | 42.9 | 199.2 | 37.6 | 33.2815 | 0 | 0 | 0 | 1.5 | 646 | 109.4465
7521 | 63.1281 | 0 | 42.9 | 148.3 | 0 | 31.5641 | 0 | 0 | 0 | 0.6 | 124.7 | 157.0075
7522 | 61.1607 | 0 | 42.9 | 90.7 | 0 | 30.5804 | 0 | 0 | 0 | 0 | 98.9 | 301.2274
7523 | 53.5453 | 0 | 42.9 | 22.1 | 0 | 26.7727 | 0 | 0 | 0 | 0 | 38 | 160.1626
7524 | 55.9481 | 0 | 42.9 | 0 | 0 | 27.9741 | 0 | 0 | 0 | 0 | 11 | 147.2377
7525 | 56.9681 | 0 | 42.9 | 0 | 75.1 | 28.484 | 0 | 0 | 0 | 0 | 292 | 220.2254
7526 | 55.9264 | 0 | 42.9 | 0 | 37.6 | 27.9632 | 0 | 0 | 0 | 0 | 181.1 | 168.0218
7527 | 54.2944 | 0 | 42.9 | 0 | 0 | 27.1472 | 0 | 0 | 0 | 0 | 0 | 131.5114
7528 | 63.7653 | 0 | 42.9 | 0 | 0 | 31.8827 | 0 | 0 | 0 | 0 | 0 | 163.4048
7529 | 68.8078 | 0 | 42.9 | 0 | 0 | 34.4039 | 0 | 0 | 0 | 0 | 0 | 174.9101
7530 | 70.4352 | 0 | 42.9 | 0 | 37.6 | 35.2176 | 0 | 0 | 0 | 0 | 250.7 | 235.0899
7531 | 66.7511 | 0 | 42.9 | 0 | 75.1 | 33.3756 | 0 | 0 | 0 | 0 | 201.2 | 187.3461
7532 | 61.8723 | 0 | 42.9 | 0 | 75.1 | 30.9362 | 0 | 0 | 0 | 0 | 142.2 | 193.2399
7533 | 49.4832 | 0 | 42.9 | 0 | 75.1 | 24.7416 | 0 | 0 | 0 | 0 | 191.3 | 196.1987
7534 | 43.6579 | 0 | 42.9 | 0 | 93.9 | 21.8289 | 0 | 0 | 0 | 0 | 200.9 | 237.8398
7535 | 42.0915 | 0 | 0 | 0 | 0 | 21.0458 | 0 | 0 | 0 | 0 | 0 | 219.7763
7536 | 40.1892 | 0 | 0 | 0 | 0 | 20.0946 | 0 | 0 | 0 | 0 | 0 | 159.0945
7537 | 41.0694 | 0 | 0 | 0 | 0 | 20.5347 | 0 | 0 | 0 | 0 | 0 | 111.995
7538 | 40.7629 | 0 | 0 | 0 | 0 | 20.3814 | 0 | 0 | 0 | 0.8 | 0 | 84.4464
7539 | 41.7676 | 0 | 0 | 0 | 0 | 20.8838 | 0 | 0 | 0 | 4.2 | 0 | 76.8505
7540 | 41.7621 | 0 | 0 | 0 | 0 | 20.881 | 0 | 0 | 0 | 7.4 | 0 | 76.9701
7541 | 43.2735 | 0 | 0 | 0 | 0 | 21.6368 | 0 | 0 | 0 | 10 | 0.3 | 76.148
7542 | 42.5266 | 0 | 0 | 0 | 0 | 21.2633 | 0 | 0 | 0 | 12.4 | 1.9 | 126.9246
7543 | 47.2889 | 0 | 42.9 | 61.2 | 56.3 | 23.6445 | 0 | 0 | 0 | 27.4 | 412.9 | 124.0828
7544 | 59.281 | 0 | 42.9 | 65 | 37.6 | 29.6405 | 0 | 0 | 0 | 26.4 | 364.6 | 119.567
7545 | 61.3287 | 0 | 42.9 | 59.2 | 0 | 30.6644 | 0 | 0 | 0 | 17.4 | 8.1 | 138.5762
7546 | 59.2122 | 0 | 42.9 | 50.8 | 0 | 29.6061 | 0 | 0 | 0 | 7.9 | 12.5 | 150.1133
7547 | 55.0726 | 0 | 42.9 | 41.2 | 0 | 27.5363 | 0 | 0 | 0 | 0.3 | 10.9 | 267.1344
7548 | 54.8479 | 0 | 42.9 | 32 | 0 | 27.424 | 0 | 0 | 0 | 0 | 8.9 | 220.1358
7549 | 51.1493 | 0 | 42.9 | 25.6 | 75.1 | 25.5746 | 0 | 0 | 0 | 0 | 373 | 208.5601
7550 | 51.1518 | 0 | 42.9 | 23.3 | 37.6 | 25.5759 | 0 | 0 | 0 | 0 | 307.3 | 293.0548
7551 | 51.6557 | 0 | 42.9 | 25.4 | 0 | 25.8279 | 0 | 0 | 0 | 0 | 1.8 | 148.5292
7552 | 52.0354 | 0 | 42.9 | 31.3 | 0 | 26.0177 | 0 | 0 | 0 | 0 | 5.2 | 122.0999
7553 | 60.8502 | 0 | 42.9 | 39 | 0 | 30.4251 | 0 | 0 | 0 | 0 | 8.5 | 109.6936
7554 | 62.2476 | 0 | 42.9 | 48.3 | 37.6 | 31.1238 | 0 | 0 | 0 | 0 | 422.3 | 127.9056
7555 | 61.6808 | 0 | 42.9 | 55.7 | 75.1 | 30.8404 | 0 | 0 | 0 | 0 | 350.5 | 219.5618
7556 | 47.4324 | 0 | 42.9 | 20.5 | 75.1 | 23.7162 | 0 | 0 | 0 | 0 | 284.6 | 199.1156
7557 | 43.3687 | 0 | 42.9 | 33.3 | 75.1 | 21.6843 | 0 | 0 | 0 | 0 | 332.4 | 285.8069
7558 | 42.5056 | 0 | 42.9 | 44.9 | 93.9 | 21.2528 | 0 | 0 | 0 | 0 | 358.6 | 306.1841
7559 | 40.5661 | 0 | 0 | 0 | 0 | 20.283 | 0 | 0 | 0 | 0 | 4.8 | 138.0334
7560 | 40.2565 | 0 | 0 | 0 | 0 | 20.1282 | 0 | 0 | 0 | 0 | 13.8 | 157.1038
7561 | 42.2452 | 0 | 0 | 0 | 0 | 21.1226 | 0 | 0 | 0 | 0 | 23.1 | 99.4689
7562 | 41.8981 | 0 | 0 | 2.4 | 0 | 20.9491 | 0 | 0 | 0 | 0 | 52.2 | 83.732
7563 | 40.8481 | 0 | 0 | 7.5 | 0 | 20.424 | 0 | 0 | 0 | 0 | 84.4 | 80.1872
7564 | 40.0407 | 0 | 0 | 13.9 | 0 | 20.0204 | 0 | 0 | 0 | 0 | 110.2 | 78.5289
7565 | 41.3502 | 0 | 0 | 23.4 | 0 | 20.6751 | 0 | 0 | 0 | 0.9 | 132.9 | 73.9325
7566 | 43.1586 | 0 | 0 | 33.4 | 0 | 21.5793 | 0 | 0 | 0 | 2.1 | 148.4 | 96.1097
7567 | 59.083 | 0 | 42.9 | 195.2 | 56.3 | 29.5415 | 0 | 0 | 0 | 19.2 | 654.4 | 163.9238
7568 | 103.7273 | 0.7 | 43 | 222.8 | 37.6 | 51.8637 | 0 | 0 | 0 | 71.3 | 602.9 | 134.6514
7569 | 202.5154 | 2.1 | 43.2 | 209.1 | 0 | 101.2577 | 0 | 0 | 0 | 70.9 | 141.9 | 126.097
7570 | 331.419 | 3.5 | 43.4 | 202.3 | 0 | 165.7095 | 0 | 0 | 0 | 82 | 183.3 | 81.4909
7571 | 390.9871 | 3.5 | 43.4 | 180 | 0 | 195.4935 | 0 | 0 | 0 | 69.8 | 170.6 | 76.1458
7572 | 330.3321 | 2.8 | 43.3 | 151 | 0 | 165.1661 | 0 | 0 | 0 | 47.3 | 149.8 | 178.908
7573 | 283.8723 | 1.4 | 43.1 | 132.5 | 75.1 | 141.9361 | 0 | 0 | 0 | 21.6 | 571.8 | 162.2398
7574 | 276.5736 | 2.1 | 43.2 | 128.9 | 37.6 | 138.2868 | 0 | 0 | 0 | 9.3 | 504.4 | 124.3994
7575 | 252.9191 | 3.5 | 43.4 | 133.9 | 0 | 126.4595 | 0 | 0 | 0 | 26.8 | 76.8 | 212.2518
7576 | 264.4869 | 2.8 | 43.3 | 136.3 | 0 | 132.2435 | 0 | 0 | 0 | 33.6 | 124.1 | 149.261
7577 | 294.4871 | 2.1 | 43.2 | 138 | 0 | 147.2436 | 0 | 0 | 0 | 33.9 | 146.7 | 145.2513
7578 | 169.0999 | 0.7 | 43 | 143.8 | 37.6 | 84.55 | 0 | 0 | 0 | 21 | 618.9 | 182.9305
7579 | 91.0106 | 0 | 42.9 | 105 | 75.1 | 45.5053 | 0 | 0 | 0 | 0 | 545.9 | 250.3578
7580 | 58.2065 | 0 | 42.9 | 78.5 | 75.1 | 29.1033 | 0 | 0 | 0 | 0 | 470.7 | 323.7077
7581 | 45.8292 | 0 | 42.9 | 95 | 75.1 | 22.9146 | 0 | 0 | 0 | 0 | 525.7 | 282.5318
7582 | 42.6026 | 0 | 42.9 | 109.9 | 93.9 | 21.3013 | 0 | 0 | 0 | 0 | 564.1 | 225.7393
7583 | 40.9436 | 0 | 0 | 6.1 | 0 | 20.4718 | 0 | 0 | 0 | 0 | 101.9 | 188.9199
7584 | 41.6929 | 0 | 0 | 22.2 | 0 | 20.8465 | 0 | 0 | 0 | 0 | 164.6 | 245.8941
7585 | 41.225 | 0 | 0 | 36.2 | 0 | 20.6125 | 0 | 0 | 0 | 0 | 190.9 | 102.0973
7586 | 40.355 | 0 | 0 | 47.6 | 0 | 20.1775 | 0 | 0 | 0 | 0 | 213.1 | 76.7329
7587 | 41.6378 | 0 | 0 | 58.7 | 0 | 20.8189 | 0 | 0 | 0 | 0 | 236.1 | 76.7352
7588 | 42.2716 | 0 | 0 | 67.7 | 0 | 21.1358 | 0 | 0 | 0 | 0 | 255.4 | 78.1616
7589 | 41.952 | 0 | 0 | 74.9 | 0 | 20.976 | 0 | 0 | 0 | 0 | 271 | 75.9143
7590 | 43.0306 | 0 | 0 | 81.4 | 0 | 21.5153 | 0 | 0 | 0 | 0 | 280.9 | 87.1742
7591 | 61.201 | 0 | 42.9 | 242.1 | 56.3 | 30.6005 | 0 | 0 | 0 | 12.1 | 805.9 | 111.2684
7592 | 92.3826 | 0.7 | 43 | 279.6 | 37.6 | 46.1913 | 0 | 0 | 0 | 64.5 | 761.3 | 124.254
7593 | 165.039 | 2.1 | 43.2 | 268.6 | 0 | 82.5195 | 0 | 0 | 0 | 68.9 | 252.7 | 125.3246
7594 | 296.6172 | 3.5 | 43.4 | 269.4 | 0 | 148.3086 | 0 | 0 | 0 | 93.1 | 307.7 | 125.3387
7595 | 384.8196 | 3.5 | 43.4 | 258.2 | 0 | 192.4098 | 0 | 0 | 0 | 93.7 | 307.6 | 89.9055
7596 | 401.1497 | 2.8 | 43.3 | 241 | 0 | 200.5749 | 0 | 0 | 0 | 77.7 | 303.7 | 122.5464
7597 | 380.309 | 1.4 | 43.1 | 216.1 | 75.1 | 190.1545 | 0 | 0 | 0 | 52.9 | 766.4 | 209.6329
7598 | 367.7097 | 2.1 | 43.2 | 152.9 | 37.6 | 183.8549 | 0 | 0 | 0 | 56.6 | 623.2 | 94.7967
7599 | 375.5991 | 3.5 | 43.4 | 120.8 | 0 | 187.7996 | 0 | 0 | 0 | 78.4 | 98 | 104.8628
7600 | 324.3689 | 2.8 | 43.3 | 110.5 | 0 | 162.1845 | 0 | 0 | 0 | 78.6 | 131.5 | 142.462
7601 | 278.0538 | 2.1 | 43.2 | 120 | 0 | 139.0269 | 0 | 0 | 0 | 64.8 | 156.2 | 217.5026
7602 | 158.2409 | 0.7 | 43 | 130.5 | 37.6 | 79.1204 | 0 | 0 | 0 | 42.2 | 634.9 | 190.7776
7603 | 92.7657 | 0 | 42.9 | 89.7 | 75.1 | 46.3828 | 0 | 0 | 0 | 0.2 | 553.9 | 206.3403
7604 | 61.3789 | 0 | 42.9 | 59.6 | 75.1 | 30.6895 | 0 | 0 | 0 | 0 | 472.6 | 264.0545
7605 | 43.8946 | 0 | 42.9 | 76 | 75.1 | 21.9473 | 0 | 0 | 0 | 0 | 519.8 | 271.1671
7606 | 41.3217 | 0 | 42.9 | 86.6 | 93.9 | 20.6608 | 0 | 0 | 0 | 0 | 539 | 256.782
7607 | 42.7203 | 0 | 0 | 0 | 0 | 21.3602 | 0 | 0 | 0 | 0 | 85.3 | 205.9836
7608 | 39.0843 | 0 | 0 | 7.2 | 0 | 19.5422 | 0 | 0 | 0 | 0.6 | 149.6 | 115.3849
7609 | 42.1987 | 0 | 0 | 21.2 | 0 | 21.0994 | 0 | 0 | 0 | 1.6 | 180.3 | 91.5785
7610 | 42.4275 | 0 | 0 | 36.9 | 0 | 21.2137 | 0 | 0 | 0 | 4.7 | 209 | 86.1022
7611 | 44.7116 | 0 | 0 | 51.4 | 0 | 22.3558 | 0 | 0 | 0 | 8.4 | 237.1 | 86.5821
7612 | 42.186 | 0 | 0 | 62.8 | 0 | 21.093 | 0 | 0 | 0 | 11.1 | 259.1 | 86.4634
7613 | 41.9523 | 0 | 0 | 72.8 | 0 | 20.9762 | 0 | 0 | 0 | 13.5 | 278.6 | 88.0063
7614 | 41.6353 | 0 | 0 | 80.8 | 0 | 20.8176 | 0 | 0 | 0 | 15 | 290.2 | 115.8361
7615 | 68.2452 | 0 | 42.9 | 243.5 | 56.3 | 34.1226 | 0 | 0 | 0 | 29.7 | 820.9 | 130.9314
7616 | 122.9057 | 0.7 | 43 | 282 | 37.6 | 61.4528 | 0 | 0 | 0 | 79.7 | 777.1 | 119.4042
7617 | 207.7488 | 2.1 | 43.2 | 273.5 | 0 | 103.8744 | 0 | 0 | 0 | 90.4 | 266.2 | 128.246
7618 | 341.6012 | 3.5 | 43.4 | 272.4 | 0 | 170.8006 | 0 | 0 | 0 | 117.3 | 317.9 | 176.4195
7619 | 409.3143 | 3.5 | 43.4 | 261.8 | 0 | 204.6572 | 0 | 0 | 0 | 115.4 | 317.4 | 177.9595
7620 | 413.7751 | 2.8 | 43.3 | 250.3 | 0 | 206.8875 | 0 | 0 | 0 | 96.7 | 320.2 | 359.9707
7621 | 371.9392 | 1.4 | 43.1 | 231.2 | 75.1 | 185.9696 | 0 | 0 | 0 | 66.2 | 799.1 | 157.7733
7622 | 338.2386 | 2.1 | 43.2 | 176.3 | 37.6 | 169.1193 | 0 | 0 | 0 | 52.9 | 668.7 | 157.978
7623 | 336.5148 | 3.5 | 43.4 | 142.6 | 0 | 168.2574 | 0 | 0 | 0 | 60.4 | 129.2 | 101.7456
7624 | 318.9103 | 2.8 | 43.3 | 128.7 | 0 | 159.4551 | 0 | 0 | 0 | 56.6 | 166.2 | 96.2285
7625 | 360.5502 | 2.1 | 43.2 | 134 | 0 | 180.2751 | 0 | 0 | 0 | 51.5 | 187.1 | 138.9203
7626 | 282.4098 | 0.7 | 43 | 146.4 | 37.6 | 141.2049 | 0 | 0 | 0 | 35 | 672.6 | 456.8649
7627 | 177.3126 | 0 | 42.9 | 107.6 | 75.1 | 88.6563 | 0 | 0 | 0 | 0 | 604.4 | 266.0363
7628 | 103.8113 | 0 | 42.9 | 80.7 | 75.1 | 51.9057 | 0 | 0 | 0 | 0 | 531.2 | 355.9252
7629 | 61.8261 | 0 | 42.9 | 100.5 | 75.1 | 30.9131 | 0 | 0 | 0 | 0 | 587 | 536.9953
7630 | 43.5252 | 0 | 42.9 | 115 | 93.9 | 21.7626 | 0 | 0 | 0 | 0 | 618.3 | 272.2463
7631 | 42.1941 | 0 | 0 | 13.7 | 0 | 21.097 | 0 | 0 | 0 | 0 | 151 | 195.67
7632 | 42.6494 | 0 | 0 | 39.1 | 0 | 21.3247 | 0 | 0 | 0 | 0 | 236.9 | 152.5764
7633 | 43.0662 | 0 | 0 | 59.9 | 0 | 21.5331 | 0 | 0 | 0 | 0.8 | 276.1 | 110.2997
7634 | 42.7179 | 0 | 0 | 78.9 | 0 | 21.3589 | 0 | 0 | 0 | 2.3 | 314 | 95.1541
7635 | 39.7634 | 0 | 0 | 96.5 | 0 | 19.8817 | 0 | 0 | 0 | 5.9 | 350.8 | 81.4919
7636 | 44.1729 | 0 | 0 | 110.8 | 0 | 22.0865 | 0 | 0 | 0 | 10.8 | 380.9 | 76.1467
7637 | 41.0613 | 0 | 0 | 122.6 | 0 | 20.5307 | 0 | 0 | 0 | 15 | 406.9 | 80.7788
7638 | 41.8324 | 0 | 0 | 132.9 | 0 | 20.9162 | 0 | 0 | 0 | 18.1 | 426 | 90.1427
7639 | 53.0237 | 0 | 42.9 | 303.1 | 56.3 | 26.5119 | 0 | 0 | 0 | 35.6 | 978.7 | 121.1396
7640 | 99.5874 | 0.7 | 43 | 352.4 | 37.6 | 49.7937 | 0 | 0 | 0 | 89.4 | 937.2 | 117.9207
7641 | 188.0269 | 2.1 | 43.2 | 333.4 | 0 | 94.0134 | 0 | 0 | 0 | 104.4 | 375.4 | 95.0333
7642 | 268.0982 | 3.5 | 43.4 | 295.7 | 0 | 134.0491 | 0 | 0 | 0 | 138 | 388.9 | 177.4003
7643 | 312.4307 | 3.5 | 43.4 | 253.1 | 0 | 156.2154 | 0 | 0 | 0 | 140.5 | 353.2 | 109.8116
7644 | 288.6076 | 2.8 | 43.3 | 215.6 | 0 | 144.3038 | 0 | 0 | 0 | 113.5 | 322 | 208.1345
7645 | 258.0613 | 1.4 | 43.1 | 170.6 | 75.1 | 129.0307 | 0 | 0 | 0 | 76.5 | 753.1 | 228.4064
7646 | 240.6306 | 2.1 | 43.2 | 160.2 | 37.6 | 120.3153 | 0 | 0 | 0 | 65.8 | 657.3 | 139.5547
7647 | 252.3067 | 3.5 | 43.4 | 166.8 | 0 | 126.1533 | 0 | 0 | 0 | 86.7 | 172.6 | 200.5305
7648 | 293.2735 | 2.8 | 43.3 | 186.3 | 0 | 146.6367 | 0 | 0 | 0 | 89.6 | 254.8 | 203.3859
7649 | 349.5414 | 2.1 | 43.2 | 197.1 | 0 | 174.7707 | 0 | 0 | 0 | 77.7 | 291.8 | 192.0185
7650 | 300.8319 | 0.7 | 43 | 204.6 | 37.6 | 150.4159 | 0 | 0 | 0 | 49.4 | 797.3 | 248.6084
7651 | 213.9485 | 0 | 42.9 | 156.5 | 75.1 | 106.9742 | 0 | 0 | 0 | 2.2 | 739.1 | 252.9221
7652 | 110.285 | 0 | 42.9 | 125.3 | 75.1 | 55.1425 | 0 | 0 | 0 | 0.1 | 660 | 303.6707
7653 | 55.8753 | 0 | 42.9 | 143.5 | 75.1 | 27.9377 | 0 | 0 | 0 | 1.4 | 713.3 | 350.4707
7654 | 41.0167 | 0 | 42.9 | 156.5 | 93.9 | 20.5083 | 0 | 0 | 0 | 3 | 746.3 | 210.8017
7655 | 41.4143 | 0 | 0 | 45.6 | 0 | 20.7072 | 0 | 0 | 0 | 5.8 | 249.5 | 143.483
7656 | 41.3303 | 0 | 0 | 74.3 | 0 | 20.6652 | 0 | 0 | 0 | 9.8 | 339.3 | 97.7936
7657 | 41.5222 | 0 | 0 | 91.3 | 0 | 20.7611 | 0 | 0 | 0 | 13.7 | 369.4 | 82.9119
7658 | 42.9314 | 0 | 0 | 105.8 | 0 | 21.4657 | 0 | 0 | 0 | 17.7 | 396.3 | 82.3191
7659 | 41.9381 | 0 | 0 | 118.9 | 0 | 20.969 | 0 | 0 | 0 | 21.6 | 422.1 | 79.5951
7660 | 39.4962 | 0 | 0 | 129.8 | 0 | 19.7481 | 0 | 0 | 0 | 24.2 | 444.7 | 77.8023
7661 | 42.513 | 0 | 0 | 138.5 | 0 | 21.2565 | 0 | 0 | 0 | 25.9 | 463.6 | 81.4903
7662 | 40.0073 | 0 | 0 | 146 | 0 | 20.0036 | 0 | 0 | 0 | 27.4 | 475.7 | 104.376
7663 | 56.6957 | 0 | 42.9 | 316.3 | 56.3 | 28.3478 | 0 | 0 | 0 | 40.6 | 1031 | 119.3847
7664 | 82.5832 | 0.7 | 43 | 363.8 | 37.6 | 41.2916 | 0 | 0 | 0 | 93.5 | 991.8 | 152.7664
7665 | 156.4913 | 2.1 | 43.2 | 322.6 | 0 | 78.2457 | 0 | 0 | 0 | 98.3 | 387.5 | 168.3266
7666 | 264.46 | 3.5 | 43.4 | 272.6 | 0 | 132.23 | 0 | 0 | 0 | 120.2 | 383.6 | 196.1938
7667 | 309.2441 | 3.5 | 43.4 | 213.6 | 0 | 154.622 | 0 | 0 | 0 | 103 | 327.8 | 193.9683
7668 | 301.3423 | 2.8 | 43.3 | 153.4 | 0 | 150.6711 | 0 | 0 | 0 | 63.1 | 265.6 | 265.3944
7669 | 233.2951 | 1.4 | 43.1 | 100.6 | 75.1 | 116.6475 | 0 | 0 | 0 | 32.2 | 665.6 | 187.1884
7670 | 203.2971 | 2.1 | 43.2 | 66.5 | 37.6 | 101.6485 | 0 | 0 | 0 | 28.9 | 536.4 | 157.3189
7671 | 206.3244 | 3.5 | 43.4 | 52.9 | 0 | 103.1622 | 0 | 0 | 0 | 55.4 | 59.6 | 138.7311
7672 | 244.1241 | 2.8 | 43.3 | 60 | 0 | 122.062 | 0 | 0 | 0 | 65.1 | 102.2 | 146.4216
7673 | 242.3371 | 2.1 | 43.2 | 88.3 | 0 | 121.1685 | 0 | 0 | 0 | 58.7 | 147.8 | 195.4031
7674 | 143.99 | 0.7 | 43 | 108.7 | 37.6 | 71.995 | 0 | 0 | 0 | 37.9 | 633.6 | 353.5347
7675 | 94.6804 | 0 | 42.9 | 65.4 | 75.1 | 47.3402 | 0 | 0 | 0 | 0 | 550.8 | 277.6378
7676 | 50.6354 | 0 | 42.9 | 36.9 | 75.1 | 25.3177 | 0 | 0 | 0 | 0 | 475.6 | 185.7208
7677 | 42.116 | 0 | 42.9 | 58.5 | 75.1 | 21.058 | 0 | 0 | 0 | 0 | 526.2 | 199.8868
7678 | 42.6478 | 0 | 42.9 | 74.6 | 93.9 | 21.3239 | 0 | 0 | 0 | 0 | 551.4 | 187.4485
7679 | 44.1017 | 0 | 0 | 0 | 0 | 22.0508 | 0 | 0 | 0 | 0 | 97.8 | 120.9984
7680 | 40.7502 | 0 | 0 | 1.5 | 0 | 20.3751 | 0 | 0 | 0 | 0 | 166.9 | 107.5188
7681 | 42.2806 | 0 | 0 | 12.7 | 0 | 21.1403 | 0 | 0 | 0 | 0 | 198.7 | 91.6993
7682 | 42.1901 | 0 | 0 | 28.5 | 0 | 21.095 | 0 | 0 | 0 | 0.3 | 228.4 | 82.0804
7683 | 42.4684 | 0 | 0 | 45.8 | 0 | 21.2342 | 0 | 0 | 0 | 1.4 | 256.7 | 75.6743
7684 | 41.0908 | 0 | 0 | 59.1 | 0 | 20.5454 | 0 | 0 | 0 | 2.3 | 278.2 | 74.509
7685 | 40.4765 | 0 | 0 | 70.6 | 0 | 20.2382 | 0 | 0 | 0 | 4 | 297.1 | 76.8552
7686 | 42.5871 | 0 | 0 | 80.6 | 0 | 21.2935 | 0 | 0 | 0 | 7 | 310.1 | 92.5299
7687 | 44.1302 | 0 | 42.9 | 247.4 | 56.3 | 22.0651 | 0 | 0 | 0 | 24.1 | 840.5 | 122.4211
7688 | 76.9507 | 0 | 42.9 | 255.1 | 37.6 | 38.4753 | 0 | 0 | 0 | 25.4 | 790.5 | 122.4873
7689 | 80.5814 | 0 | 42.9 | 208.4 | 0 | 40.2907 | 0 | 0 | 0 | 24.9 | 238.3 | 172.0685
7690 | 74.6569 | 0 | 42.9 | 163.7 | 0 | 37.3285 | 0 | 0 | 0 | 24 | 239.3 | 300.7889
7691 | 73.7891 | 0 | 42.9 | 119.3 | 0 | 36.8946 | 0 | 0 | 0 | 23.8 | 196 | 228.6246
7692 | 69.7161 | 0 | 42.9 | 103.3 | 0 | 34.8581 | 0 | 0 | 0 | 22.5 | 175.3 | 161.7251
7693 | 69.1034 | 0 | 42.9 | 120.2 | 75.1 | 34.5517 | 0 | 0 | 0 | 21.9 | 648 | 260.6723
7694 | 61.4985 | 0 | 42.9 | 130.2 | 37.6 | 30.7493 | 0 | 0 | 0 | 23 | 601.2 | 185.8035
7695 | 59.7273 | 0 | 42.9 | 136 | 0 | 29.8637 | 0 | 0 | 0 | 23.9 | 143.3 | 98.7549
7696 | 69.3201 | 0 | 42.9 | 140.7 | 0 | 34.66 | 0 | 0 | 0 | 25.2 | 203.7 | 100.9071
7697 | 81.8595 | 0 | 42.9 | 150.5 | 0 | 40.9298 | 0 | 0 | 0 | 26.9 | 229 | 161.5092
7698 | 80.3998 | 0 | 42.9 | 160.5 | 37.6 | 40.1999 | 0 | 0 | 0 | 28.6 | 715.7 | 132.3107
7699 | 81.3308 | 0 | 42.9 | 136.5 | 75.1 | 40.6654 | 0 | 0 | 0 | 28.9 | 648.6 | 179.22
7700 | 66.9724 | 0 | 42.9 | 101.2 | 75.1 | 33.4862 | 0 | 0 | 0 | 19.3 | 566.5 | 234.5249
7701 | 51.5271 | 0 | 42.9 | 115.7 | 75.1 | 25.7635 | 0 | 0 | 0 | 23.3 | 613.9 | 239.7917
7702 | 43.9046 | 0 | 42.9 | 125.6 | 93.9 | 21.9523 | 0 | 0 | 0 | 25.5 | 638.9 | 166.0702
7703 | 40.0302 | 0 | 0 | 18.8 | 0 | 20.0151 | 0 | 0 | 0 | 27.6 | 159 | 148.781
7704 | 44.2182 | 0 | 0 | 41.7 | 0 | 22.1091 | 0 | 0 | 0 | 29.7 | 236.6 | 176.6958
7705 | 40.5137 | 0 | 0 | 57.2 | 0 | 20.2568 | 0 | 0 | 0 | 31.8 | 264.9 | 132.6972
7706 | 42.6469 | 0 | 0 | 72.5 | 0 | 21.3234 | 0 | 0 | 0 | 33.7 | 295.2 | 99.716
7707 | 40.3649 | 0 | 0 | 86.6 | 0 | 20.1825 | 0 | 0 | 0 | 35.7 | 324.4 | 88.7172
7708 | 39.9741 | 0 | 0 | 97.7 | 0 | 19.9871 | 0 | 0 | 0 | 37.8 | 347.9 | 81.9608
7709 | 42.7064 | 0 | 0 | 107.4 | 0 | 21.3532 | 0 | 0 | 0 | 39.2 | 370 | 86.3441
7710 | 42.3156 | 0 | 0 | 115.3 | 0 | 21.1578 | 0 | 0 | 0 | 40.2 | 384 | 138.3937
7711 | 50.2397 | 0 | 42.9 | 281 | 56.3 | 25.1198 | 0 | 0 | 0 | 54 | 931.3 | 144.0116
7712 | 76.0317 | 0 | 42.9 | 276.2 | 37.6 | 38.0159 | 0 | 0 | 0 | 54.4 | 891.1 | 160.9796
7713 | 79.0234 | 0 | 42.9 | 255.1 | 0 | 39.5117 | 0 | 0 | 0 | 51.4 | 344.8 | 288.9321
7714 | 78.4941 | 0 | 42.9 | 235.5 | 0 | 39.247 | 0 | 0 | 0 | 45.6 | 381.7 | 181.0488
7715 | 75.7699 | 0 | 42.9 | 210.6 | 0 | 37.8849 | 0 | 0 | 0 | 38.7 | 358.5 | 178.8379
7716 | 76.3342 | 0 | 42.9 | 185.4 | 0 | 38.1671 | 0 | 0 | 0 | 33 | 333.6 | 150.306
7717 | 73.1739 | 0 | 42.9 | 170.7 | 75.1 | 36.587 | 0 | 0 | 0 | 30.2 | 792.7 | 140.9638
7718 | 70.4903 | 0 | 42.9 | 154 | 37.6 | 35.2452 | 0 | 0 | 0 | 28.6 | 717.2 | 345.855
7719 | 71.3079 | 0 | 42.9 | 153.5 | 0 | 35.6539 | 0 | 0 | 0 | 28.6 | 213.4 | 229.5443
7720 | 76.2902 | 0 | 42.9 | 160.1 | 0 | 38.1451 | 0 | 0 | 0 | 31.3 | 278.2 | 187.2872
7721 | 80.476 | 0 | 42.9 | 173.4 | 0 | 40.238 | 0 | 0 | 0 | 35.3 | 305.2 | 137.8752
7722 | 83.0537 | 0 | 42.9 | 185.9 | 37.6 | 41.5268 | 0 | 0 | 0 | 36.1 | 808.8 | 234.122
7723 | 76.0274 | 0 | 42.9 | 176.8 | 75.1 | 38.0137 | 0 | 0 | 0 | 34.5 | 743.6 | 337.3336
7724 | 66.1877 | 0 | 42.9 | 135.8 | 75.1 | 33.0938 | 0 | 0 | 0 | 22.8 | 646.1 | 243.051
7725 | 54.3548 | 0 | 42.9 | 145.4 | 75.1 | 27.1774 | 0 | 0 | 0 | 25 | 682.3 | 238.8795
7726 | 42.6162 | 0 | 42.9 | 148.8 | 93.9 | 21.3081 | 0 | 0 | 0 | 24.9 | 693.6 | 272.8749
7727 | 43.8469 | 0 | 0 | 47 | 0 | 21.9235 | 0 | 0 | 0 | 24.9 | 186.3 | 210.3758
7728 | 41.3068 | 0 | 0 | 66.5 | 0 | 20.6534 | 0 | 0 | 0 | 25.2 | 257.7 | 158.9058
7729 | 41.8631 | 0 | 0 | 72.8 | 0 | 20.9315 | 0 | 0 | 0 | 27.1 | 270.8 | 185.9298
7730 | 41.9855 | 0 | 0 | 76.6 | 0 | 20.9928 | 0 | 0 | 0 | 26.9 | 278.4 | 83.3837
7731 | 42.8849 | 0 | 0 | 79.4 | 0 | 21.4425 | 0 | 0 | 0 | 26 | 284.6 | 83.5003
7732 | 44.1562 | 0 | 0 | 81.8 | 0 | 22.0781 | 0 | 0 | 0 | 25.5 | 289.7 | 78.1678
7733 | 41.3573 | 0 | 0 | 84.4 | 0 | 20.6786 | 0 | 0 | 0 | 25.3 | 295.3 | 81.0145
7734 | 44.256 | 0 | 0 | 86.8 | 0 | 22.128 | 0 | 0 | 0 | 25.5 | 296.1 | 121.6178
7735 | 61.9371 | 0 | 42.9 | 244.6 | 56.3 | 30.9685 | 0 | 0 | 0 | 38.3 | 830.2 | 129.9797
7736 | 102.1498 | 0.7 | 43 | 280.7 | 37.6 | 51.0749 | 0 | 0 | 0 | 95.5 | 791.3 | 123.7012
7737 | 175.3948 | 2.1 | 43.2 | 238.7 | 0 | 87.6974 | 0 | 0 | 0 | 97.8 | 226.2 | 167.0252
7738 | 301.9776 | 3.5 | 43.4 | 174.7 | 0 | 150.9888 | 0 | 0 | 0 | 115 | 211.9 | 101.6228
7739 | 380.6725 | 3.5 | 43.4 | 90.7 | 0 | 190.3363 | 0 | 0 | 0 | 107.2 | 128.8 | 145.3113
7740 | 378.6075 | 2.8 | 43.3 | 79.3 | 0 | 189.3038 | 0 | 0 | 0 | 89.7 | 110.3 | 144.0715
7741 | 343.0684 | 1.4 | 43.1 | 87.4 | 75.1 | 171.5342 | 0 | 0 | 0 | 65.4 | 558.1 | 210.6142
7742 | 289.4912 | 2.1 | 43.2 | 73.4 | 37.6 | 144.7456 | 0 | 0 | 0 | 63.6 | 483.7 | 149.8442
7743 | 302.6753 | 3.5 | 43.4 | 79.3 | 0 | 151.3376 | 0 | 0 | 0 | 77.1 | 51.9 | 314.3068
7744 | 319.7706 | 2.8 | 43.3 | 92 | 0 | 159.8853 | 0 | 0 | 0 | 75.4 | 96.4 | 226.6308
7745 | 276.5234 | 2.1 | 43.2 | 101.4 | 0 | 138.2617 | 0 | 0 | 0 | 66.9 | 121.4 | 213.4719
7746 | 173.5718 | 0.7 | 43 | 108.4 | 37.6 | 86.7859 | 0 | 0 | 0 | 44.9 | 591.2 | 175.1523
7747 | 122.588 | 0 | 42.9 | 71.6 | 75.1 | 61.294 | 0 | 0 | 0 | 1.7 | 508.9 | 243.9126
7748 | 73.6615 | 0 | 42.9 | 41.5 | 75.1 | 36.8307 | 0 | 0 | 0 | 0 | 423.8 | 361.8218
7749 | 46.6728 | 0 | 42.9 | 55.4 | 75.1 | 23.3364 | 0 | 0 | 0 | 0.3 | 465.7 | 272.4328
7750 | 41.939 | 0 | 42.9 | 64.7 | 93.9 | 20.9695 | 0 | 0 | 0 | 1.2 | 478.5 | 208.498
7751 | 44.4327 | 0 | 0 | 0 | 0 | 22.2163 | 0 | 0 | 0 | 1.8 | 39.3 | 151.6089
7752 | 44.3251 | 0 | 0 | 0 | 0 | 22.1626 | 0 | 0 | 0 | 2.1 | 86.1 | 117.9449
7753 | 43.1022 | 0 | 0 | 2.9 | 0 | 21.5511 | 0 | 0 | 0 | 2.7 | 116.9 | 108.6072
7754 | 43.2766 | 0 | 0 | 15.1 | 0 | 21.6383 | 0 | 0 | 0 | 4.3 | 150.9 | 91.2207
7755 | 40.7722 | 0 | 0 | 31.8 | 0 | 20.3861 | 0 | 0 | 0 | 7 | 183.9 | 80.0689
7756 | 41.8857 | 0 | 0 | 44.7 | 0 | 20.9429 | 0 | 0 | 0 | 8.8 | 208.7 | 79.2397
7757 | 41.5439 | 0 | 0 | 55.9 | 0 | 20.7719 | 0 | 0 | 0 | 10.3 | 230.4 | 80.0664
7758 | 42.9732 | 0 | 0 | 65.2 | 0 | 21.4866 | 0 | 0 | 0 | 11.8 | 244.5 | 88.3632
7759 | 60.2127 | 0 | 42.9 | 228.7 | 56.3 | 30.1063 | 0 | 0 | 0 | 25.8 | 774.4 | 129.0485
7760 | 101.9918 | 0.7 | 43 | 263.8 | 37.6 | 50.9959 | 0 | 0 | 0 | 77.2 | 732.5 | 121.0458
7761 | 159.8868 | 2.1 | 43.2 | 236.2 | 0 | 79.9434 | 0 | 0 | 0 | 83.4 | 211.9 | 155.4751
7762 | 243.6366 | 3.5 | 43.4 | 203.6 | 0 | 121.8183 | 0 | 0 | 0 | 103 | 226.2 | 152.0547
7763 | 261.7165 | 3.5 | 43.4 | 159.2 | 0 | 130.8583 | 0 | 0 | 0 | 101.4 | 187.4 | 83.9697
7764 | 242.2701 | 2.8 | 43.3 | 117.7 | 0 | 121.1351 | 0 | 0 | 0 | 86.8 | 147.8 | 157.9392
7765 | 224.3532 | 1.4 | 43.1 | 81 | 75.1 | 112.1766 | 0 | 0 | 0 | 62.9 | 536.7 | 221.3847
7766 | 213.4157 | 2.1 | 43.2 | 59.8 | 37.6 | 106.7079 | 0 | 0 | 0 | 67.6 | 437.3 | 196.7702
7767 | 207.0614 | 3.5 | 43.4 | 57 | 0 | 103.5307 | 0 | 0 | 0 | 83.4 | 20.7 | 115.2601
7768 | 257.139 | 2.8 | 43.3 | 69.2 | 0 | 128.5695 | 0 | 0 | 0 | 77.6 | 54.2 | 109.8135
7769 | 270.0665 | 2.1 | 43.2 | 86.3 | 0 | 135.0332 | 0 | 0 | 0 | 66.2 | 87.7 | 231.4136
7770 | 165.5222 | 0.7 | 43 | 100.9 | 37.6 | 82.7611 | 0 | 0 | 0 | 43.1 | 560.5 | 346.9594
7771 | 94.2654 | 0 | 42.9 | 64.7 | 75.1 | 47.1327 | 0 | 0 | 0 | 1.3 | 485.3 | 637.7795
7772 | 66.7093 | 0 | 42.9 | 38.6 | 75.1 | 33.3546 | 0 | 0 | 0 | 0 | 419 | 331.1858
7773 | 52.3072 | 0 | 42.9 | 59.8 | 75.1 | 26.1536 | 0 | 0 | 0 | 0 | 476 | 207.816
7774 | 42.1507 | 0 | 42.9 | 75.6 | 93.9 | 21.0753 | 0 | 0 | 0 | 0.2 | 505.8 | 241.2227
7775 | 41.7215 | 0 | 0 | 0 | 0 | 20.8607 | 0 | 0 | 0 | 1.1 | 72.5 | 232.2085
7776 | 39.6031 | 0 | 0 | 3.6 | 0 | 19.8016 | 0 | 0 | 0 | 2 | 141.5 | 158.0522
7777 | 40.9625 | 0 | 0 | 18 | 0 | 20.4812 | 0 | 0 | 0 | 4.1 | 178.1 | 118.4531
7778 | 42.3115 | 0 | 0 | 36.2 | 0 | 21.1558 | 0 | 0 | 0 | 8.4 | 211.4 | 102.5784
7779 | 40.9426 | 0 | 0 | 53.8 | 0 | 20.4713 | 0 | 0 | 0 | 12.9 | 244.6 | 103.1813
7780 | 41.3288 | 0 | 0 | 68.9 | 0 | 20.6644 | 0 | 0 | 0 | 16.6 | 274.5 | 99.9501
7781 | 42.4612 | 0 | 0 | 81.3 | 0 | 21.2306 | 0 | 0 | 0 | 19.2 | 299.5 | 96.8344
7782 | 42.7594 | 0 | 0 | 91.7 | 0 | 21.3797 | 0 | 0 | 0 | 22.4 | 316.4 | 101.4984
7783 | 60.645 | 0 | 42.9 | 258.3 | 56.3 | 30.3225 | 0 | 0 | 0 | 36.8 | 848.2 | 103.4201
7784 | 101.2201 | 0.7 | 43 | 301.4 | 37.6 | 50.61 | 0 | 0 | 0 | 89.6 | 805.6 | 91.9391
7785 | 173.137 | 2.1 | 43.2 | 284.2 | 0 | 86.5685 | 0 | 0 | 0 | 89 | 284.9 | 102.4611
7786 | 279.4404 | 3.5 | 43.4 | 263.2 | 0 | 139.7202 | 0 | 0 | 0 | 97.9 | 314.5 | 100.9047
7787 | 318.1866 | 3.5 | 43.4 | 230 | 0 | 159.0933 | 0 | 0 | 0 | 82.6 | 288.5 | 123.3581
7788 | 321.8561 | 2.8 | 43.3 | 197.4 | 0 | 160.928 | 0 | 0 | 0 | 56.9 | 264.3 | 142.9836
7789 | 268.9746 | 1.4 | 43.1 | 166.7 | 75.1 | 134.4873 | 0 | 0 | 0 | 32.1 | 701.8 | 169.8717
7790 | 222.8795 | 2.1 | 43.2 | 152.3 | 37.6 | 111.4398 | 0 | 0 | 0 | 31.8 | 611.6 | 125.3899
7791 | 215.5378 | 3.5 | 43.4 | 158.2 | 0 | 107.7689 | 0 | 0 | 0 | 47.9 | 142.4 | 112.4828
7792 | 294.1196 | 2.8 | 43.3 | 165.8 | 0 | 147.0598 | 0 | 0 | 0 | 52.7 | 207 | 95.8742
7793 | 277.4144 | 2.1 | 43.2 | 173.3 | 0 | 138.7072 | 0 | 0 | 0 | 50.1 | 238.3 | 140.6274
7794 | 194.0902 | 0.7 | 43 | 179.3 | 37.6 | 97.0451 | 0 | 0 | 0 | 33.2 | 730.7 | 107.153
7795 | 97.5081 | 0 | 42.9 | 132.9 | 75.1 | 48.7541 | 0 | 0 | 0 | 0 | 661 | 199.5151
7796 | 72.0666 | 0 | 42.9 | 101.6 | 75.1 | 36.0333 | 0 | 0 | 0 | 0 | 576.9 | 180.7348
7797 | 48.726 | 0 | 42.9 | 116 | 75.1 | 24.363 | 0 | 0 | 0 | 0 | 623.7 | 145.3048
7798 | 40.6516 | 0 | 42.9 | 124.6 | 93.9 | 20.3258 | 0 | 0 | 0 | 0 | 644.7 | 132.2112
7799 | 45.0497 | 0 | 0 | 18 | 0 | 22.5249 | 0 | 0 | 0 | 0 | 159.5 | 120.6744
7800 | 43.02 | 0 | 0 | 40.1 | 0 | 21.51 | 0 | 0 | 0 | 0 | 235.9 | 119.6016
7801 | 42.0776 | 0 | 0 | 54.8 | 0 | 21.0388 | 0 | 0 | 0 | 0 | 262.6 | 91.2214
7802 | 42.9218 | 0 | 0 | 64.9 | 0 | 21.4609 | 0 | 0 | 0 | 0.5 | 279.9 | 77.4475
7803 | 39.1497 | 0 | 0 | 71.8 | 0 | 19.5749 | 0 | 0 | 0 | 1.6 | 290.7 | 77.447
7804 | 41.427 | 0 | 0 | 78.3 | 0 | 20.7135 | 0 | 0 | 0 | 2.3 | 301.7 | 77.6859
7805 | 41.2758 | 0 | 0 | 84.2 | 0 | 20.6379 | 0 | 0 | 0 | 3.2 | 313.2 | 79.2412
7806 | 41.2467 | 0 | 0 | 88.6 | 0 | 20.6233 | 0 | 0 | 0 | 4.8 | 317.5 | 85.2767
7807 | 59.0021 | 0 | 42.9 | 248.5 | 56.3 | 29.5011 | 0 | 0 | 0 | 21.7 | 851 | 90.5038
7808 | 87.5413 | 0.7 | 43 | 288.2 | 37.6 | 43.7707 | 0 | 0 | 0 | 72.4 | 807.3 | 100.786
7809 | 179.1247 | 2.1 | 43.2 | 278.6 | 0 | 89.5623 | 0 | 0 | 0 | 80.3 | 281.6 | 122.7727
7810 | 299.9824 | 3.5 | 43.4 | 279 | 0 | 149.9912 | 0 | 0 | 0 | 105.3 | 334.1 | 202.1234
7811 | 324.1783 | 3.5 | 43.4 | 266.6 | 0 | 162.0892 | 0 | 0 | 0 | 105.7 | 331.2 | 87.173
7812 | 309.02 | 2.8 | 43.3 | 247.2 | 0 | 154.51 | 0 | 0 | 0 | 88.9 | 323.5 | 127.9031
7813 | 286.3972 | 1.4 | 43.1 | 223.1 | 75.1 | 143.1986 | 0 | 0 | 0 | 59.8 | 800.7 | 279.9306
7814 | 268.0752 | 2.1 | 43.2 | 164.8 | 37.6 | 134.0376 | 0 | 0 | 0 | 47.3 | 665.1 | 145.8419
7815 | 224.8026 | 3.5 | 43.4 | 133 | 0 | 112.4013 | 0 | 0 | 0 | 56.1 | 126.2 | 124.0746
7816 | 242.0377 | 2.8 | 43.3 | 127.4 | 0 | 121.0188 | 0 | 0 | 0 | 53.9 | 168.1 | 128.7907
7817 | 261.1268 | 2.1 | 43.2 | 135.3 | 0 | 130.5634 | 0 | 0 | 0 | 48.9 | 190.5 | 122.8667
7818 | 185.1561 | 0.7 | 43 | 143 | 37.6 | 92.578 | 0 | 0 | 0 | 33.1 | 675.1 | 129.4646
7819 | 112.3485 | 0 | 42.9 | 103.4 | 75.1 | 56.1742 | 0 | 0 | 0 | 0 | 601.4 | 201.6545
7820 | 63.7266 | 0 | 42.9 | 75 | 75.1 | 31.8633 | 0 | 0 | 0 | 0 | 519.5 | 215.9092
7821 | 53.2338 | 0 | 42.9 | 91.2 | 75.1 | 26.6169 | 0 | 0 | 0 | 0 | 566.6 | 165.8186
7822 | 43.8962 | 0 | 42.9 | 102 | 93.9 | 21.9481 | 0 | 0 | 0 | 0 | 586.7 | 182.9606
7823 | 39.7342 | 0 | 0 | 5.6 | 0 | 19.8671 | 0 | 0 | 0 | 0 | 119.3 | 134.88
7824 | 40.9169 | 0 | 0 | 21.3 | 0 | 20.4584 | 0 | 0 | 0 | 0 | 188.7 | 99.8338
7825 | 39.7612 | 0 | 0 | 39.8 | 0 | 19.8806 | 0 | 0 | 0 | 0 | 222.8 | 79.3568
7826 | 40.9674 | 0 | 0 | 57.1 | 0 | 20.4837 | 0 | 0 | 0 | 0.1 | 256.5 | 81.0176
7827 | 41.3843 | 0 | 0 | 73.4 | 0 | 20.6921 | 0 | 0 | 0 | 1 | 290 | 83.7325
7828 | 40.9175 | 0 | 0 | 86.3 | 0 | 20.4588 | 0 | 0 | 0 | 1.9 | 316.1 | 79.9517
7829 | 44.132 | 0 | 0 | 96.5 | 0 | 22.066 | 0 | 0 | 0 | 3.1 | 337.3 | 79.2387
7830 | 40.0848 | 0 | 0 | 105.9 | 0 | 20.0424 | 0 | 0 | 0 | 5.7 | 354.1 | 83.7341
7831 | 54.0768 | 0 | 42.9 | 271.5 | 56.3 | 27.0384 | 0 | 0 | 0 | 22.6 | 898.9 | 107.6437
7832 | 91.5623 | 0.7 | 43 | 315 | 37.6 | 45.7811 | 0 | 0 | 0 | 72.9 | 855.3 | 134.2601
7833 | 129.8467 | 2.1 | 43.2 | 272.4 | 0 | 64.9233 | 0 | 0 | 0 | 80.6 | 287.5 | 104.9829
7834 | 202.9903 | 3.5 | 43.4 | 222.4 | 0 | 101.4951 | 0 | 0 | 0 | 105.2 | 287.2 | 117.2175
7835 | 254.0376 | 3.5 | 43.4 | 148.7 | 0 | 127.0188 | 0 | 0 | 0 | 105.4 | 219 | 107.3956
7836 | 259.6072 | 2.8 | 43.3 | 77.6 | 0 | 129.8036 | 0 | 0 | 0 | 88.2 | 144.1 | 94.3243
7837 | 234.1186 | 1.4 | 43.1 | 24.2 | 75.1 | 117.0593 | 0 | 0 | 0 | 57.8 | 507.6 | 111.8739
7838 | 233.9493 | 2.1 | 43.2 | 8.5 | 37.6 | 116.9747 | 0 | 0 | 0 | 37.2 | 380.6 | 202.0884
7839 | 293.981 | 3.5 | 43.4 | 4.3 | 0 | 146.9905 | 0 | 0 | 0 | 42.6 | 6.8 | 104.7369
7840 | 349.7816 | 2.8 | 43.3 | 8.8 | 0 | 174.8908 | 0 | 0 | 0 | 40.4 | 11.6 | 101.2656
7841 | 317.9266 | 2.1 | 43.2 | 20.1 | 0 | 158.9633 | 0 | 0 | 0 | 38.6 | 27.5 | 126.6126
7842 | 214.8953 | 0.7 | 43 | 44.3 | 37.6 | 107.4477 | 0 | 0 | 0 | 26.8 | 503.5 | 184.5987
7843 | 109.5743 | 0 | 42.9 | 19.9 | 75.1 | 54.7872 | 0 | 0 | 0 | 0 | 432.5 | 335.7086
7844 | 68.6305 | 0 | 42.9 | 9.1 | 75.1 | 34.3152 | 0 | 0 | 0 | 0 | 382.7 | 189.6272
7845 | 50.1328 | 0 | 42.9 | 27.7 | 75.1 | 25.0664 | 0 | 0 | 0 | 0 | 453.6 | 222.9415
7846 | 43.3885 | 0 | 42.9 | 54 | 93.9 | 21.6943 | 0 | 0 | 0 | 0 | 501.2 | 274.8488
7847 | 40.2549 | 0 | 0 | 0 | 0 | 20.1275 | 0 | 0 | 0 | 0 | 74.6 | 224.3039
7848 | 40.3414 | 0 | 0 | 0.7 | 0 | 20.1707 | 0 | 0 | 0 | 0 | 158.3 | 135.2169
7849 | 44.6865 | 0 | 0 | 16.5 | 0 | 22.3432 | 0 | 0 | 0 | 0 | 215.6 | 101.9808
7850 | 40.377 | 0 | 0 | 44.2 | 0 | 20.1885 | 0 | 0 | 0 | 1.1 | 272.2 | 96.5922
7851 | 42.7259 | 0 | 0 | 73.8 | 0 | 21.363 | 0 | 0 | 0 | 3.1 | 329.8 | 79.2407
7852 | 41.617 | 0 | 0 | 97.4 | 0 | 20.8085 | 0 | 0 | 0 | 6.5 | 375.2 | 82.9125
7853 | 42.1271 | 0 | 0 | 117.7 | 0 | 21.0636 | 0 | 0 | 0 | 11.7 | 415.8 | 77.6836
7854 | 41.0309 | 0 | 0 | 134.9 | 0 | 20.5155 | 0 | 0 | 0 | 16.1 | 447 | 102.8211
7855 | 46.4004 | 0 | 42.9 | 315.3 | 56.3 | 23.2002 | 0 | 0 | 0 | 33.9 | 997.8 | 110.5397
7856 | 57.3078 | 0 | 42.9 | 340.3 | 37.6 | 28.6539 | 0 | 0 | 0 | 35.9 | 951.8 | 127.2555
7857 | 70.1661 | 0 | 42.9 | 298.1 | 0 | 35.0831 | 0 | 0 | 0 | 37.5 | 386 | 111.3895
7858 | 68.0515 | 0 | 42.9 | 252.9 | 0 | 34.0258 | 0 | 0 | 0 | 37.7 | 392.3 | 141.2719
7859 | 68.2787 | 0 | 42.9 | 187.2 | 0 | 34.1394 | 0 | 0 | 0 | 37.6 | 332.4 | 106.0633
7860 | 64.992 | 0 | 42.9 | 117.8 | 0 | 32.496 | 0 | 0 | 0 | 38.2 | 263.2 | 106.059
7861 | 60.6339 | 0 | 42.9 | 64.9 | 75.1 | 30.3169 | 0 | 0 | 0 | 35.8 | 672.1 | 150.9084
7862 | 54.0133 | 0 | 42.9 | 28.1 | 37.6 | 27.0066 | 0 | 0 | 0 | 22.4 | 524.7 | 145.7304
7863 | 57.1571 | 0 | 42.9 | 22 | 0 | 28.5786 | 0 | 0 | 0 | 17.9 | 56 | 153.7762
7864 | 62.5563 | 0 | 42.9 | 36.6 | 0 | 31.2782 | 0 | 0 | 0 | 20.5 | 112.2 | 257.1911
7865 | 71.6783 | 0 | 42.9 | 81.2 | 0 | 35.8391 | 0 | 0 | 0 | 27.1 | 174.5 | 127.9863
7866 | 71.4864 | 0 | 42.9 | 112.2 | 37.6 | 35.7432 | 0 | 0 | 0 | 30.3 | 682 | 177.6794
7867 | 69.6566 | 0 | 42.9 | 92.8 | 75.1 | 34.8283 | 0 | 0 | 0 | 29.8 | 607 | 223.5085
7868 | 54.7184 | 0 | 42.9 | 59.3 | 75.1 | 27.3592 | 0 | 0 | 0 | 18.8 | 539.2 | 174.8704
7869 | 45.0113 | 0 | 42.9 | 83.6 | 75.1 | 22.5056 | 0 | 0 | 0 | 23.8 | 595.7 | 175.7674
7870 | 42.9274 | 0 | 42.9 | 102.5 | 93.9 | 21.4637 | 0 | 0 | 0 | 27.1 | 631.7 | 139.8261
7871 | 38.338 | 0 | 0 | 1.9 | 0 | 19.169 | 0 | 0 | 0 | 30.4 | 158.3 | 175.4675
7872 | 41.2925 | 0 | 0 | 17.1 | 0 | 20.6463 | 0 | 0 | 0 | 33.4 | 241.1 | 163.469
7873 | 44.2703 | 0 | 0 | 35.4 | 0 | 22.1351 | 0 | 0 | 0 | 35.9 | 271.6 | 94.5608
7874 | 42.6404 | 0 | 0 | 50.7 | 0 | 21.3202 | 0 | 0 | 0 | 37.3 | 292.6 | 83.7347
7875 | 39.7401 | 0 | 0 | 63 | 0 | 19.8701 | 0 | 0 | 0 | 38.1 | 309.4 | 79.4754
7876 | 43.7124 | 0 | 0 | 74 | 0 | 21.8562 | 0 | 0 | 0 | 38.7 | 326.3 | 78.2834
7877 | 43.2581 | 0 | 0 | 83.3 | 0 | 21.629 | 0 | 0 | 0 | 39.3 | 341.4 | 96.4669
7878 | 40.342 | 0 | 0 | 91.8 | 0 | 20.171 | 0 | 0 | 0 | 41.2 | 351.9 | 82.1968
7879 | 48.3724 | 0 | 42.9 | 258.1 | 56.3 | 24.1862 | 0 | 0 | 0 | 54.8 | 883.1 | 116.4756
7880 | 65.5037 | 0 | 42.9 | 247.8 | 37.6 | 32.7518 | 0 | 0 | 0 | 54 | 835.3 | 136.2818
7881 | 71.4328 | 0 | 42.9 | 227.8 | 0 | 35.7164 | 0 | 0 | 0 | 43.2 | 309.4 | 90.6199
7882 | 67.6142 | 0 | 42.9 | 170.8 | 0 | 33.8071 | 0 | 0 | 0 | 30.3 | 298.2 | 100.4315
7883 | 66.1046 | 0 | 42.9 | 166.6 | 0 | 33.0523 | 0 | 0 | 0 | 18.7 | 294.3 | 140.9586
7884 | 63.2372 | 0 | 42.9 | 171.1 | 0 | 31.6186 | 0 | 0 | 0 | 11.3 | 310 | 209.2389
7885 | 57.1237 | 0 | 42.9 | 155.2 | 75.1 | 28.5618 | 0 | 0 | 0 | 10.8 | 760.9 | 115.6011
7886 | 56.7902 | 0 | 42.9 | 114.2 | 37.6 | 28.3951 | 0 | 0 | 0 | 13.4 | 630.8 | 105.3397
7887 | 56.7846 | 0 | 42.9 | 100.5 | 0 | 28.3923 | 0 | 0 | 0 | 13.6 | 131.9 | 111.6355
7888 | 65.1445 | 0 | 42.9 | 97.3 | 0 | 32.5722 | 0 | 0 | 0 | 15.8 | 177 | 188.2613
7889 | 73.601 | 0 | 42.9 | 114.2 | 0 | 36.8005 | 0 | 0 | 0 | 21.3 | 205.7 | 197.0795
7890 | 72.1084 | 0 | 42.9 | 131.2 | 37.6 | 36.0542 | 0 | 0 | 0 | 23.8 | 696.2 | 244.5831
7891 | 67.542 | 0 | 42.9 | 129.8 | 75.1 | 33.771 | 0 | 0 | 0 | 23.3 | 625.7 | 244.9402
7892 | 50.5942 | 0 | 42.9 | 96 | 75.1 | 25.2971 | 0 | 0 | 0 | 13.3 | 545.4 | 197.117
7893 | 47.3952 | 0 | 42.9 | 110.6 | 75.1 | 23.6976 | 0 | 0 | 0 | 17.4 | 594.2 | 256.2383
7894 | 40.8004 | 0 | 42.9 | 120.4 | 93.9 | 20.4002 | 0 | 0 | 0 | 19.4 | 618 | 207.98
7895 | 41.9979 | 0 | 0 | 18.5 | 0 | 20.999 | 0 | 0 | 0 | 21.6 | 143 | 219.1055
7896 | 43.6901 | 0 | 0 | 41.5 | 0 | 21.845 | 0 | 0 | 0 | 24 | 221.3 | 172.7774
7897 | 42.6429 | 0 | 0 | 58.5 | 0 | 21.3214 | 0 | 0 | 0 | 26.3 | 256.1 | 102.8203
7898 | 42.7327 | 0 | 0 | 74.4 | 0 | 21.3664 | 0 | 0 | 0 | 28.5 | 290.1 | 77.8037
7899 | 43.2732 | 0 | 0 | 89.9 | 0 | 21.6366 | 0 | 0 | 0 | 31.1 | 324.6 | 77.6845
7900 | 40.6504 | 0 | 0 | 102.1 | 0 | 20.3252 | 0 | 0 | 0 | 32.9 | 351.8 | 81.6078
7901 | 40.2134 | 0 | 0 | 112.2 | 0 | 20.1067 | 0 | 0 | 0 | 34.5 | 375.3 | 81.1386
7902 | 44.0824 | 0 | 0 | 121.5 | 0 | 22.0412 | 0 | 0 | 0 | 36 | 393.2 | 85.6318
7903 | 56.1784 | 0 | 42.9 | 288.3 | 56.3 | 28.0892 | 0 | 0 | 0 | 49.7 | 942.2 | 104.6194
7904 | 96.199 | 0.7 | 43 | 337.1 | 37.6 | 48.0995 | 0 | 0 | 0 | 110.1 | 905.2 | 124.0246
7905 | 195.8884 | 2.1 | 43.2 | 320.2 | 0 | 97.9442 | 0 | 0 | 0 | 107.9 | 352.4 | 140.3607
7906 | 306.1185 | 3.5 | 43.4 | 300.3 | 0 | 153.0593 | 0 | 0 | 0 | 125.3 | 384.2 | 131.0929
7907 | 325.3647 | 3.5 | 43.4 | 262.8 | 0 | 162.6824 | 0 | 0 | 0 | 117.4 | 355.7 | 144.336
7908 | 309.3448 | 2.8 | 43.3 | 225 | 0 | 154.6724 | 0 | 0 | 0 | 92.2 | 326.8 | 144.6569
7909 | 258.8953 | 1.4 | 43.1 | 198.1 | 75.1 | 129.4477 | 0 | 0 | 0 | 60.9 | 787.6 | 166.2628
7910 | 276.4654 | 2.1 | 43.2 | 189.5 | 37.6 | 138.2327 | 0 | 0 | 0 | 62.6 | 713.7 | 169.6497
7911 | 334.9847 | 3.5 | 43.4 | 195.1 | 0 | 167.4923 | 0 | 0 | 0 | 84.9 | 212 | 169.3782
7912 | 389.1768 | 2.8 | 43.3 | 198.3 | 0 | 194.5884 | 0 | 0 | 0 | 85.9 | 277.4 | 105.3406
7913 | 343.0284 | 2.1 | 43.2 | 203.4 | 0 | 171.5142 | 0 | 0 | 0 | 75.8 | 305.5 | 127.2284
7914 | 230.5833 | 0.7 | 43 | 208.1 | 37.6 | 115.2916 | 0 | 0 | 0 | 49.8 | 811.4 | 141.7891
7915 | 127.9614 | 0 | 42.9 | 159.3 | 75.1 | 63.9807 | 0 | 0 | 0 | 3.2 | 750.4 | 225.6583
7916 | 85.5572 | 0 | 42.9 | 128.2 | 75.1 | 42.7786 | 0 | 0 | 0 | 1.2 | 663.1 | 151.4643
7917 | 61.6932 | 0 | 42.9 | 142.4 | 75.1 | 30.8466 | 0 | 0 | 0 | 3.3 | 708.4 | 147.2865
7918 | 41.7593 | 0 | 42.9 | 151.7 | 93.9 | 20.8796 | 0 | 0 | 0 | 5.5 | 732.2 | 140.3451
7919 | 42.4411 | 0 | 0 | 43 | 0 | 21.2205 | 0 | 0 | 0 | 10.7 | 228 | 161.2911
7920 | 40.7963 | 0 | 0 | 67.7 | 0 | 20.3982 | 0 | 0 | 0 | 15.9 | 309.7 | 140.6198
7921 | 42.0543 | 0 | 0 | 88.8 | 0 | 21.0272 | 0 | 0 | 0 | 20.6 | 352.9 | 106.5522
7922 | 41.2566 | 0 | 0 | 96.4 | 0 | 20.6283 | 0 | 0 | 0 | 25 | 364 | 93.8426
7923 | 43.5627 | 0 | 0 | 103.8 | 0 | 21.7814 | 0 | 0 | 0 | 29.2 | 376.6 | 99.9516
7924 | 41.2842 | 0 | 0 | 109.5 | 0 | 20.6421 | 0 | 0 | 0 | 32.7 | 387.2 | 79.3588
7925 | 42.7681 | 0 | 0 | 114.1 | 0 | 21.384 | 0 | 0 | 0 | 35.6 | 396 | 80.7777
7926 | 43.9241 | 0 | 0 | 121.3 | 0 | 21.962 | 0 | 0 | 0 | 38.2 | 406.7 | 87.643
7927 | 66.7697 | 0 | 42.9 | 284.3 | 56.3 | 33.3849 | 0 | 0 | 0 | 52.7 | 948 | 119.2855
7928 | 117.8483 | 0.7 | 43 | 329.3 | 37.6 | 58.9242 | 0 | 0 | 0 | 111.6 | 909.8 | 145.2073
7929 | 200.2341 | 2.1 | 43.2 | 324.8 | 0 | 100.1171 | 0 | 0 | 0 | 118.1 | 360.8 | 166.528
7930 | 305.9552 | 3.5 | 43.4 | 328.8 | 0 | 152.9776 | 0 | 0 | 0 | 140.7 | 416.2 | 115.1385
7931 | 377.7202 | 3.5 | 43.4 | 320.4 | 0 | 188.8601 | 0 | 0 | 0 | 120.9 | 419.7 | 110.4169
7932 | 393.3257 | 2.8 | 43.3 | 307.4 | 0 | 196.6629 | 0 | 0 | 0 | 79.9 | 424.8 | 106.4327
7933 | 349.6558 | 1.4 | 43.1 | 292.2 | 75.1 | 174.8279 | 0 | 0 | 0 | 37.7 | 964.9 | 203.9396
7934 | 323.3285 | 2.1 | 43.2 | 288.8 | 37.6 | 161.6643 | 0 | 0 | 0 | 30.1 | 899.8 | 209.7843
7935 | 329.4163 | 3.5 | 43.4 | 297.8 | 0 | 164.7082 | 0 | 0 | 0 | 44.6 | 348.1 | 240.1635
7936 | 397.7586 | 2.8 | 43.3 | 290.5 | 0 | 198.8793 | 0 | 0 | 0 | 50.2 | 408.2 | 129.1437
7937 | 346.2491 | 2.1 | 43.2 | 281.3 | 0 | 173.1246 | 0 | 0 | 0 | 50.7 | 425.8 | 151.7177
7938 | 241.2558 | 0.7 | 43 | 277.9 | 37.6 | 120.6279 | 0 | 0 | 0 | 32.3 | 975 | 208.8453
7939 | 156.7545 | 0 | 42.9 | 228.1 | 75.1 | 78.3772 | 0 | 0 | 0 | 0 | 957.5 | 380.593
7940 | 88.1413 | 0 | 42.9 | 187.3 | 75.1 | 44.0707 | 0 | 0 | 0 | 0 | 844.7 | 431.9315
7941 | 59.992 | 0 | 42.9 | 193 | 75.1 | 29.996 | 0 | 0 | 0 | 0 | 868.3 | 243.8131
7942 | 43.4462 | 0 | 42.9 | 194.4 | 93.9 | 21.7231 | 0 | 0 | 0 | 0 | 875 | 335.4756
7943 | 41.0548 | 0 | 0 | 85.6 | 0 | 20.5274 | 0 | 0 | 0 | 0.5 | 319.8 | 325.5908
7944 | 42.0212 | 0 | 0 | 110.1 | 0 | 21.0106 | 0 | 0 | 0 | 2.5 | 403.1 | 151.3072
7945 | 40.7192 | 0 | 0 | 123.5 | 0 | 20.3596 | 0 | 0 | 0 | 4.4 | 433.5 | 92.2926
7946 | 43.1022 | 0 | 0 | 139.6 | 0 | 21.5511 | 0 | 0 | 0 | 7.4 | 470.5 | 84.4475
7947 | 42.5942 | 0 | 0 | 155.5 | 0 | 21.2971 | 0 | 0 | 0 | 13.6 | 507.7 | 84.3302
7948 | 42.253 | 0 | 0 | 168 | 0 | 21.1265 | 0 | 0 | 0 | 19.9 | 537 | 80.3065
7949 | 42.8201 | 0 | 0 | 178.6 | 0 | 21.4101 | 0 | 0 | 0 | 25.8 | 564.2 | 84.2102
7950 | 43.3377 | 0 | 0 | 187.6 | 0 | 21.6689 | 0 | 0 | 0 | 32 | 584.2 | 83.4987
7951 | 65.3093 | 0 | 42.9 | 368.7 | 56.3 | 32.6547 | 0 | 0 | 0 | 51.1 | 1199 | 95.2756
7952 | 109.8846 | 0.7 | 43 | 428.3 | 37.6 | 54.9423 | 0 | 0 | 0 | 109.6 | 1155.4 | 227.7852
7953 | 196.0421 | 2.1 | 43.2 | 411.3 | 0 | 98.021 | 0 | 0 | 0 | 121.6 | 532.2 | 202.0794
7954 | 327.8692 | 3.5 | 43.4 | 396.1 | 0 | 163.9346 | 0 | 0 | 0 | 154.8 | 562 | 242.6337
7955 | 358.6566 | 3.5 | 43.4 | 355.6 | 0 | 179.3283 | 0 | 0 | 0 | 143.7 | 533.3 | 218.066
7956 | 322.108 | 2.8 | 43.3 | 304.4 | 0 | 161.054 | 0 | 0 | 0 | 103.2 | 495.9 | 195.9348
7957 | 304.4638 | 1.4 | 43.1 | 262.9 | 75.1 | 152.2319 | 0 | 0 | 0 | 56.5 | 1006.1 | 278.2143
7958 | 298.0178 | 2.1 | 43.2 | 251 | 37.6 | 149.0089 | 0 | 0 | 0 | 51.7 | 907 | 203.287
7959 | 290.9047 | 3.5 | 43.4 | 261.3 | 0 | 145.4524 | 0 | 0 | 0 | 77.4 | 354.2 | 216.1373
7960 | 335.139 | 2.8 | 43.3 | 268.5 | 0 | 167.5695 | 0 | 0 | 0 | 85 | 430.2 | 167.2615
7961 | 298.1513 | 2.1 | 43.2 | 272.8 | 0 | 149.0757 | 0 | 0 | 0 | 77.7 | 458.8 | 210.1664
7962 | 243.9059 | 0.7 | 43 | 278.4 | 37.6 | 121.953 | 0 | 0 | 0 | 49.8 | 1001.1 | 192.5687
7963 | 152.8231 | 0 | 42.9 | 222.5 | 75.1 | 76.4115 | 0 | 0 | 0 | 1.9 | 969.7 | 280.2258
7964 | 89.5688 | 0 | 42.9 | 192.3 | 75.1 | 44.7844 | 0 | 0 | 0 | 0 | 881.2 | 275.1563
7965 | 58.6504 | 0 | 42.9 | 209.4 | 75.1 | 29.3252 | 0 | 0 | 0 | 1.2 | 931.7 | 265.6623
7966 | 43.1142 | 0 | 42.9 | 220.7 | 93.9 | 21.5571 | 0 | 0 | 0 | 2.9 | 967 | 234.4488
7967 | 41.2194 | 0 | 0 | 110.2 | 0 | 20.6097 | 0 | 0 | 0 | 4.9 | 420.4 | 163.9834
7968 | 41.4803 | 0 | 0 | 139 | 0 | 20.7402 | 0 | 0 | 0 | 8.1 | 516.2 | 135.3061
7969 | 43.1945 | 0 | 0 | 155 | 0 | 21.5973 | 0 | 0 | 0 | 13.1 | 548.8 | 108.7324
7970 | 42.7042 | 0 | 0 | 166.8 | 0 | 21.3521 | 0 | 0 | 0 | 18.5 | 572.5 | 82.3202
7971 | 41.1298 | 0 | 0 | 175.8 | 0 | 20.5649 | 0 | 0 | 0 | 23 | 589.7 | 75.4425
7972 | 42.9391 | 0 | 0 | 183.9 | 0 | 21.4696 | 0 | 0 | 0 | 26.6 | 605.7 | 75.9102
7973 | 40.8165 | 0 | 0 | 190.4 | 0 | 20.4082 | 0 | 0 | 0 | 29.9 | 620 | 78.5251
7974 | 39.7947 | 0 | 0 | 196.6 | 0 | 19.8973 | 0 | 0 | 0 | 33.6 | 631.4 | 80.0669
7975 | 60.2303 | 0 | 42.9 | 376.9 | 56.3 | 30.1152 | 0 | 0 | 0 | 51.2 | 1242.1 | 115.3787
7976 | 99.9853 | 0.7 | 43 | 435.8 | 37.6 | 49.9927 | 0 | 0 | 0 | 109.3 | 1196.5 | 178.4387
7977 | 185.9368 | 2.1 | 43.2 | 432.3 | 0 | 92.9684 | 0 | 0 | 0 | 127 | 581.3 | 165.7372
7978 | 305.8889 | 3.5 | 43.4 | 445 | 0 | 152.9444 | 0 | 0 | 0 | 174 | 639.6 | 85.8638
7979 | 370.7113 | 3.5 | 43.4 | 431.6 | 0 | 185.3557 | 0 | 0 | 0 | 180.6 | 639.2 | 88.6006
7980 | 342.9317 | 2.8 | 43.3 | 407.5 | 0 | 171.4659 | 0 | 0 | 0 | 151.4 | 636.8 | 115.3797
7981 | 328.679 | 1.4 | 43.1 | 381.4 | 75.1 | 164.3395 | 0 | 0 | 0 | 107.4 | 1235.8 | 143.9114
7982 | 295.1671 | 2.1 | 43.2 | 372.8 | 37.6 | 147.5835 | 0 | 0 | 0 | 115 | 1140.4 | 149.203
7983 | 248.1478 | 3.5 | 43.4 | 388.6 | 0 | 124.0739 | 0 | 0 | 0 | 154.2 | 532.5 | 127.5638
7984 | 281.6759 | 2.8 | 43.3 | 382.8 | 0 | 140.8379 | 0 | 0 | 0 | 153.4 | 603 | 118.9245
7985 | 226.4588 | 2.1 | 43.2 | 369.3 | 0 | 113.2294 | 0 | 0 | 0 | 126 | 624.9 | 134.5072
7986 | 152.688 | 0.7 | 43 | 362.2 | 37.6 | 76.344 | 0 | 0 | 0 | 77.2 | 1229 | 210.5932
7987 | 98.427 | 0 | 42.9 | 286.3 | 75.1 | 49.2135 | 0 | 0 | 0 | 24.5 | 1177.8 | 267.895
7988 | 53.0686 | 0 | 42.9 | 249.3 | 75.1 | 26.5343 | 0 | 0 | 0 | 18.6 | 1077.7 | 450.6538
7989 | 42.3534 | 0 | 42.9 | 260.1 | 75.1 | 21.1767 | 0 | 0 | 0 | 23.6 | 1111.9 | 186.7446
7990 | 41.3923 | 0 | 42.9 | 268.4 | 93.9 | 20.6962 | 0 | 0 | 0 | 27.1 | 1139.9 | 219.391
7991 | 42.9968 | 0 | 0 | 152.6 | 0 | 21.4984 | 0 | 0 | 0 | 30.8 | 527.7 | 186.2294
7992 | 41.3483 | 0 | 0 | 185.3 | 0 | 20.6742 | 0 | 0 | 0 | 34 | 627.1 | 133.906
7993 | 41.9418 | 0 | 0 | 195.1 | 0 | 20.9709 | 0 | 0 | 0 | 36.7 | 647.4 | 142.8836
7994 | 38.979 | 0 | 0 | 194.7 | 0 | 19.4895 | 0 | 0 | 0 | 39.1 | 644.4 | 102.6998
7995 | 40.6135 | 0 | 0 | 197.5 | 0 | 20.3067 | 0 | 0 | 0 | 41.7 | 652.1 | 93.1251
7996 | 42.4523 | 0 | 0 | 202.1 | 0 | 21.2261 | 0 | 0 | 0 | 44.1 | 666.5 | 86.9378
7997 | 41.6257 | 0 | 0 | 206.7 | 0 | 20.8128 | 0 | 0 | 0 | 46.3 | 682.7 | 89.3071
7998 | 42.3506 | 0 | 0 | 211.3 | 0 | 21.1753 | 0 | 0 | 0 | 47.8 | 694.7 | 96.1076
7999 | 58.9352 | 0 | 42.9 | 395.7 | 56.3 | 29.4676 | 0 | 0 | 0 | 61.8 | 1335.9 | 95.1582
8000 | 103.675 | 0.7 | 43 | 458 | 37.6 | 51.8375 | 0 | 0 | 0 | 126.6 | 1278.6 | 99.3519
8001 | 140.3685 | 2.1 | 43.2 | 452 | 0 | 70.1843 | 0 | 0 | 0 | 142.2 | 634.8 | 107.1522
8002 | 235.1301 | 3.5 | 43.4 | 456.4 | 0 | 117.5651 | 0 | 0 | 0 | 185.8 | 681.2 | 157.3342
8003 | 293.9001 | 3.5 | 43.4 | 436.5 | 0 | 146.9501 | 0 | 0 | 0 | 183.9 | 671.6 | 175.2261
8004 | 289.3601 | 2.8 | 43.3 | 411.4 | 0 | 144.68 | 0 | 0 | 0 | 150.4 | 666.9 | 204.2189
8005 | 266.0753 | 1.4 | 43.1 | 389.2 | 75.1 | 133.0376 | 0 | 0 | 0 | 105.4 | 1286.4 | 202.8894
8006 | 294.1205 | 2.1 | 43.2 | 377.6 | 37.6 | 147.0602 | 0 | 0 | 0 | 110.3 | 1181.6 | 223.164
8007 | 353.3141 | 3.5 | 43.4 | 388.5 | 0 | 176.6571 | 0 | 0 | 0 | 145.5 | 549.9 | 219.1937
8008 | 373.9234 | 2.8 | 43.3 | 382.7 | 0 | 186.9617 | 0 | 0 | 0 | 147.7 | 619 | 135.1955
8009 | 302.5147 | 2.1 | 43.2 | 371.9 | 0 | 151.2574 | 0 | 0 | 0 | 122.7 | 643.8 | 135.5244
8010 | 240.3238 | 0.7 | 43 | 359.4 | 37.6 | 120.1619 | 0 | 0 | 0 | 76.7 | 1246.5 | 206.7213
8011 | 163.6313 | 0 | 42.9 | 275.3 | 75.1 | 81.8157 | 0 | 0 | 0 | 23.5 | 1166.3 | 399.5207
8012 | 99.3949 | 0 | 42.9 | 227.8 | 75.1 | 49.6975 | 0 | 0 | 0 | 18.6 | 1036.3 | 309.5054
8013 | 59.4283 | 0 | 42.9 | 231.8 | 75.1 | 29.7141 | 0 | 0 | 0 | 25 | 1049.6 | 308.157
8014 | 41.3127 | 0 | 42.9 | 230 | 93.9 | 20.6563 | 0 | 0 | 0 | 29.5 | 1043.2 | 382.6057
8015 | 41.3412 | 0 | 0 | 112 | 0 | 20.6706 | 0 | 0 | 0 | 33.1 | 425.8 | 175.9058
8016 | 41.6805 | 0 | 0 | 131.8 | 0 | 20.8403 | 0 | 0 | 0 | 36.6 | 488.5 | 131.2688
8017 | 41.6238 | 0 | 0 | 134.6 | 0 | 20.8119 | 0 | 0 | 0 | 40.8 | 491.3 | 102.6989
8018 | 40.479 | 0 | 0 | 136.8 | 0 | 20.2395 | 0 | 0 | 0 | 44.4 | 494.7 | 96.5915
8019 | 41.181 | 0 | 0 | 139.1 | 0 | 20.5905 | 0 | 0 | 0 | 47.3 | 499.7 | 81.8459
8020 | 40.7114 | 0 | 0 | 141.3 | 0 | 20.3557 | 0 | 0 | 0 | 49.6 | 505.8 | 73.9312
8021 | 42.8282 | 0 | 0 | 143.2 | 0 | 21.4141 | 0 | 0 | 0 | 52.5 | 512.3 | 85.7464
8022 | 41.8972 | 0 | 0 | 144.6 | 0 | 20.9486 | 0 | 0 | 0 | 55.3 | 513.4 | 135.9663
8023 | 44.2517 | 0 | 42.9 | 316.6 | 56.3 | 22.1258 | 0 | 0 | 0 | 70.4 | 1133.5 | 97.6738
8024 | 71.5093 | 0 | 42.9 | 340.7 | 37.6 | 35.7547 | 0 | 0 | 0 | 72.7 | 1080.1 | 118.2837
8025 | 81.2859 | 0 | 42.9 | 325.2 | 0 | 40.6429 | 0 | 0 | 0 | 69 | 452.5 | 205.5837
8026 | 79.417 | 0 | 42.9 | 311.7 | 0 | 39.7085 | 0 | 0 | 0 | 55.4 | 485.2 | 121.9377
8027 | 77.569 | 0 | 42.9 | 287.7 | 0 | 38.7845 | 0 | 0 | 0 | 40.7 | 470.4 | 163.0408
8028 | 70.8393 | 0 | 42.9 | 266.2 | 0 | 35.4196 | 0 | 0 | 0 | 27.7 | 458.4 | 138.3714
8029 | 68.5434 | 0 | 42.9 | 251.1 | 75.1 | 34.2717 | 0 | 0 | 0 | 16.4 | 1004.9 | 193.4395
8030 | 65.5533 | 0 | 42.9 | 236.6 | 37.6 | 32.7766 | 0 | 0 | 0 | 7.3 | 919.8 | 231.2199
8031 | 62.7196 | 0 | 42.9 | 234.1 | 0 | 31.3598 | 0 | 0 | 0 | 5.3 | 330.6 | 156.9559
8032 | 71.9817 | 0 | 42.9 | 230.5 | 0 | 35.9908 | 0 | 0 | 0 | 10.9 | 387 | 143.4221
8033 | 84.2465 | 0 | 42.9 | 232.3 | 0 | 42.1233 | 0 | 0 | 0 | 23.2 | 403.9 | 223.6981
8034 | 80.9976 | 0 | 42.9 | 235.6 | 37.6 | 40.4988 | 0 | 0 | 0 | 29.8 | 970.5 | 229.9517
8035 | 66.0002 | 0 | 42.9 | 201.6 | 75.1 | 33.0001 | 0 | 0 | 0 | 31.7 | 895.7 | 206.1613
8036 | 43.3228 | 0 | 42.9 | 158.1 | 75.1 | 21.6614 | 0 | 0 | 0 | 20.7 | 786.5 | 226.0771
8037 | 42.9559 | 0 | 42.9 | 168 | 75.1 | 21.4779 | 0 | 0 | 0 | 26.5 | 815.9 | 233.1092
8038 | 41.591 | 0 | 42.9 | 173.4 | 93.9 | 20.7955 | 0 | 0 | 0 | 30.8 | 823.4 | 185.6965
8039 | 41.6251 | 0 | 0 | 69.6 | 0 | 20.8125 | 0 | 0 | 0 | 35.5 | 274.2 | 199.6818
8040 | 40.1774 | 0 | 0 | 91.8 | 0 | 20.0887 | 0 | 0 | 0 | 40.1 | 346.4 | 146.4757
8041 | 43.1285 | 0 | 0 | 101.7 | 0 | 21.5643 | 0 | 0 | 0 | 44.7 | 367.6 | 102.7006
8042 | 40.845 | 0 | 0 | 111.9 | 0 | 20.4225 | 0 | 0 | 0 | 48.8 | 389.2 | 84.3291
8043 | 39.8325 | 0 | 0 | 121.9 | 0 | 19.9162 | 0 | 0 | 0 | 52.8 | 410.5 | 77.9292
8044 | 41.609 | 0 | 0 | 130.3 | 0 | 20.8045 | 0 | 0 | 0 | 56 | 429.6 | 78.4052
8045 | 40.2936 | 0 | 0 | 137.3 | 0 | 20.1468 | 0 | 0 | 0 | 59.3 | 447.2 | 80.8961
8046 | 42.7024 | 0 | 0 | 143.9 | 0 | 21.3512 | 0 | 0 | 0 | 62.4 | 460.3 | 98.2715
8047 | 42.672 | 0 | 42.9 | 317.4 | 56.3 | 21.336 | 0 | 0 | 0 | 79.2 | 1060 | 137.3977
8048 | 60.7783 | 0 | 42.9 | 318.7 | 37.6 | 30.3891 | 0 | 0 | 0 | 83.4 | 1019 | 128.8072
8049 | 73.6862 | 0 | 42.9 | 303.7 | 0 | 36.8431 | 0 | 0 | 0 | 82.2 | 431.6 | 115.257
8050 | 75.6914 | 0 | 42.9 | 296.4 | 0 | 37.8457 | 0 | 0 | 0 | 70.8 | 488 | 115.5035
8051 | 75.1643 | 0 | 42.9 | 289 | 0 | 37.5821 | 0 | 0 | 0 | 59.1 | 493 | 184.4943
8052 | 74.1933 | 0 | 42.9 | 282.8 | 0 | 37.0966 | 0 | 0 | 0 | 50.5 | 497.6 | 190.2374
8053 | 72.9809 | 0 | 42.9 | 289.5 | 75.1 | 36.4904 | 0 | 0 | 0 | 41.6 | 1069.5 | 179.0098
8054 | 69.4316 | 0 | 42.9 | 276.3 | 37.6 | 34.7158 | 0 | 0 | 0 | 33.2 | 994 | 110.7777
8055 | 72.9898 | 0 | 42.9 | 275.8 | 0 | 36.4949 | 0 | 0 | 0 | 27.8 | 416 | 102.5816
8056 | 76.2803 | 0 | 42.9 | 276.7 | 0 | 38.1401 | 0 | 0 | 0 | 29.1 | 480.6 | 138.8459
8057 | 74.9749 | 0 | 42.9 | 282 | 0 | 37.4875 | 0 | 0 | 0 | 41.7 | 502 | 146.0477
8058 | 77.1273 | 0 | 42.9 | 296.8 | 37.6 | 38.5637 | 0 | 0 | 0 | 46.8 | 1078.7 | 202.7659
8059 | 71.2909 | 0 | 42.9 | 269.4 | 75.1 | 35.6454 | 0 | 0 | 0 | 46.4 | 1003.9 | 182.1178
8060 | 55.5821 | 0 | 42.9 | 214.4 | 75.1 | 27.7911 | 0 | 0 | 0 | 35 | 882.5 | 197.1291
8061 | 48.8872 | 0 | 42.9 | 218.3 | 75.1 | 24.4436 | 0 | 0 | 0 | 39.1 | 904.1 | 250.3124
8062 | 40.4232 | 0 | 42.9 | 217.3 | 93.9 | 20.2116 | 0 | 0 | 0 | 41.4 | 904.6 | 221.7749
8063 | 41.5457 | 0 | 0 | 102.5 | 0 | 20.7729 | 0 | 0 | 0 | 44.2 | 332.8 | 169.5577
8064 | 41.8138 | 0 | 0 | 122.5 | 0 | 20.9069 | 0 | 0 | 0 | 46.9 | 400.6 | 149.3843
8065 | 43.8289 | 0 | 0 | 124.8 | 0 | 21.9145 | 0 | 0 | 0 | 48.4 | 405.7 | 93.7275
8066 | 42.5846 | 0 | 0 | 124.8 | 0 | 21.2923 | 0 | 0 | 0 | 48.8 | 404.9 | 73.932
8067 | 42.7123 | 0 | 0 | 123.8 | 0 | 21.3561 | 0 | 0 | 0 | 48.7 | 401.3 | 59.5517
8068 | 42.5973 | 0 | 0 | 122.8 | 0 | 21.2986 | 0 | 0 | 0 | 48.7 | 400 | 55.519
8069 | 41.9613 | 0 | 0 | 122.4 | 0 | 20.9807 | 0 | 0 | 0 | 48.9 | 401.9 | 45.6541
8070 | 43.6603 | 0 | 0 | 121.4 | 0 | 21.8302 | 0 | 0 | 0 | 49 | 398.1 | 47.8253
8071 | 58.778 | 0 | 42.9 | 287.3 | 56.3 | 29.389 | 0 | 0 | 0 | 64.2 | 982.5 | 56.8997
8072 | 86.0986 | 0.7 | 43 | 330.2 | 37.6 | 43.0493 | 0 | 0 | 0 | 128.9 | 929.5 | 108.4839
8073 | 152.5079 | 2.1 | 43.2 | 316.8 | 0 | 76.254 | 0 | 0 | 0 | 135.7 | 341.6 | 149.8713
8074 | 293.4975 | 3.5 | 43.4 | 309.4 | 0 | 146.7488 | 0 | 0 | 0 | 168.5 | 384.9 | 161.9516
8075 | 389.2376 | 3.5 | 43.4 | 292.5 | 0 | 194.6188 | 0 | 0 | 0 | 162.9 | 380.4 | 149.2629
8076 | 381.849 | 2.8 | 43.3 | 272.7 | 0 | 190.9245 | 0 | 0 | 0 | 135.1 | 375.7 | 184.1848
8077 | 360.5208 | 1.4 | 43.1 | 243.9 | 75.1 | 180.2604 | 0 | 0 | 0 | 93.5 | 891.6 | 103.5367
8078 | 328.8566 | 2.1 | 43.2 | 170.2 | 37.6 | 164.4283 | 0 | 0 | 0 | 71.7 | 722.7 | 198.6427
8079 | 361.8491 | 3.5 | 43.4 | 118.4 | 0 | 180.9245 | 0 | 0 | 0 | 74.9 | 131.6 | 110.9006
8080 | 408.3502 | 2.8 | 43.3 | 119.8 | 0 | 204.1751 | 0 | 0 | 0 | 69.7 | 182.4 | 170.7454
8081 | 349.9868 | 2.1 | 43.2 | 125.3 | 0 | 174.9934 | 0 | 0 | 0 | 67.2 | 194.3 | 149.3177
8082 | 257.5456 | 0.7 | 43 | 126.3 | 37.6 | 128.7728 | 0 | 0 | 0 | 46.2 | 666.8 | 135.8681
8083 | 148.1219 | 0 | 42.9 | 86.6 | 75.1 | 74.0609 | 0 | 0 | 0 | 2.2 | 594.5 | 150.3864
8084 | 84.7824 | 0 | 42.9 | 57.5 | 75.1 | 42.3912 | 0 | 0 | 0 | 0.2 | 496.8 | 241.3286
8085 | 57.6995 | 0 | 42.9 | 70.4 | 75.1 | 28.8498 | 0 | 0 | 0 | 1.4 | 532.2 | 341.0993
8086 | 43.7102 | 0 | 42.9 | 78.2 | 93.9 | 21.8551 | 0 | 0 | 0 | 2.5 | 537.6 | 195.9722
8087 | 43.4437 | 0 | 0 | 1.3 | 0 | 21.7218 | 0 | 0 | 0 | 3.5 | 70.5 | 141.1279
8088 | 41.8925 | 0 | 0 | 5.6 | 0 | 20.9463 | 0 | 0 | 0 | 4.3 | 122.6 | 239.2994
8089 | 41.5631 | 0 | 0 | 14 | 0 | 20.7815 | 0 | 0 | 0 | 6.1 | 152 | 119.0803
8090 | 40.3408 | 0 | 0 | 30.6 | 0 | 20.1704 | 0 | 0 | 0 | 9.4 | 185.5 | 88.8369
8091 | 44.6527 | 0 | 0 | 46.7 | 0 | 22.3264 | 0 | 0 | 0 | 13.2 | 218.4 | 81.7279
8092 | 42.1981 | 0 | 0 | 59.1 | 0 | 21.0991 | 0 | 0 | 0 | 16.4 | 243.4 | 78.0466
8093 | 43.8054 | 0 | 0 | 69.8 | 0 | 21.9027 | 0 | 0 | 0 | 18.9 | 265.5 | 79.001
8094 | 40.7997 | 0 | 0 | 79.4 | 0 | 20.3999 | 0 | 0 | 0 | 21.8 | 281.7 | 94.0804
8095 | 58.3048 | 0 | 42.9 | 243.4 | 56.3 | 29.1524 | 0 | 0 | 0 | 36.6 | 822.1 | 124.3784
8096 | 83.0332 | 0.7 | 43 | 288.3 | 37.6 | 41.5166 | 0 | 0 | 0 | 91.7 | 792.3 | 141.1787
8097 | 160.2017 | 2.1 | 43.2 | 277.5 | 0 | 80.1009 | 0 | 0 | 0 | 103.9 | 266.3 | 112.3586
8098 | 307.1227 | 3.5 | 43.4 | 256.4 | 0 | 153.5613 | 0 | 0 | 0 | 132.8 | 295.3 | 87.8838
8099 | 376.1133 | 3.5 | 43.4 | 225 | 0 | 188.0566 | 0 | 0 | 0 | 131.1 | 272.5 | 118.0092
8100 | 329.8384 | 2.8 | 43.3 | 193 | 0 | 164.9192 | 0 | 0 | 0 | 108.5 | 249.4 | 134.4223
8101 | 286.7589 | 1.4 | 43.1 | 171.7 | 75.1 | 143.3794 | 0 | 0 | 0 | 74 | 699.3 | 150.3896
8102 | 224.9387 | 2.1 | 43.2 | 164.5 | 37.6 | 112.4693 | 0 | 0 | 0 | 56.3 | 635 | 155.1292
8103 | 292.1137 | 3.5 | 43.4 | 170.2 | 0 | 146.0569 | 0 | 0 | 0 | 67 | 154.6 | 93.7261
8104 | 365.1212 | 2.8 | 43.3 | 174.2 | 0 | 182.5606 | 0 | 0 | 0 | 66.1 | 214.3 | 153.0111
8105 | 332.7595 | 2.1 | 43.2 | 178.2 | 0 | 166.3797 | 0 | 0 | 0 | 61.7 | 238.8 | 143.2505
8106 | 242.3262 | 0.7 | 43 | 186.7 | 37.6 | 121.1631 | 0 | 0 | 0 | 42 | 739.9 | 199.4538
8107 | 166.3357 | 0 | 42.9 | 145.5 | 75.1 | 83.1679 | 0 | 0 | 0 | 0.9 | 685.8 | 305.8605
8108 | 102.0203 | 0 | 42.9 | 120.8 | 75.1 | 51.0101 | 0 | 0 | 0 | 0 | 610.4 | 237.3497
8109 | 56.692 | 0 | 42.9 | 139.1 | 75.1 | 28.346 | 0 | 0 | 0 | 0.4 | 667.1 | 253.7394
8110 | 42.5263 | 0 | 42.9 | 153.1 | 93.9 | 21.2632 | 0 | 0 | 0 | 2.3 | 703.3 | 218.2227
8111 | 41.67 | 0 | 0 | 50.1 | 0 | 20.835 | 0 | 0 | 0 | 4.1 | 217.8 | 191.8108
8112 | 42.0366 | 0 | 0 | 78.8 | 0 | 21.0183 | 0 | 0 | 0 | 6.5 | 309.2 | 151.6713
8113 | 42.4445 | 0 | 0 | 95.6 | 0 | 21.2223 | 0 | 0 | 0 | 12.1 | 343.2 | 109.4502
8114 | 42.1863 | 0 | 0 | 110.4 | 0 | 21.0932 | 0 | 0 | 0 | 18.7 | 374.2 | 97.0744
8115 | 41.5436 | 0 | 0 | 123.3 | 0 | 20.7718 | 0 | 0 | 0 | 25 | 402.5 | 91.2194
8116 | 38.9535 | 0 | 0 | 133.9 | 0 | 19.4768 | 0 | 0 | 0 | 29.5 | 427.1 | 91.4564
8117 | 39.4259 | 0 | 0 | 143.3 | 0 | 19.7129 | 0 | 0 | 0 | 32.9 | 450.1 | 98.5158
8118 | 39.3007 | 0 | 0 | 151.4 | 0 | 19.6503 | 0 | 0 | 0 | 36.9 | 465.8 | 121.0979
8119 | 55.9996 | 0 | 42.9 | 323.2 | 56.3 | 27.9998 | 0 | 0 | 0 | 53.4 | 1020.7 | 149.081
8120 | 92.1657 | 0.7 | 43 | 378.2 | 37.6 | 46.0828 | 0 | 0 | 0 | 113.4 | 990.8 | 181.9251
8121 | 185.7279 | 2.1 | 43.2 | 368.4 | 0 | 92.8639 | 0 | 0 | 0 | 130 | 424.1 | 178.9256
8122 | 281.9306 | 3.5 | 43.4 | 336.9 | 0 | 140.9653 | 0 | 0 | 0 | 163.6 | 439.8 | 233.693
8123 | 272.1033 | 3.5 | 43.4 | 288.6 | 0 | 136.0516 | 0 | 0 | 0 | 151.2 | 398.5 | 193.8691
8124 | 257.0894 | 2.8 | 43.3 | 245.1 | 0 | 128.5447 | 0 | 0 | 0 | 111.5 | 363.9 | 150.7859
8125 | 237.4016 | 1.4 | 43.1 | 212.4 | 75.1 | 118.7008 | 0 | 0 | 0 | 68 | 829.5 | 207.2299
8126 | 226.3714 | 2.1 | 43.2 | 193.7 | 37.6 | 113.1857 | 0 | 0 | 0 | 67.1 | 736.4 | 138.6179
8127 | 232.308 | 3.5 | 43.4 | 196.9 | 0 | 116.154 | 0 | 0 | 0 | 94.9 | 224.1 | 165.5493
8128 | 323.9071 | 2.8 | 43.3 | 207.3 | 0 | 161.9536 | 0 | 0 | 0 | 100.8 | 300.1 | 136.9448
8129 | 328.2237 | 2.1 | 43.2 | 219.5 | 0 | 164.1119 | 0 | 0 | 0 | 89.1 | 339.6 | 162.6885
8130 | 292.9434 | 0.7 | 43 | 226.5 | 37.6 | 146.4717 | 0 | 0 | 0 | 56.3 | 857.1 | 257.3153
8131 | 207.5408 | 0 | 42.9 | 175.2 | 75.1 | 103.7704 | 0 | 0 | 0 | 5 | 798.5 | 209.3173
8132 | 107.4675 | 0 | 42.9 | 142.7 | 75.1 | 53.7337 | 0 | 0 | 0 | 2.9 | 710.6 | 341.811
8133 | 58.2549 | 0 | 42.9 | 157.6 | 75.1 | 29.1274 | 0 | 0 | 0 | 5.7 | 756.6 | 253.1621
8134 | 42.2759 | 0 | 42.9 | 168.5 | 93.9 | 21.138 | 0 | 0 | 0 | 10.7 | 785 | 207.0444
8135 | 40.2596 | 0 | 0 | 57.7 | 0 | 20.1298 | 0 | 0 | 0 | 16.8 | 271.6 | 280.0864
8136 | 40.3767 | 0 | 0 | 83.8 | 0 | 20.1884 | 0 | 0 | 0 | 23.1 | 356.6 | 157.8344
8137 | 41.0412 | 0 | 0 | 98.4 | 0 | 20.5206 | 0 | 0 | 0 | 28.3 | 383.2 | 112.8456
8138 | 41.5067 | 0 | 0 | 123.5 | 0 | 20.7533 | 0 | 0 | 0 | 33.7 | 439.2 | 104.8636
8139 | 43.8373 | 0 | 0 | 134 | 0 | 21.9186 | 0 | 0 | 0 | 39.1 | 460.2 | 92.6516
8140 | 41.511 | 0 | 0 | 134.1 | 0 | 20.7555 | 0 | 0 | 0 | 43.4 | 456.4 | 78.4066
8141 | 42.7541 | 0 | 0 | 137.5 | 0 | 21.3771 | 0 | 0 | 0 | 47 | 461.8 | 77.5643
8142 | 41.9111 | 0 | 0 | 143.2 | 0 | 20.9556 | 0 | 0 | 0 | 50.4 | 469 | 89.1886
8143 | 55.8415 | 0 | 42.9 | 312.1 | 56.3 | 27.9208 | 0 | 0 | 0 | 65.2 | 1025.1 | 158.8409
8144 | 88.2225 | 0.7 | 43 | 363.3 | 37.6 | 44.1113 | 0 | 0 | 0 | 129 | 995.4 | 116.8963
8145 | 170.9198 | 2.1 | 43.2 | 361.9 | 0 | 85.4599 | 0 | 0 | 0 | 146.5 | 428.9 | 160.1507
8146 | 277.8254 | 3.5 | 43.4 | 371 | 0 | 138.9127 | 0 | 0 | 0 | 180.8 | 489.3 | 101.7416
8147 | 329.967 | 3.5 | 43.4 | 363.4 | 0 | 164.9835 | 0 | 0 | 0 | 162.9 | 495.4 | 119.886
8148 | 336.9955 | 2.8 | 43.3 | 349.2 | 0 | 168.4977 | 0 | 0 | 0 | 117.4 | 502.1 | 136.7122
8149 | 292.4971 | 1.4 | 43.1 | 332.3 | 75.1 | 146.2486 | 0 | 0 | 0 | 68.9 | 1068.7 | 135.5507
8150 | 252.9473 | 2.1 | 43.2 | 328.9 | 37.6 | 126.4736 | 0 | 0 | 0 | 65.9 | 995.8 | 124.4693
8151 | 271.1704 | 3.5 | 43.4 | 341.3 | 0 | 135.5852 | 0 | 0 | 0 | 89.2 | 423.9 | 89.1899
8152 | 287.6276 | 2.8 | 43.3 | 335 | 0 | 143.8138 | 0 | 0 | 0 | 94 | 490.7 | 119.3489
8153 | 260.6851 | 2.1 | 43.2 | 321.8 | 0 | 130.3426 | 0 | 0 | 0 | 88 | 507.1 | 229.413
8154 | 189.4643 | 0.7 | 43 | 317.7 | 37.6 | 94.7322 | 0 | 0 | 0 | 56.6 | 1082.1 | 165.2523
8155 | 112.473 | 0 | 42.9 | 249.8 | 75.1 | 56.2365 | 0 | 0 | 0 | 4.4 | 1037.4 | 261.8839
8156 | 68.2012 | 0 | 42.9 | 212.6 | 75.1 | 34.1006 | 0 | 0 | 0 | 2.1 | 936.4 | 229.272
8157 | 46.4121 | 0 | 42.9 | 222.7 | 75.1 | 23.2061 | 0 | 0 | 0 | 4.3 | 971.6 | 340.1476
8158 | 42.177 | 0 | 42.9 | 229.8 | 93.9 | 21.0885 | 0 | 0 | 0 | 6.1 | 995.7 | 302.2024
8159 | 41.6734 | 0 | 0 | 124.4 | 0 | 20.8367 | 0 | 0 | 0 | 9.9 | 432 | 226.5214
8160 | 41.1872 | 0 | 0 | 150.6 | 0 | 20.5936 | 0 | 0 | 0 | 15.3 | 518.7 | 147.3947
8161 | 42.0698 | 0 | 0 | 157.6 | 0 | 21.0349 | 0 | 0 | 0 | 20 | 532.7 | 99.1134
8162 | 40.0578 | 0 | 0 | 166.4 | 0 | 20.0289 | 0 | 0 | 0 | 24.4 | 551.5 | 82.2026
8163 | 42.39 | 0 | 0 | 176.9 | 0 | 21.195 | 0 | 0 | 0 | 28.6 | 576.1 | 76.6148
8164 | 41.3372 | 0 | 0 | 185.2 | 0 | 20.6686 | 0 | 0 | 0 | 32.1 | 597.9 | 75.5573
8165 | 40.1616 | 0 | 0 | 192.1 | 0 | 20.0808 | 0 | 0 | 0 | 35.9 | 617.7 | 84.2069
8166 | 42.7083 | 0 | 0 | 199.2 | 0 | 21.3541 | 0 | 0 | 0 | 39 | 635 | 114.1629
8167 | 67.9713 | 0 | 42.9 | 379.7 | 56.3 | 33.9856 | 0 | 0 | 0 | 54 | 1262.1 | 124.6777
8168 | 113.8237 | 0.7 | 43 | 443.3 | 37.6 | 56.9118 | 0 | 0 | 0 | 114 | 1214.1 | 121.106
8169 | 191.6446 | 2.1 | 43.2 | 436.6 | 0 | 95.8223 | 0 | 0 | 0 | 130.9 | 587 | 117.6043
8170 | 296.5134 | 3.5 | 43.4 | 424.9 | 0 | 148.2567 | 0 | 0 | 0 | 178.3 | 615.4 | 124.0094
8171 | 326.6084 | 3.5 | 43.4 | 386.8 | 0 | 163.3042 | 0 | 0 | 0 | 185.1 | 584.8 | 234.3867
8172 | 309.2456 | 2.8 | 43.3 | 345.9 | 0 | 154.6228 | 0 | 0 | 0 | 150.7 | 557.8 | 194.6298
8173 | 279.4608 | 1.4 | 43.1 | 309.9 | 75.1 | 139.7304 | 0 | 0 | 0 | 98.8 | 1111.7 | 191.6735
8174 | 219.4158 | 2.1 | 43.2 | 295 | 37.6 | 109.7079 | 0 | 0 | 0 | 84.8 | 1009.7 | 240.9238
8175 | 224.9597 | 3.5 | 43.4 | 303.1 | 0 | 112.4799 | 0 | 0 | 0 | 97.4 | 418.7 | 97.9164
8176 | 306.9826 | 2.8 | 43.3 | 303.1 | 0 | 153.4913 | 0 | 0 | 0 | 93.8 | 489.4 | 141.5422
8177 | 279.0105 | 2.1 | 43.2 | 307 | 0 | 139.5053 | 0 | 0 | 0 | 84.9 | 523.7 | 154.7647
8178 | 203.4607 | 0.7 | 43 | 308.3 | 37.6 | 101.7304 | 0 | 0 | 0 | 54.6 | 1108.8 | 225.5085
8179 | 117.7904 | 0 | 42.9 | 241.9 | 75.1 | 58.8952 | 0 | 0 | 0 | 3.8 | 1054.2 | 196.0336
8180 | 71.7114 | 0 | 42.9 | 209 | 75.1 | 35.8557 | 0 | 0 | 0 | 1.4 | 953.9 | 259.2481
8181 | 56.5695 | 0 | 42.9 | 221.7 | 75.1 | 28.2848 | 0 | 0 | 0 | 3.3 | 993 | 312.7132
8182 | 43.0631 | 0 | 42.9 | 229.2 | 93.9 | 21.5316 | 0 | 0 | 0 | 4.7 | 1017.2 | 238.8621
8183 | 41.5857 | 0 | 0 | 121.6 | 0 | 20.7929 | 0 | 0 | 0 | 7 | 443.4 | 208.8759
8184 | 40.156 | 0 | 0 | 146.5 | 0 | 20.078 | 0 | 0 | 0 | 10.9 | 529.4 | 263.1486
8185 | 43.0476 | 0 | 0 | 157.2 | 0 | 21.5238 | 0 | 0 | 0 | 15.2 | 550.6 | 104.2602
8186 | 42.2471 | 0 | 0 | 165.9 | 0 | 21.1235 | 0 | 0 | 0 | 19 | 567 | 80.8966
8187 | 40.3677 | 0 | 0 | 173.4 | 0 | 20.1839 | 0 | 0 | 0 | 21.9 | 582.7 | 76.9714
8188 | 41.128 | 0 | 0 | 180.4 | 0 | 20.564 | 0 | 0 | 0 | 24.7 | 599.3 | 75.9116
8189 | 41.428 | 0 | 0 | 185.8 | 0 | 20.714 | 0 | 0 | 0 | 27 | 614.1 | 76.1494
8190 | 41.1593 | 0 | 0 | 190.1 | 0 | 20.5796 | 0 | 0 | 0 | 28.9 | 622.8 | 108.7306
8191 | 44.8256 | 0 | 42.9 | 367.7 | 56.3 | 22.4128 | 0 | 0 | 0 | 42.8 | 1245.6 | 200.6973
8192 | 55.0893 | 0 | 42.9 | 397.9 | 37.6 | 27.5447 | 0 | 0 | 0 | 43.6 | 1194.2 | 186.8816
8193 | 59.1038 | 0 | 42.9 | 384.2 | 0 | 29.5519 | 0 | 0 | 0 | 43.9 | 562.5 | 193.3784
8194 | 54.0784 | 0 | 42.9 | 358.8 | 0 | 27.0392 | 0 | 0 | 0 | 43.1 | 580.6 | 214.1536
8195 | 54.0359 | 0 | 42.9 | 309.4 | 0 | 27.018 | 0 | 0 | 0 | 42 | 534.9 | 206.3899
8196 | 51.4846 | 0 | 42.9 | 259.8 | 0 | 25.7423 | 0 | 0 | 0 | 41 | 486.9 | 133.2428
8197 | 51.5782 | 0 | 42.9 | 226.2 | 75.1 | 25.7891 | 0 | 0 | 0 | 40.6 | 997.8 | 165.0927
8198 | 50.3249 | 0 | 42.9 | 202.7 | 37.6 | 25.1625 | 0 | 0 | 0 | 41.5 | 888.9 | 121.6341
8199 | 55.1281 | 0 | 42.9 | 200.4 | 0 | 27.564 | 0 | 0 | 0 | 43.4 | 316.4 | 109.8107
8200 | 54.1788 | 0 | 42.9 | 205.3 | 0 | 27.0894 | 0 | 0 | 0 | 44.1 | 382.8 | 115.3818
8201 | 56.9297 | 0 | 42.9 | 223 | 0 | 28.4648 | 0 | 0 | 0 | 45.3 | 416.3 | 181.5986
8202 | 56.9455 | 0 | 42.9 | 236.3 | 37.6 | 28.4727 | 0 | 0 | 0 | 46.4 | 978.6 | 184.0958
8203 | 55.9633 | 0 | 42.9 | 207 | 75.1 | 27.9817 | 0 | 0 | 0 | 45.5 | 925.3 | 310.6062
8204 | 41.0688 | 0 | 42.9 | 173.5 | 75.1 | 20.5344 | 0 | 0 | 0 | 34.7 | 830.5 | 227.5847
8205 | 40.5118 | 0 | 42.9 | 189.1 | 75.1 | 20.2559 | 0 | 0 | 0 | 38.4 | 875.8 | 263.2564
8206 | 41.203 | 0 | 42.9 | 198.8 | 93.9 | 20.6015 | 0 | 0 | 0 | 40.3 | 902.3 | 205.0222
8207 | 42.6143 | 0 | 0 | 93.6 | 0 | 21.3072 | 0 | 0 | 0 | 42.3 | 357.3 | 208.7477
8208 | 41.7785 | 0 | 0 | 120.7 | 0 | 20.8892 | 0 | 0 | 0 | 43.6 | 447.6 | 134.4906
8209 | 41.8278 | 0 | 0 | 135.6 | 0 | 20.9139 | 0 | 0 | 0 | 46 | 479.3 | 121.3167
8210 | 44.102 | 0 | 0 | 150.9 | 0 | 22.051 | 0 | 0 | 0 | 49.4 | 513 | 83.0301
8211 | 42.0881 | 0 | 0 | 165.6 | 0 | 21.044 | 0 | 0 | 0 | 53.6 | 546.5 | 76.8538
8212 | 41.4689 | 0 | 0 | 177.6 | 0 | 20.7344 | 0 | 0 | 0 | 56.6 | 573.6 | 75.2058
8213 | 41.0452 | 0 | 0 | 187.2 | 0 | 20.5226 | 0 | 0 | 0 | 59.4 | 596.8 | 77.8056
8214 | 44.2817 | 0 | 0 | 196.7 | 0 | 22.1409 | 0 | 0 | 0 | 61.9 | 617.1 | 91.3376
8215 | 50.2986 | 0 | 42.9 | 380.4 | 56.3 | 25.1493 | 0 | 0 | 0 | 79.9 | 1235.5 | 116.5547
8216 | 72.4156 | 0 | 42.9 | 387.7 | 37.6 | 36.2078 | 0 | 0 | 0 | 83 | 1196.9 | 161.7394
8217 | 76.0621 | 0 | 42.9 | 366.9 | 0 | 38.0311 | 0 | 0 | 0 | 81 | 581.6 | 136.7795
8218 | 74.9963 | 0 | 42.9 | 330.9 | 0 | 37.4981 | 0 | 0 | 0 | 69.1 | 605.8 | 103.7772
8219 | 73.6537 | 0 | 42.9 | 294.4 | 0 | 36.8269 | 0 | 0 | 0 | 53.5 | 569.8 | 125.2175
8220 | 68.2335 | 0 | 42.9 | 261.2 | 0 | 34.1167 | 0 | 0 | 0 | 40.8 | 533.2 | 132.8528
8221 | 65.4116 | 0 | 42.9 | 256.4 | 75.1 | 32.7058 | 0 | 0 | 0 | 32.3 | 1078.6 | 132.1575
8222 | 64.4282 | 0 | 42.9 | 244 | 37.6 | 32.2141 | 0 | 0 | 0 | 25.7 | 992.2 | 110.5349
8223 | 66.3811 | 0 | 42.9 | 244.6 | 0 | 33.1905 | 0 | 0 | 0 | 25.3 | 421.7 | 79.5956
8224 | 77.304 | 0 | 42.9 | 252.4 | 0 | 38.652 | 0 | 0 | 0 | 31.4 | 495.6 | 156.333
8225 | 75.5817 | 0 | 42.9 | 270.4 | 0 | 37.7909 | 0 | 0 | 0 | 42.1 | 529.5 | 150.2949
8226 | 76.575 | 0 | 42.9 | 291.1 | 37.6 | 38.2875 | 0 | 0 | 0 | 46.3 | 1103.8 | 230.4314
8227 | 65.7088 | 0 | 42.9 | 273.8 | 75.1 | 32.8544 | 0 | 0 | 0 | 46 | 1059 | 269.1674
8228 | 56.1704 | 0 | 42.9 | 231.4 | 75.1 | 28.0852 | 0 | 0 | 0 | 34.9 | 960.9 | 281.2407
8229 | 47.6165 | 0 | 42.9 | 243.1 | 75.1 | 23.8082 | 0 | 0 | 0 | 39.9 | 1002 | 241.2865
8230 | 44.2873 | 0 | 42.9 | 250.1 | 93.9 | 22.1437 | 0 | 0 | 0 | 42.7 | 1029.1 | 177.7471
8231 | 43.259 | 0 | 0 | 140 | 0 | 21.6295 | 0 | 0 | 0 | 45.4 | 457.6 | 184.9638
8232 | 40.9327 | 0 | 0 | 166.1 | 0 | 20.4664 | 0 | 0 | 0 | 48.1 | 546.1 | 119.0007
8233 | 40.7529 | 0 | 0 | 174.2 | 0 | 20.3765 | 0 | 0 | 0 | 49 | 564.6 | 102.9417
8234 | 41.1717 | 0 | 0 | 178.9 | 0 | 20.5858 | 0 | 0 | 0 | 49.8 | 574 | 83.5009
8235 | 42.2037 | 0 | 0 | 182.9 | 0 | 21.1018 | 0 | 0 | 0 | 50.5 | 582.3 | 76.851
8236 | 41.5491 | 0 | 0 | 186.7 | 0 | 20.7746 | 0 | 0 | 0 | 51.5 | 592.8 | 76.6166
8237 | 40.5403 | 0 | 0 | 189.8 | 0 | 20.2702 | 0 | 0 | 0 | 52.3 | 603.6 | 78.1654
8238 | 43.7626 | 0 | 0 | 192.8 | 0 | 21.8813 | 0 | 0 | 0 | 53.2 | 611.5 | 98.3914
8239 | 54.3598 | 0 | 42.9 | 372.1 | 56.3 | 27.1799 | 0 | 0 | 0 | 68.6 | 1228.2 | 114.166
8240 | 84.1486 | 0.7 | 43 | 428.6 | 37.6 | 42.0743 | 0 | 0 | 0 | 135.1 | 1173.5 | 108.1213
8241 | 164.3414 | 2.1 | 43.2 | 421.7 | 0 | 82.1707 | 0 | 0 | 0 | 146.3 | 552.3 | 146.8348
8242 | 327.8112 | 3.5 | 43.4 | 425.5 | 0 | 163.9056 | 0 | 0 | 0 | 184.3 | 600.6 | 115.5678
8243 | 392.192 | 3.5 | 43.4 | 405.2 | 0 | 196.096 | 0 | 0 | 0 | 175.9 | 592 | 170.8439
8244 | 352.7194 | 2.8 | 43.3 | 379.4 | 0 | 176.3597 | 0 | 0 | 0 | 143.5 | 585.4 | 140.5761
8245 | 335.2184 | 1.4 | 43.1 | 353 | 75.1 | 167.6092 | 0 | 0 | 0 | 101.3 | 1169.1 | 132.9939
8246 | 311.3785 | 2.1 | 43.2 | 343.3 | 37.6 | 155.6893 | 0 | 0 | 0 | 103 | 1078.7 | 133.5691
8247 | 263.2689 | 3.5 | 43.4 | 353.6 | 0 | 131.6345 | 0 | 0 | 0 | 128.2 | 472.5 | 213.9599
8248 | 319.169 | 2.8 | 43.3 | 347.5 | 0 | 159.5845 | 0 | 0 | 0 | 127.8 | 538.7 | 267.574
8249 | 294.3786 | 2.1 | 43.2 | 336.4 | 0 | 147.1893 | 0 | 0 | 0 | 110.9 | 560.2 | 123.92
8250 | 161.5003 | 0.7 | 43 | 332.3 | 37.6 | 80.7502 | 0 | 0 | 0 | 72.2 | 1159 | 158.5768
8251 | 87.4762 | 0 | 42.9 | 260.2 | 75.1 | 43.7381 | 0 | 0 | 0 | 20.7 | 1098.5 | 245.4168
8252 | 58.54 | 0 | 42.9 | 220.2 | 75.1 | 29.27 | 0 | 0 | 0 | 15.4 | 989.8 | 271.5289
8253 | 42.35 | 0 | 42.9 | 235.2 | 75.1 | 21.175 | 0 | 0 | 0 | 21 | 1033.7 | 237.5917
8254 | 42.8868 | 0 | 42.9 | 241.1 | 93.9 | 21.4434 | 0 | 0 | 0 | 24.9 | 1050.3 | 227.5562
8255 | 42.2502 | 0 | 0 | 126.5 | 0 | 21.1251 | 0 | 0 | 0 | 28.1 | 448.9 | 205.867
8256 | 40.7697 | 0 | 0 | 152.5 | 0 | 20.3848 | 0 | 0 | 0 | 31.2 | 529.2 | 127.1862
8257 | 40.4009 | 0 | 0 | 170.6 | 0 | 20.2004 | 0 | 0 | 0 | 35.3 | 570.6 | 106.3046
8258 | 41.9945 | 0 | 0 | 178.6 | 0 | 20.9972 | 0 | 0 | 0 | 40.2 | 588.8 | 96.1083
8259 | 40.9854 | 0 | 0 | 183 | 0 | 20.4927 | 0 | 0 | 0 | 44.3 | 599.8 | 89.908
8260 | 43.2057 | 0 | 0 | 190.3 | 0 | 21.6028 | 0 | 0 | 0 | 47.3 | 620.5 | 85.5115
8261 | 42.8852 | 0 | 0 | 198.9 | 0 | 21.4426 | 0 | 0 | 0 | 50.1 | 646.2 | 90.5031
8262 | 41.4627 | 0 | 0 | 205.1 | 0 | 20.7313 | 0 | 0 | 0 | 53.2 | 661.6 | 84.9257
8263 | 61.7084 | 0 | 42.9 | 386.6 | 56.3 | 30.8542 | 0 | 0 | 0 | 70.1 | 1290.8 | 139.6028
8264 | 93.5591 | 0.7 | 43 | 447.7 | 37.6 | 46.7795 | 0 | 0 | 0 | 140.3 | 1234.2 | 151.2725
8265 | 166.4284 | 2.1 | 43.2 | 444.7 | 0 | 83.2142 | 0 | 0 | 0 | 158.5 | 604 | 109.0862
8266 | 293.707 | 3.5 | 43.4 | 459.9 | 0 | 146.8535 | 0 | 0 | 0 | 202.7 | 667 | 120.1321
8267 | 295.967 | 3.5 | 43.4 | 453.7 | 0 | 147.9835 | 0 | 0 | 0 | 194.3 | 676.5 | 87.8808
8268 | 243.9595 | 2.8 | 43.3 | 436.8 | 0 | 121.9798 | 0 | 0 | 0 | 152.1 | 685.7 | 110.4178
8269 | 226.6553 | 1.4 | 43.1 | 414.5 | 75.1 | 113.3277 | 0 | 0 | 0 | 101.7 | 1314.8 | 187.8061
8270 | 219.9384 | 2.1 | 43.2 | 410.3 | 37.6 | 109.9692 | 0 | 0 | 0 | 101 | 1221.5 | 153.4919
8271 | 241.049 | 3.5 | 43.4 | 428.4 | 0 | 120.5245 | 0 | 0 | 0 | 128.3 | 593 | 378.8985
8272 | 338.7413 | 2.8 | 43.3 | 418.7 | 0 | 169.3706 | 0 | 0 | 0 | 127.8 | 661.4 | 210.9059
8273 | 335.4332 | 2.1 | 43.2 | 398.8 | 0 | 167.7166 | 0 | 0 | 0 | 114.7 | 678.9 | 129.5907
8274 | 287.1513 | 0.7 | 43 | 388.6 | 37.6 | 143.5756 | 0 | 0 | 0 | 73.5 | 1297.7 | 146.4572
8275 | 178.5284 | 0 | 42.9 | 310.2 | 75.1 | 89.2642 | 0 | 0 | 0 | 18.2 | 1244 | 218.4408
8276 | 104.9714 | 0 | 42.9 | 267.9 | 75.1 | 52.4857 | 0 | 0 | 0 | 11.5 | 1133.6 | 245.2325
8277 | 58.734 | 0 | 42.9 | 280.5 | 75.1 | 29.367 | 0 | 0 | 0 | 19.2 | 1170.5 | 189.5095
8278 | 41.9322 | 0 | 42.9 | 286.8 | 93.9 | 20.9661 | 0 | 0 | 0 | 25.2 | 1192 | 278.6544
8279 | 39.7265 | 0 | 0 | 169.8 | 0 | 19.8632 | 0 | 0 | 0 | 30.8 | 567.3 | 198.3491
8280 | 42.2682 | 0 | 0 | 196.2 | 0 | 21.1341 | 0 | 0 | 0 | 35.4 | 647.8 | 123.2709
8281 | 44.4522 | 0 | 0 | 203.8 | 0 | 22.2261 | 0 | 0 | 0 | 38.4 | 665.9 | 127.072
8282 | 41.683 | 0 | 0 | 208.8 | 0 | 20.8415 | 0 | 0 | 0 | 40.9 | 679.9 | 88.2424
8283 | 40.7489 | 0 | 0 | 212.2 | 0 | 20.3745 | 0 | 0 | 0 | 42.9 | 692.2 | 79.9507
8284 | 42.027 | 0 | 0 | 214.9 | 0 | 21.0135 | 0 | 0 | 0 | 44.4 | 704.1 | 78.5246
8285 | 42.8477 | 0 | 0 | 217.4 | 0 | 21.4239 | 0 | 0 | 0 | 45.9 | 715.3 | 78.1659
8286 | 38.7865 | 0 | 0 | 219.8 | 0 | 19.3932 | 0 | 0 | 0 | 46.6 | 720.8 | 122.4583
8287 | 60.8719 | 0 | 42.9 | 410.4 | 56.3 | 30.4359 | 0 | 0 | 0 | 59.7 | 1368.5 | 133.5085
8288 | 105.8113 | 0.7 | 43 | 467.9 | 37.6 | 52.9056 | 0 | 0 | 0 | 122.4 | 1304.8 | 152.2831
8289 | 177.1189 | 2.1 | 43.2 | 460.5 | 0 | 88.5594 | 0 | 0 | 0 | 135.8 | 652.2 | 231.3657
8290 | 259.1587 | 3.5 | 43.4 | 471.8 | 0 | 129.5794 | 0 | 0 | 0 | 167.4 | 710.3 | 304.4873
8291 | 327.4703 | 3.5 | 43.4 | 464.5 | 0 | 163.7352 | 0 | 0 | 0 | 150.9 | 718.4 | 158.1961
8292 | 314.6814 | 2.8 | 43.3 | 441.7 | 0 | 157.3407 | 0 | 0 | 0 | 110.5 | 718.8 | 270.9127
8293 | 270.2499 | 1.4 | 43.1 | 409.1 | 75.1 | 135.125 | 0 | 0 | 0 | 68.4 | 1338.9 | 379.4001
8294 | 227.3774 | 2.1 | 43.2 | 352.8 | 37.6 | 113.6887 | 0 | 0 | 0 | 64.6 | 1159.3 | 391.8464
8295 | 229.9458 | 3.5 | 43.4 | 327 | 0 | 114.9729 | 0 | 0 | 0 | 84.7 | 485.7 | 220.1484
8296 | 248.1292 | 2.8 | 43.3 | 310.3 | 0 | 124.0646 | 0 | 0 | 0 | 88.9 | 535.6 | 129.9325
8297 | 230.2644 | 2.1 | 43.2 | 309.5 | 0 | 115.1322 | 0 | 0 | 0 | 82.2 | 560.8 | 224.9318
8298 | 167.479 | 0.7 | 43 | 309.8 | 37.6 | 83.7395 | 0 | 0 | 0 | 53.9 | 1158.2 | 168.2025
8299 | 106.5055 | 0 | 42.9 | 242.6 | 75.1 | 53.2527 | 0 | 0 | 0 | 5.1 | 1090.4 | 179.6911
8300 | 65.3444 | 0 | 42.9 | 206 | 75.1 | 32.6722 | 0 | 0 | 0 | 2.4 | 978.2 | 216.6866
8301 | 46.8848 | 0 | 42.9 | 216.5 | 75.1 | 23.4424 | 0 | 0 | 0 | 4.3 | 1007.3 | 380.2938
8302 | 44.6632 | 0 | 42.9 | 222.3 | 93.9 | 22.3316 | 0 | 0 | 0 | 6 | 1021.6 | 439.6121
8303 | 41.1335 | 0 | 0 | 111.2 | 0 | 20.5668 | 0 | 0 | 0 | 9.9 | 430.6 | 176.0402
8304 | 40.3457 | 0 | 0 | 135.6 | 0 | 20.1729 | 0 | 0 | 0 | 13.9 | 508.7 | 150.2993
8305 | 42.0301 | 0 | 0 | 146.8 | 0 | 21.0151 | 0 | 0 | 0 | 18 | 529.3 | 106.1809
8306 | 42.16 | 0 | 0 | 158.1 | 0 | 21.08 | 0 | 0 | 0 | 22.4 | 553.5 | 86.3459
8307 | 40.6184 | 0 | 0 | 168.8 | 0 | 20.3092 | 0 | 0 | 0 | 26.7 | 578.6 | 91.7
8308 | 42.6562 | 0 | 0 | 177.3 | 0 | 21.3281 | 0 | 0 | 0 | 30.4 | 600 | 85.0408
8309 | 40.4148 | 0 | 0 | 184 | 0 | 20.2074 | 0 | 0 | 0 | 32.9 | 618.5 | 100.5494
8310 | 43.0513 | 0 | 0 | 189.8 | 0 | 21.5257 | 0 | 0 | 0 | 35.6 | 631.9 | 127.606
8311 | 50.7408 | 0 | 42.9 | 373.2 | 56.3 | 25.3704 | 0 | 0 | 0 | 49.7 | 1272.6 | 126.948
8312 | 83.8892 | 0.7 | 43 | 441.8 | 37.6 | 41.9446 | 0 | 0 | 0 | 108.4 | 1235.9 | 203.7094
8313 | 143.3438 | 2.1 | 43.2 | 435.1 | 0 | 71.6719 | 0 | 0 | 0 | 123.4 | 597.9 | 180.9699
8314 | 205.5146 | 3.5 | 43.4 | 443.1 | 0 | 102.7573 | 0 | 0 | 0 | 164.1 | 648.7 | 118.0967
8315 | 263.5221 | 3.5 | 43.4 | 435.6 | 0 | 131.7611 | 0 | 0 | 0 | 168.2 | 657.7 | 100.7845
8316 | 239.3005 | 2.8 | 43.3 | 417.1 | 0 | 119.6502 | 0 | 0 | 0 | 143.6 | 663.6 | 93.3667
8317 | 213.5168 | 1.4 | 43.1 | 394 | 75.1 | 106.7584 | 0 | 0 | 0 | 104.2 | 1281.4 | 121.9029
8318 | 186.0524 | 2.1 | 43.2 | 388 | 37.6 | 93.0262 | 0 | 0 | 0 | 110 | 1187.2 | 90.8593
8319 | 167.6427 | 3.5 | 43.4 | 403.2 | 0 | 83.8213 | 0 | 0 | 0 | 143.5 | 562.2 | 113.2056
8320 | 208.0745 | 2.8 | 43.3 | 395.5 | 0 | 104.0373 | 0 | 0 | 0 | 142.7 | 631.5 | 149.8991
8321 | 208.0525 | 2.1 | 43.2 | 379.8 | 0 | 104.0263 | 0 | 0 | 0 | 119 | 651.9 | 142.1225
8322 | 135.4089 | 0.7 | 43 | 374.8 | 37.6 | 67.7044 | 0 | 0 | 0 | 74.5 | 1275 | 216.3967
8323 | 88.6983 | 0 | 42.9 | 298.1 | 75.1 | 44.3491 | 0 | 0 | 0 | 21.6 | 1220.8 | 175.4329
8324 | 55.6568 | 0 | 42.9 | 255.8 | 75.1 | 27.8284 | 0 | 0 | 0 | 15.3 | 1108.1 | 165.1778
8325 | 45.5344 | 0 | 42.9 | 267.4 | 75.1 | 22.7672 | 0 | 0 | 0 | 20 | 1142.2 | 175.0635
8326 | 41.3551 | 0 | 42.9 | 274.9 | 93.9 | 20.6776 | 0 | 0 | 0 | 24.5 | 1166 | 176.7706
8327 | 44.4227 | 0 | 0 | 161 | 0 | 22.2114 | 0 | 0 | 0 | 28 | 550.9 | 164.0526
8328 | 43.2543 | 0 | 0 | 188.7 | 0 | 21.6272 | 0 | 0 | 0 | 30.5 | 635 | 156.5722
8329 | 40.4576 | 0 | 0 | 196.9 | 0 | 20.2288 | 0 | 0 | 0 | 32.2 | 653.7 | 118.9337
8330 | 42.7293 | 0 | 0 | 203 | 0 | 21.3647 | 0 | 0 | 0 | 33.3 | 669.6 | 91.5766
8331 | 39.367 | 0 | 0 | 208.3 | 0 | 19.6835 | 0 | 0 | 0 | 34.6 | 685.6 | 78.0437
8332 | 40.4464 | 0 | 0 | 212.6 | 0 | 20.2232 | 0 | 0 | 0 | 35.8 | 701.2 | 79.833
8333 | 42.4389 | 0 | 0 | 216.5 | 0 | 21.2195 | 0 | 0 | 0 | 37.7 | 716.5 | 79.4809
8334 | 41.7298 | 0 | 0 | 220.4 | 0 | 20.8649 | 0 | 0 | 0 | 37.5 | 726.4 | 95.6296
8335 | 57.1392 | 0 | 42.9 | 410.2 | 56.3 | 28.5696 | 0 | 0 | 0 | 49 | 1377.1 | 121.4812
8336 | 89.0878 | 0.7 | 43 | 468.7 | 37.6 | 44.5439 | 0 | 0 | 0 | 108.9 | 1314.2 | 118.084
8337 | 165.4658 | 2.1 | 43.2 | 453.1 | 0 | 82.7329 | 0 | 0 | 0 | 119.3 | 651.7 | 120.1794
8338 | 302.7611 | 3.5 | 43.4 | 404.1 | 0 | 151.3806 | 0 | 0 | 0 | 151.8 | 637.5 | 217.0998
8339 | 383.4612 | 3.5 | 43.4 | 307.4 | 0 | 191.7306 | 0 | 0 | 0 | 149.2 | 546.5 | 173.8269
8340 | 393.7262 | 2.8 | 43.3 | 216.2 | 0 | 196.8631 | 0 | 0 | 0 | 125.8 | 453.8 | 133.9311
8341 | 376.6786 | 1.4 | 43.1 | 146.1 | 75.1 | 188.3393 | 0 | 0 | 0 | 91.8 | 902.9 | 178.6755
8342 | 378.6413 | 2.1 | 43.2 | 105.1 | 37.6 | 189.3207 | 0 | 0 | 0 | 93.5 | 753.7 | 163.7341
8343 | 358.726 | 3.5 | 43.4 | 92.6 | 0 | 179.363 | 0 | 0 | 0 | 117.4 | 196.9 | 113.4434
8344 | 351.7968 | 2.8 | 43.3 | 108.2 | 0 | 175.8984 | 0 | 0 | 0 | 116.2 | 264.3 | 132.2499
8345 | 322.727 | 2.1 | 43.2 | 144.8 | 0 | 161.3635 | 0 | 0 | 0 | 98.9 | 316.2 | 175.5045
8346 | 196.9926 | 0.7 | 43 | 164.2 | 37.6 | 98.4963 | 0 | 0 | 0 | 62.6 | 835.7 | 303.298
8347 | 95.4456 | 0 | 42.9 | 113.9 | 75.1 | 47.7228 | 0 | 0 | 0 | 12.5 | 765.1 | 243.8803
8348 | 63.3565 | 0 | 42.9 | 79.4 | 75.1 | 31.6783 | 0 | 0 | 0 | 5.7 | 668.1 | 239.6188
8349 | 54.6802 | 0 | 42.9 | 97.3 | 75.1 | 27.3401 | 0 | 0 | 0 | 10.1 | 706 | 280.6632
8350 | 41.7822 | 0 | 42.9 | 109.8 | 93.9 | 20.8911 | 0 | 0 | 0 | 13 | 720.8 | 225.1397
8351 | 41.3805 | 0 | 0 | 9.4 | 0 | 20.6903 | 0 | 0 | 0 | 15.2 | 209.1 | 173.7551
8352 | 41.4069 | 0 | 0 | 23.4 | 0 | 20.7034 | 0 | 0 | 0 | 17.2 | 283.6 | 119.0376
8353 | 40.2552 | 0 | 0 | 40.4 | 0 | 20.1276 | 0 | 0 | 0 | 18.9 | 306.8 | 91.8208
8354 | 41.6161 | 0 | 0 | 57 | 0 | 20.808 | 0 | 0 | 0 | 20.9 | 331.4 | 82.1989
8355 | 41.1589 | 0 | 0 | 72 | 0 | 20.5795 | 0 | 0 | 0 | 22.4 | 355.7 | 79.8365
8356 | 41.2181 | 0 | 0 | 84.1 | 0 | 20.6091 | 0 | 0 | 0 | 23.4 | 375 | 78.4037
8357 | 42.3782 | 0 | 0 | 94.1 | 0 | 21.1891 | 0 | 0 | 0 | 24.2 | 390.9 | 81.9623
8358 | 43.9368 | 0 | 0 | 103.6 | 0 | 21.9684 | 0 | 0 | 0 | 25.2 | 403.3 | 84.4469
8359 | 50.3723 | 0 | 42.9 | 270.9 | 56.3 | 25.1862 | 0 | 0 | 0 | 37.6 | 961.1 | 92.4103
8360 | 75.8188 | 0 | 42.9 | 291.6 | 37.6 | 37.9094 | 0 | 0 | 0 | 37.8 | 935 | 117.6916
8361 | 78.9664 | 0 | 42.9 | 286.5 | 0 | 39.4832 | 0 | 0 | 0 | 38.1 | 375.4 | 120.1459
8362 | 68.5167 | 0 | 42.9 | 284.7 | 0 | 34.2584 | 0 | 0 | 0 | 37.1 | 428.1 | 172.0387
8363 | 67.5476 | 0 | 42.9 | 269 | 0 | 33.7738 | 0 | 0 | 0 | 35.2 | 424 | 181.5232
8364 | 64.4682 | 0 | 42.9 | 252.8 | 0 | 32.2341 | 0 | 0 | 0 | 33.1 | 419.8 | 191.1736
8365 | 60.1008 | 0 | 42.9 | 243.3 | 75.1 | 30.0504 | 0 | 0 | 0 | 31.4 | 950.1 | 200.8697
8366 | 56.951 | 0 | 42.9 | 237.7 | 37.6 | 28.4755 | 0 | 0 | 0 | 30.2 | 886 | 171.1084
8367 | 58.4229 | 0 | 42.9 | 241.4 | 0 | 29.2114 | 0 | 0 | 0 | 30.1 | 332.7 | 186.4617
8368 | 69.2441 | 0 | 42.9 | 238.2 | 0 | 34.6221 | 0 | 0 | 0 | 31.2 | 392.8 | 190.6593
8369 | 79.4942 | 0 | 42.9 | 240.2 | 0 | 39.7471 | 0 | 0 | 0 | 32.9 | 410.1 | 223.8319
8370 | 80.3672 | 0 | 42.9 | 245.7 | 37.6 | 40.1836 | 0 | 0 | 0 | 33.7 | 960.3 | 133.2111
8371 | 75.3143 | 0 | 42.9 | 210.4 | 75.1 | 37.6571 | 0 | 0 | 0 | 32.5 | 902.8 | 147.7988
8372 | 57.2576 | 0 | 42.9 | 169.9 | 75.1 | 28.6288 | 0 | 0 | 0 | 22 | 801 | 247.3101
8373 | 43.9597 | 0 | 42.9 | 181 | 75.1 | 21.9799 | 0 | 0 | 0 | 25.7 | 838.2 | 259.5313
8374 | 42.3432 | 0 | 42.9 | 187.1 | 93.9 | 21.1716 | 0 | 0 | 0 | 26.7 | 855.8 | 188.238
8375 | 42.3506 | 0 | 0 | 81.6 | 0 | 21.1753 | 0 | 0 | 0 | 28 | 309.1 | 154.9275
8376 | 42.3078 | 0 | 0 | 104.6 | 0 | 21.1539 | 0 | 0 | 0 | 29 | 388.2 | 98.3981
8377 | 41.4168 | 0 | 0 | 112.4 | 0 | 20.7084 | 0 | 0 | 0 | 29.6 | 405 | 80.4222
8378 | 42.8229 | 0 | 0 | 117.7 | 0 | 21.4115 | 0 | 0 | 0 | 30.4 | 415 | 89.1893
8379 | 43.598 | 0 | 0 | 121.8 | 0 | 21.799 | 0 | 0 | 0 | 30.9 | 422.3 | 89.6671
8380 | 41.057 | 0 | 0 | 125.2 | 0 | 20.5285 | 0 | 0 | 0 | 31.1 | 428.1 | 87.7601
8381 | 42.7154 | 0 | 0 | 128 | 0 | 21.3577 | 0 | 0 | 0 | 31.5 | 434.3 | 80.6609
8382 | 42.8865 | 0 | 0 | 130.3 | 0 | 21.4432 | 0 | 0 | 0 | 31.9 | 436.4 | 131.152
8383 | 47.9202 | 0 | 42.9 | 296 | 56.3 | 23.9601 | 0 | 0 | 0 | 45.9 | 1019.7 | 101.5032
8384 | 59.4865 | 0 | 42.9 | 289.6 | 37.6 | 29.7433 | 0 | 0 | 0 | 46.5 | 972.8 | 118.5408
8385 | 61.007 | 0 | 42.9 | 265 | 0 | 30.5035 | 0 | 0 | 0 | 44.3 | 378.4 | 139.3736
8386 | 57.2046 | 0 | 42.9 | 208.8 | 0 | 28.6023 | 0 | 0 | 0 | 31.6 | 369.5 | 125.5003
8387 | 57.4748 | 0 | 42.9 | 150 | 0 | 28.7374 | 0 | 0 | 0 | 16.3 | 306.8 | 114.0415
8388 | 56.6994 | 0 | 42.9 | 113.2 | 0 | 28.3497 | 0 | 0 | 0 | 9.2 | 258.5 | 162.3133
8389 | 57.1305 | 0 | 42.9 | 123.9 | 75.1 | 28.5652 | 0 | 0 | 0 | 14.3 | 744.4 | 180.9616
8390 | 57.592 | 0 | 42.9 | 139.6 | 37.6 | 28.796 | 0 | 0 | 0 | 18.3 | 727.9 | 150.6113
8391 | 56.5754 | 0 | 42.9 | 142.5 | 0 | 28.2877 | 0 | 0 | 0 | 21.7 | 216.2 | 148.4178
8392 | 60.2926 | 0 | 42.9 | 138.6 | 0 | 30.1463 | 0 | 0 | 0 | 24.3 | 265.4 | 127.038
8393 | 61.3609 | 0 | 42.9 | 150.5 | 0 | 30.6805 | 0 | 0 | 0 | 26.5 | 286.5 | 134.3166
8394 | 57.035 | 0 | 42.9 | 164.8 | 37.6 | 28.5175 | 0 | 0 | 0 | 27.9 | 792.5 | 186.4385
8395 | 57.2424 | 0 | 42.9 | 160.5 | 75.1 | 28.6212 | 0 | 0 | 0 | 27.1 | 736.4 | 205.1758
8396 | 50.0794 | 0 | 42.9 | 124.4 | 75.1 | 25.0397 | 0 | 0 | 0 | 16.9 | 643.7 | 202.2043
8397 | 42.8254 | 0 | 42.9 | 137.2 | 75.1 | 21.4127 | 0 | 0 | 0 | 20.3 | 685.2 | 161.3279
8398 | 42.7795 | 0 | 42.9 | 144.4 | 93.9 | 21.3898 | 0 | 0 | 0 | 21.6 | 702.5 | 183.1007
8399 | 41.4091 | 0 | 0 | 43.5 | 0 | 20.7045 | 0 | 0 | 0 | 22.9 | 197.3 | 181.9658
8400 | 42.2167 | 0 | 0 | 65.9 | 0 | 21.1084 | 0 | 0 | 0 | 23.9 | 274.2 | 130.7684
8401 | 41.7053 | 0 | 0 | 81.2 | 0 | 20.8527 | 0 | 0 | 0 | 26.1 | 307.6 | 123.7536
8402 | 42.2418 | 0 | 0 | 99.1 | 0 | 21.1209 | 0 | 0 | 0 | 29.5 | 349.5 | 116.6226
8403 | 41.9369 | 0 | 0 | 117 | 0 | 20.9684 | 0 | 0 | 0 | 33.2 | 392.9 | 86.2226
8404 | 41.4329 | 0 | 0 | 131.4 | 0 | 20.7165 | 0 | 0 | 0 | 35.8 | 427.6 | 75.5577
8405 | 40.3302 | 0 | 0 | 142.6 | 0 | 20.1651 | 0 | 0 | 0 | 37.9 | 454.7 | 78.5275
8406 | 42.4749 | 0 | 0 | 153.7 | 0 | 21.2374 | 0 | 0 | 0 | 40.3 | 477.8 | 96.1068
8407 | 61.0402 | 0 | 42.9 | 329.5 | 56.3 | 30.5201 | 0 | 0 | 0 | 56.2 | 1050.8 | 140.2039
8408 | 112.3299 | 0.7 | 43 | 388.6 | 37.6 | 56.1649 | 0 | 0 | 0 | 121.3 | 1033 | 117.8619
8409 | 177.1244 | 2.1 | 43.2 | 386.5 | 0 | 88.5622 | 0 | 0 | 0 | 132.2 | 461.8 | 100.4292
8410 | 309.8537 | 3.5 | 43.4 | 368.8 | 0 | 154.9268 | 0 | 0 | 0 | 168.1 | 494.3 | 90.0254
8411 | 363.2112 | 3.5 | 43.4 | 324 | 0 | 181.6056 | 0 | 0 | 0 | 167.5 | 461.7 | 108.1258
8412 | 306.0596 | 2.8 | 43.3 | 275.9 | 0 | 153.0298 | 0 | 0 | 0 | 131.6 | 428.2 | 158.7748
8413 | 264.7194 | 1.4 | 43.1 | 235.7 | 75.1 | 132.3597 | 0 | 0 | 0 | 93.4 | 908.8 | 169.7775
8414 | 258.5838 | 2.1 | 43.2 | 224.8 | 37.6 | 129.2919 | 0 | 0 | 0 | 94.3 | 823.6 | 123.3267
8415 | 348.1843 | 3.5 | 43.4 | 234.2 | 0 | 174.0921 | 0 | 0 | 0 | 117 | 296.1 | 102.7014
8416 | 369.6464 | 2.8 | 43.3 | 239.9 | 0 | 184.8232 | 0 | 0 | 0 | 120.9 | 373.4 | 111.0245
8417 | 322.753 | 2.1 | 43.2 | 250.5 | 0 | 161.3765 | 0 | 0 | 0 | 106.5 | 411.6 | 132.3426
8418 | 239.9913 | 0.7 | 43 | 254.5 | 37.6 | 119.9956 | 0 | 0 | 0 | 67.5 | 937.3 | 199.0373
8419 | 164.2047 | 0 | 42.9 | 197.6 | 75.1 | 82.1023 | 0 | 0 | 0 | 15.2 | 886.4 | 252.2544
8420 | 99.1145 | 0 | 42.9 | 163.6 | 75.1 | 49.5572 | 0 | 0 | 0 | 7.7 | 794.6 | 392.7249
8421 | 55.9537 | 0 | 42.9 | 176.7 | 75.1 | 27.9769 | 0 | 0 | 0 | 12 | 835.9 | 236.0312
8422 | 41.0108 | 0 | 42.9 | 185.1 | 93.9 | 20.5054 | 0 | 0 | 0 | 14.7 | 859.8 | 183.1068
8423 | 41.4847 | 0 | 0 | 70.7 | 0 | 20.7423 | 0 | 0 | 0 | 17 | 324.6 | 167.3226
8424 | 41.4515 | 0 | 0 | 96.3 | 0 | 20.7258 | 0 | 0 | 0 | 19.4 | 409.3 | 131.5305
8425 | 40.669 | 0 | 0 | 105.2 | 0 | 20.3345 | 0 | 0 | 0 | 20.8 | 422.1 | 96.7111
8426 | 42.6069 | 0 | 0 | 109.6 | 0 | 21.3035 | 0 | 0 | 0 | 21.5 | 426.2 | 86.9366
8427 | 41.3601 | 0 | 0 | 112.7 | 0 | 20.68 | 0 | 0 | 0 | 21.7 | 428.2 | 79.002
8428 | 40.6473 | 0 | 0 | 115.4 | 0 | 20.3236 | 0 | 0 | 0 | 22.1 | 430.5 | 79.5996
8429 | 42.5263 | 0 | 0 | 117.9 | 0 | 21.2632 | 0 | 0 | 0 | 22.3 | 432.3 | 78.7649
8430 | 44.6586 | 0 | 0 | 120.3 | 0 | 22.3293 | 0 | 0 | 0 | 22.5 | 430.5 | 84.5676
8431 | 71.2276 | 0 | 42.9 | 282.6 | 56.3 | 35.6138 | 0 | 0 | 0 | 33.9 | 997.3 | 136.1326
8432 | 122.3097 | 0.7 | 43 | 324.6 | 37.6 | 61.1548 | 0 | 0 | 0 | 88 | 952.3 | 133.5394
8433 | 213.2614 | 2.1 | 43.2 | 312.1 | 0 | 106.6307 | 0 | 0 | 0 | 94.4 | 370.5 | 114.8942
8434 | 251.0918 | 3.5 | 43.4 | 274.6 | 0 | 125.5459 | 0 | 0 | 0 | 111.8 | 377.9 | 125.5074
8435 | 263.0436 | 3.5 | 43.4 | 216.7 | 0 | 131.5218 | 0 | 0 | 0 | 104.1 | 320.4 | 161.0495
8436 | 242.9721 | 2.8 | 43.3 | 170.2 | 0 | 121.4861 | 0 | 0 | 0 | 84.9 | 273.9 | 114.5366
8437 | 221.7517 | 1.4 | 43.1 | 135.4 | 75.1 | 110.8759 | 0 | 0 | 0 | 60 | 722.1 | 112.1162
8438 | 210.1947 | 2.1 | 43.2 | 118 | 37.6 | 105.0974 | 0 | 0 | 0 | 57.5 | 644 | 119.1529
8439 | 207.5306 | 3.5 | 43.4 | 109.4 | 0 | 103.7653 | 0 | 0 | 0 | 70.3 | 129.8 | 137.3249
8440 | 290.3534 | 2.8 | 43.3 | 112.8 | 0 | 145.1767 | 0 | 0 | 0 | 68.8 | 178.9 | 133.5778
8441 | 266.0124 | 2.1 | 43.2 | 127.7 | 0 | 133.0062 | 0 | 0 | 0 | 60.7 | 208.7 | 146.3015
8442 | 180.2013 | 0.7 | 43 | 136.8 | 37.6 | 90.1007 | 0 | 0 | 0 | 41.3 | 704.9 | 139.6208
8443 | 109.5499 | 0 | 42.9 | 97 | 75.1 | 54.7749 | 0 | 0 | 0 | 0.8 | 636.8 | 240.5152
8444 | 66.8165 | 0 | 42.9 | 68.2 | 75.1 | 33.4083 | 0 | 0 | 0 | 0 | 542.3 | 246.9604
8445 | 48.0107 | 0 | 42.9 | 81.2 | 75.1 | 24.0054 | 0 | 0 | 0 | 0 | 580.2 | 219.9268
8446 | 42.2979 | 0 | 42.9 | 89.5 | 93.9 | 21.149 | 0 | 0 | 0 | 0 | 589.5 | 183.6795
8447 | 41.4438 | 0 | 0 | 1.7 | 0 | 20.7219 | 0 | 0 | 0 | 0.4 | 109.8 | 184.7766
8448 | 39.3276 | 0 | 0 | 10 | 0 | 19.6638 | 0 | 0 | 0 | 0.8 | 170.3 | 169.1327
8449 | 42.4086 | 0 | 0 | 24.6 | 0 | 21.2043 | 0 | 0 | 0 | 1.3 | 198.9 | 124.5683
8450 | 42.7473 | 0 | 0 | 42.1 | 0 | 21.3737 | 0 | 0 | 0 | 2.1 | 232.3 | 97.1934
8451 | 41.6263 | 0 | 0 | 58.8 | 0 | 20.8132 | 0 | 0 | 0 | 3.9 | 266.4 | 90.2664
8452 | 42.0171 | 0 | 0 | 71.8 | 0 | 21.0086 | 0 | 0 | 0 | 7 | 292.5 | 89.9049
8453 | 41.3155 | 0 | 0 | 82.3 | 0 | 20.6577 | 0 | 0 | 0 | 10 | 313.7 | 91.0994
8454 | 41.604 | 0 | 0 | 92 | 0 | 20.802 | 0 | 0 | 0 | 12.7 | 329.8 | 93.7221
8455 | 63.1157 | 0 | 42.9 | 256.5 | 56.3 | 31.5579 | 0 | 0 | 0 | 27.1 | 877.9 | 107.7624
8456 | 119.3716 | 0.7 | 43 | 304.1 | 37.6 | 59.6858 | 0 | 0 | 0 | 78.3 | 850.2 | 111.8729
8457 | 203.7991 | 2.1 | 43.2 | 300.2 | 0 | 101.8996 | 0 | 0 | 0 | 88.9 | 318.5 | 156.2402
8458 | 357.4318 | 3.5 | 43.4 | 306.1 | 0 | 178.7159 | 0 | 0 | 0 | 111 | 377.6 | 264.2572
8459 | 421.5687 | 3.5 | 43.4 | 296.1 | 0 | 210.7843 | 0 | 0 | 0 | 105.6 | 378.5 | 158.6534
8460 | 401.173 | 2.8 | 43.3 | 269.3 | 0 | 200.5865 | 0 | 0 | 0 | 84.9 | 366.6 | 294.2268
8461 | 363.5177 | 1.4 | 43.1 | 220 | 75.1 | 181.7589 | 0 | 0 | 0 | 57.3 | 826.2 | 106.7928
8462 | 326.2436 | 2.1 | 43.2 | 180.3 | 37.6 | 163.1218 | 0 | 0 | 0 | 56.9 | 706.9 | 92.0561
8463 | 368.271 | 3.5 | 43.4 | 176.5 | 0 | 184.1355 | 0 | 0 | 0 | 75.2 | 191.1 | 128.7532
8464 | 386.1597 | 2.8 | 43.3 | 168.1 | 0 | 193.0799 | 0 | 0 | 0 | 77.3 | 243.4 | 184.3186
8465 | 335.333 | 2.1 | 43.2 | 175.7 | 0 | 167.6665 | 0 | 0 | 0 | 68.1 | 270.6 | 134.1872
8466 | 256.6462 | 0.7 | 43 | 185.6 | 37.6 | 128.3231 | 0 | 0 | 0 | 45 | 776.2 | 215.7965
8467 | 198.577 | 0 | 42.9 | 141.5 | 75.1 | 99.2885 | 0 | 0 | 0 | 1.6 | 715 | 205.1101
8468 | 111.8966 | 0 | 42.9 | 111.9 | 75.1 | 55.9483 | 0 | 0 | 0 | 0 | 634.1 | 508.7804
8469 | 58.0562 | 0 | 42.9 | 129.7 | 75.1 | 29.0281 | 0 | 0 | 0 | 0.6 | 686.7 | 268.3812
8470 | 41.4713 | 0 | 42.9 | 142.6 | 93.9 | 20.7357 | 0 | 0 | 0 | 2 | 717.3 | 200.1515
8471 | 43.3337 | 0 | 0 | 35.6 | 0 | 21.6668 | 0 | 0 | 0 | 3.4 | 220.9 | 164.2858
8472 | 40.5481 | 0 | 0 | 62.7 | 0 | 20.274 | 0 | 0 | 0 | 6.9 | 308.2 | 127.0205
8473 | 41.568 | 0 | 0 | 78.1 | 0 | 20.784 | 0 | 0 | 0 | 10.5 | 336.5 | 96.8322
8474 | 41.4357 | 0 | 0 | 90.1 | 0 | 20.7179 | 0 | 0 | 0 | 13.2 | 358.5 | 81.014
8475 | 39.2483 | 0 | 0 | 100.6 | 0 | 19.6241 | 0 | 0 | 0 | 15.6 | 379.2 | 81.6083
8476 | 43.2655 | 0 | 0 | 109.4 | 0 | 21.6327 | 0 | 0 | 0 | 17.8 | 398.2 | 80.4238
8477 | 41.9198 | 0 | 0 | 116.6 | 0 | 20.9599 | 0 | 0 | 0 | 19.6 | 413.9 | 78.2862
8478 | 41.8377 | 0 | 0 | 123.3 | 0 | 20.9188 | 0 | 0 | 0 | 21.1 | 423.5 | 89.9018
8479 | 66.0832 | 0 | 42.9 | 288.9 | 56.3 | 33.0416 | 0 | 0 | 0 | 33.5 | 976.7 | 98.3907
8480 | 122.4715 | 0.7 | 43 | 335.7 | 37.6 | 61.2357 | 0 | 0 | 0 | 85.3 | 945.3 | 143.616
8481 | 255.3842 | 2.1 | 43.2 | 329.8 | 0 | 127.6921 | 0 | 0 | 0 | 96.7 | 384.3 | 168.6864
8482 | 413.2789 | 3.5 | 43.4 | 310.1 | 0 | 206.6394 | 0 | 0 | 0 | 117 | 414.4 | 111.1426
8483 | 398.4159 | 3.5 | 43.4 | 268.6 | 0 | 199.208 | 0 | 0 | 0 | 107.6 | 378.5 | 98.2752
8484 | 314.6367 | 2.8 | 43.3 | 232.6 | 0 | 157.3184 | 0 | 0 | 0 | 84.7 | 351.2 | 173.4088
8485 | 253.3833 | 1.4 | 43.1 | 205.8 | 75.1 | 126.6917 | 0 | 0 | 0 | 56.4 | 836.7 | 149.7674
8486 | 218.8028 | 2.1 | 43.2 | 186.3 | 37.6 | 109.4014 | 0 | 0 | 0 | 55.4 | 752.1 | 121.3931
8487 | 252.28 | 3.5 | 43.4 | 185.2 | 0 | 126.14 | 0 | 0 | 0 | 72.1 | 224.2 | 109.3286
8488 | 327.0817 | 2.8 | 43.3 | 191.4 | 0 | 163.5408 | 0 | 0 | 0 | 73 | 290.8 | 114.6541
8489 | 339.3534 | 2.1 | 43.2 | 198.3 | 0 | 169.6767 | 0 | 0 | 0 | 64.2 | 318.8 | 140.3503
8490 | 259.5161 | 0.7 | 43 | 206.7 | 37.6 | 129.758 | 0 | 0 | 0 | 42.8 | 837.8 | 287.6183
8491 | 168.1798 | 0 | 42.9 | 161.8 | 75.1 | 84.0899 | 0 | 0 | 0 | 0.9 | 797.3 | 335.2945
8492 | 107.5629 | 0 | 42.9 | 135.6 | 75.1 | 53.7815 | 0 | 0 | 0 | 0 | 713.8 | 245.7699
8493 | 60.4761 | 0 | 42.9 | 153.3 | 75.1 | 30.2381 | 0 | 0 | 0 | 0 | 765.9 | 292.6482
8494 | 44.0003 | 0 | 42.9 | 166.1 | 93.9 | 22.0002 | 0 | 0 | 0 | 0.6 | 797.9 | 242.017
8495 | 41.9406 | 0 | 0 | 62.3 | 0 | 20.9703 | 0 | 0 | 0 | 1.7 | 281.6 | 252.1249
8496 | 45.1535 | 0 | 0 | 90.4 | 0 | 22.5768 | 0 | 0 | 0 | 3.1 | 373.9 | 128.9093
8497 | 44.437 | 0 | 0 | 111.9 | 0 | 22.2185 | 0 | 0 | 0 | 7.6 | 420.4 | 91.222
8498 | 43.1849 | 0 | 0 | 137 | 0 | 21.5925 | 0 | 0 | 0 | 13.7 | 478.6 | 80.305
8499 | 39.9623 | 0 | 0 | 161.7 | 0 | 19.9812 | 0 | 0 | 0 | 20.1 | 537.8 | 77.8061
8500 | 43.3365 | 0 | 0 | 181.1 | 0 | 21.6682 | 0 | 0 | 0 | 25.4 | 583.4 | 77.3251
8501 | 39.7252 | 0 | 0 | 197.2 | 0 | 19.8626 | 0 | 0 | 0 | 29.7 | 621.2 | 84.8033
8502 | 41.3248 | 0 | 0 | 213.7 | 0 | 20.6624 | 0 | 0 | 0 | 34.3 | 657.9 | 104.736
8503 | 69.5224 | 0 | 42.9 | 402.2 | 56.3 | 34.7612 | 0 | 0 | 0 | 50.3 | 1278.4 | 91.3408
8504 | 118.5388 | 0.7 | 43 | 474.6 | 37.6 | 59.2694 | 0 | 0 | 0 | 109.9 | 1254.8 | 129.8114
8505 | 201.988 | 2.1 | 43.2 | 475.1 | 0 | 100.994 | 0 | 0 | 0 | 131 | 647.8 | 148.9049
8506 | 324.2657 | 3.5 | 43.4 | 458 | 0 | 162.1329 | 0 | 0 | 0 | 180 | 674.3 | 169.0395
8507 | 405.9309 | 3.5 | 43.4 | 395.6 | 0 | 202.9655 | 0 | 0 | 0 | 187.2 | 629.3 | 150.4229
8508 | 402.762 | 2.8 | 43.3 | 327.2 | 0 | 201.381 | 0 | 0 | 0 | 156.7 | 577.8 | 184.2221
8509 | 397.2974 | 1.4 | 43.1 | 270.1 | 75.1 | 198.6487 | 0 | 0 | 0 | 111.6 | 1078 | 152.5496
8510 | 430.7101 | 2.1 | 43.2 | 243.2 | 37.6 | 215.3551 | 0 | 0 | 0 | 121.2 | 943.3 | 214.9424
8511 | 473.1581 | 3.5 | 43.4 | 253.8 | 0 | 236.579 | 0 | 0 | 0 | 163.9 | 390.4 | 223.7492
8512 | 452.428 | 2.8 | 43.3 | 267.6 | 0 | 226.214 | 0 | 0 | 0 | 165.3 | 482 | 200.798
8513 | 391.1727 | 2.1 | 43.2 | 290.2 | 0 | 195.5864 | 0 | 0 | 0 | 137.3 | 535.7 | 159.8551
8514 | 274.7981 | 0.7 | 43 | 302 | 37.6 | 137.399 | 0 | 0 | 0 | 86 | 1085.3 | 190.8444
8515 | 159.7787 | 0 | 42.9 | 232.9 | 75.1 | 79.8893 | 0 | 0 | 0 | 31.2 | 1037.6 | 286.679
8516 | 102.1892 | 0 | 42.9 | 194 | 75.1 | 51.0946 | 0 | 0 | 0 | 25.8 | 941.9 | 354.6177
8517 | 64.5181 | 0 | 42.9 | 210.8 | 75.1 | 32.2591 | 0 | 0 | 0 | 31.6 | 984.8 | 323.3847
8518 | 43.2593 | 0 | 42.9 | 222.7 | 93.9 | 21.6296 | 0 | 0 | 0 | 35.8 | 1017.9 | 203.8046
8519 | 42.5006 | 0 | 0 | 99.1 | 0 | 21.2503 | 0 | 0 | 0 | 39.6 | 461.6 | 133.9168
8520 | 40.3519 | 0 | 0 | 129.5 | 0 | 20.176 | 0 | 0 | 0 | 43.6 | 552.6 | 105.6993
8521 | 42.4585 | 0 | 0 | 140.5 | 0 | 21.2292 | 0 | 0 | 0 | 46.4 | 564.3 | 69.3242
8522 | 42.6875 | 0 | 0 | 144.9 | 0 | 21.3437 | 0 | 0 | 0 | 47.7 | 563.2 | 59.3225
8523 | 41.269 | 0 | 0 | 146.6 | 0 | 20.6345 | 0 | 0 | 0 | 47.4 | 557.5 | 48.8601
8524 | 40.2878 | 0 | 0 | 149.3 | 0 | 20.1439 | 0 | 0 | 0 | 47.9 | 556 | 50.6971
8525 | 43.5255 | 0 | 0 | 152 | 0 | 21.7628 | 0 | 0 | 0 | 47.9 | 556.3 | 49.5484
8526 | 41.6167 | 0 | 0 | 153.7 | 0 | 20.8084 | 0 | 0 | 0 | 47.9 | 552.3 | 84.3297
8527 | 57.1776 | 0 | 42.9 | 321.4 | 56.3 | 28.5888 | 0 | 0 | 0 | 60.8 | 1140.2 | 84.3274
8528 | 72.9629 | 0 | 42.9 | 339.6 | 37.6 | 36.4814 | 0 | 0 | 0 | 61.2 | 1086.3 | 94.5601
8529 | 71.8152 | 0 | 42.9 | 330.1 | 0 | 35.9076 | 0 | 0 | 0 | 59 | 481.2 | 101.4992
8530 | 66.9733 | 0 | 42.9 | 320.3 | 0 | 33.4867 | 0 | 0 | 0 | 49.1 | 519.5 | 176.2861
8531 | 63.9847 | 0 | 42.9 | 289.5 | 0 | 31.9924 | 0 | 0 | 0 | 34.8 | 493.3 | 187.4898
8532 | 65.7752 | 0 | 42.9 | 259.2 | 0 | 32.8876 | 0 | 0 | 0 | 23.4 | 468.7 | 109.2097
8533 | 61.7214 | 0 | 42.9 | 238 | 75.1 | 30.8607 | 0 | 0 | 0 | 17.3 | 998.6 | 180.7861
8534 | 60.2867 | 0 | 42.9 | 219.8 | 37.6 | 30.1434 | 0 | 0 | 0 | 12.3 | 908 | 208.81
8535 | 62.2303 | 0 | 42.9 | 215.4 | 0 | 31.1151 | 0 | 0 | 0 | 9 | 324.2 | 91.1026
8536 | 71.4347 | 0 | 42.9 | 213.6 | 0 | 35.7173 | 0 | 0 | 0 | 12.4 | 382.7 | 115.3828
8537 | 75.8495 | 0 | 42.9 | 220.6 | 0 | 37.9248 | 0 | 0 | 0 | 20 | 407 | 198.24
8538 | 71.8596 | 0 | 42.9 | 226.1 | 37.6 | 35.9298 | 0 | 0 | 0 | 23.1 | 973 | 324.2362
8539 | 68.9373 | 0 | 42.9 | 193 | 75.1 | 34.4687 | 0 | 0 | 0 | 22.5 | 899.1 | 194.7041
8540 | 60.0091 | 0 | 42.9 | 153.9 | 75.1 | 30.0045 | 0 | 0 | 0 | 11.9 | 797.3 | 172.0137
8541 | 50.575 | 0 | 42.9 | 163.3 | 75.1 | 25.2875 | 0 | 0 | 0 | 15.7 | 825.8 | 251.2923
8542 | 42.9066 | 0 | 42.9 | 166.7 | 93.9 | 21.4533 | 0 | 0 | 0 | 17.7 | 829.2 | 183.9524
8543 | 42.3137 | 0 | 0 | 63.3 | 0 | 21.1569 | 0 | 0 | 0 | 19.8 | 277.4 | 126.0348
8544 | 40.0042 | 0 | 0 | 85 | 0 | 20.0021 | 0 | 0 | 0 | 21.8 | 349.8 | 97.6761
8545 | 42.0924 | 0 | 0 | 101.5 | 0 | 21.0462 | 0 | 0 | 0 | 24.4 | 386.9 | 95.3922
8546 | 42.4008 | 0 | 0 | 123.6 | 0 | 21.2004 | 0 | 0 | 0 | 28.2 | 437.9 | 90.1415
8547 | 39.7023 | 0 | 0 | 145.5 | 0 | 19.8512 | 0 | 0 | 0 | 32.3 | 489.5 | 83.853
8548 | 43.3817 | 0 | 0 | 162.5 | 0 | 21.6909 | 0 | 0 | 0 | 35.8 | 530.9 | 81.0181
8549 | 41.2845 | 0 | 0 | 175.5 | 0 | 20.6422 | 0 | 0 | 0 | 37.6 | 563.9 | 77.5634
8550 | 43.1195 | 0 | 0 | 188.6 | 0 | 21.5598 | 0 | 0 | 0 | 39.4 | 593.9 | 81.2555
8551 | 52.3803 | 0 | 42.9 | 374 | 56.3 | 26.1902 | 0 | 0 | 0 | 54.5 | 1223.5 | 140.3243
8552 | 74.1738 | 0 | 42.9 | 386 | 37.6 | 37.0869 | 0 | 0 | 0 | 56.5 | 1190.8 | 104.6168
8553 | 79.0216 | 0 | 42.9 | 369.2 | 0 | 39.5108 | 0 | 0 | 0 | 58.4 | 581.3 | 114.4049
8554 | 78.919 | 0 | 42.9 | 342.9 | 0 | 39.4595 | 0 | 0 | 0 | 60.7 | 620.4 | 210.933
8555 | 71.1114 | 0 | 42.9 | 316.1 | 0 | 35.5557 | 0 | 0 | 0 | 63.3 | 600.9 | 120.3864
8556 | 69.2165 | 0 | 42.9 | 291.1 | 0 | 34.6083 | 0 | 0 | 0 | 65.5 | 580.6 | 152.6053
8557 | 73.1628 | 0 | 42.9 | 252.2 | 75.1 | 36.5814 | 0 | 0 | 0 | 67.3 | 1090 | 191.7135
8558 | 77.8169 | 0 | 42.9 | 231.7 | 37.6 | 38.9084 | 0 | 0 | 0 | 68.8 | 975.1 | 161.5779
8559 | 76.4997 | 0 | 42.9 | 230 | 0 | 38.2499 | 0 | 0 | 0 | 70.1 | 411.2 | 189.5149
8560 | 78.6785 | 0 | 42.9 | 239.4 | 0 | 39.3392 | 0 | 0 | 0 | 68.8 | 488.8 | 217.3756
8561 | 79.4641 | 0 | 42.9 | 262.4 | 0 | 39.7321 | 0 | 0 | 0 | 67.8 | 524.9 | 212.7387
8562 | 76.9392 | 0 | 42.9 | 289.4 | 37.6 | 38.4696 | 0 | 0 | 0 | 69.3 | 1083.9 | 279.4824
8563 | 69.6365 | 0 | 42.9 | 277.3 | 75.1 | 34.8182 | 0 | 0 | 0 | 68.7 | 1067.9 | 352.7845
8564 | 54.5956 | 0 | 42.9 | 244.2 | 75.1 | 27.2978 | 0 | 0 | 0 | 55.4 | 989 | 276.2729
8565 | 45.8211 | 0 | 42.9 | 262.8 | 75.1 | 22.9106 | 0 | 0 | 0 | 59.3 | 1050 | 255.0519
8566 | 41.3263 | 0 | 42.9 | 276.8 | 93.9 | 20.6632 | 0 | 0 | 0 | 63.9 | 1102.2 | 264.5183
8567 | 42.4647 | 0 | 0 | 170.1 | 0 | 21.2323 | 0 | 0 | 0 | 67.4 | 544.3 | 179.1905
8568 | 42.5065 | 0 | 0 | 202.9 | 0 | 21.2532 | 0 | 0 | 0 | 69 | 655.3 | 119.1805
8569 | 41.7218 | 0 | 0 | 216.2 | 0 | 20.8609 | 0 | 0 | 0 | 70.1 | 686.3 | 94.2057
8570 | 41.4261 | 0 | 0 | 227 | 0 | 20.7131 | 0 | 0 | 0 | 70.9 | 710.8 | 82.9098
8571 | 42.6447 | 0 | 0 | 235.9 | 0 | 21.3224 | 0 | 0 | 0 | 71.9 | 730.3 | 76.6134
8572 | 43.8881 | 0 | 0 | 242.5 | 0 | 21.9441 | 0 | 0 | 0 | 72.7 | 746.3 | 73.4712
8573 | 42.4079 | 0 | 0 | 248.4 | 0 | 21.204 | 0 | 0 | 0 | 73.5 | 763.8 | 75.9139
8574 | 39.706 | 0 | 0 | 254.4 | 0 | 19.853 | 0 | 0 | 0 | 74.8 | 779.7 | 91.461
8575 | 51.6681 | 0 | 42.9 | 442.8 | 56.3 | 25.8341 | 0 | 0 | 0 | 93 | 1413.7 | 138.2242
8576 | 102.6401 | 0.7 | 43 | 512.3 | 37.6 | 51.3201 | 0 | 0 | 0 | 165.9 | 1362 | 122.9015
8577 | 186.2197 | 2.1 | 43.2 | 511.5 | 0 | 93.1099 | 0 | 0 | 0 | 177.8 | 723.7 | 113.6812
8578 | 325.9576 | 3.5 | 43.4 | 530.7 | 0 | 162.9788 | 0 | 0 | 0 | 227.1 | 791.7 | 88.3596
8579 | 403.0263 | 3.5 | 43.4 | 524.2 | 0 | 201.5132 | 0 | 0 | 0 | 227.3 | 801.5 | 104.2561
8580 | 419.7683 | 2.8 | 43.3 | 503.4 | 0 | 209.8842 | 0 | 0 | 0 | 190.6 | 811.3 | 128.1033
8581 | 371.1071 | 1.4 | 43.1 | 468.9 | 75.1 | 185.5535 | 0 | 0 | 0 | 136.4 | 1456.9 | 118.2918
8582 | 350.3686 | 2.1 | 43.2 | 414.6 | 37.6 | 175.1843 | 0 | 0 | 0 | 143.9 | 1272.2 | 155.4564
8583 | 316.7442 | 3.5 | 43.4 | 399.3 | 0 | 158.3721 | 0 | 0 | 0 | 184.5 | 596.1 | 129.949
8584 | 343.3511 | 2.8 | 43.3 | 382.4 | 0 | 171.6755 | 0 | 0 | 0 | 183 | 655.8 | 106.4301
8585 | 311.8877 | 2.1 | 43.2 | 379.2 | 0 | 155.9439 | 0 | 0 | 0 | 153.4 | 686.9 | 109.8144
8586 | 227.462 | 0.7 | 43 | 379.5 | 37.6 | 113.731 | 0 | 0 | 0 | 101.8 | 1306.2 | 216.2529
8587 | 143.9333 | 0 | 42.9 | 305.6 | 75.1 | 71.9666 | 0 | 0 | 0 | 42 | 1262.7 | 148.3881
8588 | 79.5255 | 0 | 42.9 | 271.2 | 75.1 | 39.7627 | 0 | 0 | 0 | 38.2 | 1162.4 | 187.9359
8589 | 62.6214 | 0 | 42.9 | 286.1 | 75.1 | 31.3107 | 0 | 0 | 0 | 43.7 | 1206 | 330.925
8590 | 44.5349 | 0 | 42.9 | 295.2 | 93.9 | 22.2675 | 0 | 0 | 0 | 47.5 | 1239.6 | 250.807
8591 | 42.3385 | 0 | 0 | 181 | 0 | 21.1693 | 0 | 0 | 0 | 50.8 | 624.1 | 184.9431
8592 | 39.8123 | 0 | 0 | 210.9 | 0 | 19.9062 | 0 | 0 | 0 | 52.8 | 716.4 | 124.5578
8593 | 44.2334 | 0 | 0 | 225.2 | 0 | 22.1167 | 0 | 0 | 0 | 56.4 | 747.6 | 97.7929
8594 | 39.9791 | 0 | 0 | 239.9 | 0 | 19.9895 | 0 | 0 | 0 | 60.5 | 782.9 | 94.3223
8595 | 41.2454 | 0 | 0 | 254.4 | 0 | 20.6227 | 0 | 0 | 0 | 63.4 | 820.7 | 84.686
8596 | 42.6782 | 0 | 0 | 266.4 | 0 | 21.3391 | 0 | 0 | 0 | 66.7 | 854.8 | 78.1621
8597 | 41.5591 | 0 | 0 | 276.3 | 0 | 20.7795 | 0 | 0 | 0 | 69.4 | 886 | 81.0155
8598 | 43.3039 | 0 | 0 | 286.2 | 0 | 21.652 | 0 | 0 | 0 | 72.1 | 912.3 | 83.0307
8599 | 51.2832 | 0 | 42.9 | 490.6 | 56.3 | 25.6416 | 0 | 0 | 0 | 90.7 | 1591.9 | 95.6331
8600 | 66.0984 | 0.7 | 43 | 566.4 | 37.6 | 33.0492 | 0 | 0 | 0 | 164 | 1534.7 | 106.0581
8601 | 69.5643 | 2.1 | 43.2 | 561.7 | 0 | 34.7821 | 0 | 0 | 0 | 180.6 | 857.5 | 126.3853
8602 | 69.8671 | 3.5 | 43.4 | 537.9 | 0 | 34.9335 | 0 | 0 | 0 | 239.1 | 875 | 164.6907
8603 | 68.9364 | 3.5 | 43.4 | 470.2 | 0 | 34.4682 | 0 | 0 | 0 | 247 | 820.3 | 235.9104
8604 | 65.8241 | 2.8 | 43.3 | 396.3 | 0 | 32.9121 | 0 | 0 | 0 | 211 | 759.2 | 333.6253
8605 | 63.8304 | 1.4 | 43.1 | 331.3 | 75.1 | 31.9152 | 0 | 0 | 0 | 153.2 | 1315.3 | 230.1044
8606 | 62.4767 | 2.1 | 43.2 | 298.8 | 37.6 | 31.2383 | 0 | 0 | 0 | 163.4 | 1147.6 | 169.5677
8607 | 60.8505 | 3.5 | 43.4 | 304.8 | 0 | 30.4252 | 0 | 0 | 0 | 213.5 | 529.4 | 168.4733
8608 | 65.3558 | 2.8 | 43.3 | 315.3 | 0 | 32.6779 | 0 | 0 | 0 | 211.6 | 614.6 | 126.4215
8609 | 70.9887 | 2.1 | 43.2 | 336 | 0 | 35.4943 | 0 | 0 | 0 | 172.9 | 660.6 | 214.2843
8610 | 70.5455 | 0.7 | 43 | 350.3 | 37.6 | 35.2727 | 0 | 0 | 0 | 117.8 | 1247.6 | 255.2464
8611 | 67.0787 | 0 | 42.9 | 283.9 | 75.1 | 33.5393 | 0 | 0 | 0 | 55.3 | 1232 | 248.3281
8612 | 48.6253 | 0 | 42.9 | 250.9 | 75.1 | 24.3126 | 0 | 0 | 0 | 51.2 | 1144.6 | 279.8779
8613 | 44.935 | 0 | 42.9 | 274 | 75.1 | 22.4675 | 0 | 0 | 0 | 56.7 | 1201.7 | 198.2717
8614 | 41.9288 | 0 | 42.9 | 291.7 | 93.9 | 20.9644 | 0 | 0 | 0 | 60.6 | 1254.1 | 156.7645
8615 | 40.6677 | 0 | 0 | 171 | 0 | 20.3339 | 0 | 0 | 0 | 63.9 | 667.3 | 152.7709
8616 | 41.1208 | 0 | 0 | 208.4 | 0 | 20.5604 | 0 | 0 | 0 | 66.3 | 778.2 | 113.4414
8617 | 41.1676 | 0 | 0 | 225.8 | 0 | 20.5838 | 0 | 0 | 0 | 68.2 | 806.4 | 104.4968
8618 | 42.6968 | 0 | 0 | 238.2 | 0 | 21.3484 | 0 | 0 | 0 | 70.2 | 824.5 | 194.6191
8619 | 40.3488 | 0 | 0 | 249 | 0 | 20.1744 | 0 | 0 | 0 | 72.3 | 842.9 | 79.3573
8620 | 42.5204 | 0 | 0 | 257.9 | 0 | 21.2602 | 0 | 0 | 0 | 74.5 | 861 | 78.8859
8621 | 39.4252 | 0 | 0 | 266.1 | 0 | 19.7126 | 0 | 0 | 0 | 76.5 | 880.4 | 78.884
8622 | 43.9861 | 0 | 0 | 274.1 | 0 | 21.993 | 0 | 0 | 0 | 78.3 | 896.6 | 77.3269
8623 | 49.061 | 0 | 42.9 | 467.1 | 56.3 | 24.5305 | 0 | 0 | 0 | 96.8 | 1551.7 | 79.7158
8624 | 69.7261 | 0.7 | 43 | 536.3 | 37.6 | 34.863 | 0 | 0 | 0 | 173.6 | 1493 | 87.5248
8625 | 82.3703 | 2.1 | 43.2 | 533.7 | 0 | 41.1851 | 0 | 0 | 0 | 190.6 | 826 | 110.0598
8626 | 78.9841 | 3.5 | 43.4 | 514.8 | 0 | 39.492 | 0 | 0 | 0 | 235.5 | 840.3 | 161.1358
8627 | 75.229 | 3.5 | 43.4 | 452.7 | 0 | 37.6145 | 0 | 0 | 0 | 222 | 778.3 | 123.8513
8628 | 67.609 | 2.8 | 43.3 | 382.6 | 0 | 33.8045 | 0 | 0 | 0 | 172.4 | 716.2 | 266.532
8629 | 64.7282 | 1.4 | 43.1 | 316 | 75.1 | 32.3641 | 0 | 0 | 0 | 115.6 | 1253.8 | 229.4432
8630 | 61.7183 | 2.1 | 43.2 | 268.5 | 37.6 | 30.8591 | 0 | 0 | 0 | 118.8 | 1076.6 | 293.0915
8631 | 58.4802 | 3.5 | 43.4 | 254.3 | 0 | 29.2401 | 0 | 0 | 0 | 155.2 | 444.5 | 184.0274
8632 | 68.3767 | 2.8 | 43.3 | 253.7 | 0 | 34.1883 | 0 | 0 | 0 | 158.3 | 510 | 212.594
8633 | 82.9018 | 2.1 | 43.2 | 276.4 | 0 | 41.4509 | 0 | 0 | 0 | 138.3 | 554.8 | 169.467
8634 | 81.3413 | 0.7 | 43 | 289.6 | 37.6 | 40.6707 | 0 | 0 | 0 | 91.2 | 1134 | 204.013
8635 | 80.7373 | 0 | 42.9 | 228.4 | 75.1 | 40.3686 | 0 | 0 | 0 | 33.9 | 1086.8 | 319.7744
8636 | 80.7621 | 0 | 42.9 | 194.4 | 75.1 | 40.381 | 0 | 0 | 0 | 28.4 | 989.5 | 275.8432
8637 | 58.9209 | 0 | 42.9 | 213 | 75.1 | 29.4605 | 0 | 0 | 0 | 34.9 | 1033.4 | 218.5294
8638 | 43.5305 | 0 | 42.9 | 225.4 | 93.9 | 21.7652 | 0 | 0 | 0 | 39.5 | 1063.6 | 176.4814
8639 | 43.064 | 0 | 0 | 107.3 | 0 | 21.532 | 0 | 0 | 0 | 43.4 | 488.9 | 167.6108
8640 | 41.578 | 0 | 0 | 137.5 | 0 | 20.789 | 0 | 0 | 0 | 46.2 | 581.4 | 140.1726
8641 | 42.3422 | 0 | 0 | 155.5 | 0 | 21.1711 | 0 | 0 | 0 | 49.2 | 611.9 | 108.9674
8642 | 41.9833 | 0 | 0 | 173.2 | 0 | 20.9917 | 0 | 0 | 0 | 52.9 | 644.5 | 99.3534
8643 | 41.6071 | 0 | 0 | 188.9 | 0 | 20.8035 | 0 | 0 | 0 | 55.5 | 675.4 | 86.3453
8644 | 41.0709 | 0 | 0 | 201.9 | 0 | 20.5355 | 0 | 0 | 0 | 58.2 | 703 | 91.459
8645 | 39.5449 | 0 | 0 | 213.1 | 0 | 19.7724 | 0 | 0 | 0 | 60.4 | 728.8 | 101.6196
8646 | 41.6725 | 0 | 0 | 222.6 | 0 | 20.8362 | 0 | 0 | 0 | 62 | 747.6 | 102.5776
8647 | 58.9466 | 0 | 42.9 | 410.2 | 56.3 | 29.4733 | 0 | 0 | 0 | 77.3 | 1390.3 | 119.4839
8648 | 97.5184 | 0.7 | 43 | 475.2 | 37.6 | 48.7592 | 0 | 0 | 0 | 146.2 | 1341.2 | 206.5955
8649 | 160.1779 | 2.1 | 43.2 | 475.6 | 0 | 80.0889 | 0 | 0 | 0 | 162.6 | 702 | 137.6235
8650 | 221.8856 | 3.5 | 43.4 | 474 | 0 | 110.9428 | 0 | 0 | 0 | 216.1 | 740.3 | 108.7279
8651 | 296.5376 | 3.5 | 43.4 | 438.9 | 0 | 148.2688 | 0 | 0 | 0 | 219.7 | 711.5 | 107.0309
8652 | 315.4701 | 2.8 | 43.3 | 391.9 | 0 | 157.7351 | 0 | 0 | 0 | 184.6 | 679.6 | 102.7046
8653 | 319.96 | 1.4 | 43.1 | 345.8 | 75.1 | 159.98 | 0 | 0 | 0 | 130.8 | 1251.7 | 99.4712
8654 | 294.0811 | 2.1 | 43.2 | 332.8 | 37.6 | 147.0406 | 0 | 0 | 0 | 140.2 | 1136.7 | 121.1801
8655 | 242.0783 | 3.5 | 43.4 | 348.9 | 0 | 121.0391 | 0 | 0 | 0 | 182.3 | 526.8 | 103.178
8656 | 257.3612 | 2.8 | 43.3 | 347.7 | 0 | 128.6806 | 0 | 0 | 0 | 182.2 | 600.5 | 144.3964
8657 | 257.712 | 2.1 | 43.2 | 349.3 | 0 | 128.856 | 0 | 0 | 0 | 152.7 | 636.6 | 307.8707
8658 | 181.8808 | 0.7 | 43 | 352.7 | 37.6 | 90.9404 | 0 | 0 | 0 | 100.2 | 1249.7 | 196.3759
8659 | 106.2718 | 0 | 42.9 | 283.8 | 75.1 | 53.1359 | 0 | 0 | 0 | 41.4 | 1210 | 235.7658
8660 | 67.3022 | 0 | 42.9 | 252.6 | 75.1 | 33.6511 | 0 | 0 | 0 | 36.2 | 1113.3 | 233.3438
8661 | 45.845 | 0 | 42.9 | 268.1 | 75.1 | 22.9225 | 0 | 0 | 0 | 41.1 | 1159 | 153.9121
8662 | 42.112 | 0 | 42.9 | 279.4 | 93.9 | 21.056 | 0 | 0 | 0 | 44.4 | 1197.8 | 130.1147
8663 | 40.0039 | 0 | 0 | 169.2 | 0 | 20.0019 | 0 | 0 | 0 | 47.6 | 597.4 | 139.6844
8664 | 43.9616 | 0 | 0 | 198.9 | 0 | 21.9808 | 0 | 0 | 0 | 50.6 | 694.9 | 106.4319
8665 | 39.5511 | 0 | 0 | 213.1 | 0 | 19.7755 | 0 | 0 | 0 | 52.8 | 723.7 | 85.865
8666 | 43.1105 | 0 | 0 | 226.2 | 0 | 21.5553 | 0 | 0 | 0 | 54 | 752.9 | 84.0896
8667 | 41.7134 | 0 | 0 | 238 | 0 | 20.8567 | 0 | 0 | 0 | 56.3 | 781.9 | 83.8524
8668 | 41.1853 | 0 | 0 | 247.7 | 0 | 20.5926 | 0 | 0 | 0 | 57.9 | 807.7 | 78.7659
8669 | 41.6378 | 0 | 0 | 256 | 0 | 20.8189 | 0 | 0 | 0 | 59.3 | 832.3 | 82.5548
8670 | 42.8059 | 0 | 0 | 262.5 | 0 | 21.4029 | 0 | 0 | 0 | 61.1 | 850.2 | 118.8555
8671 | 59.2606 | 0 | 42.9 | 455.7 | 56.3 | 29.6303 | 0 | 0 | 0 | 77.5 | 1512.2 | 124.5217
8672 | 118.6606 | 0.7 | 43 | 527.8 | 37.6 | 59.3303 | 0 | 0 | 0 | 147.1 | 1456.6 | 105.822
8673 | 236.1371 | 2.1 | 43.2 | 520.1 | 0 | 118.0685 | 0 | 0 | 0 | 162 | 786.6 | 103.7739
8674 | 336.8086 | 3.5 | 43.4 | 484.8 | 0 | 168.4043 | 0 | 0 | 0 | 209.6 | 785 | 105.5766
8675 | 312.471 | 3.5 | 43.4 | 399.8 | 0 | 156.2355 | 0 | 0 | 0 | 208.5 | 706 | 141.5819
8676 | 276.9619 | 2.8 | 43.3 | 313.2 | 0 | 138.481 | 0 | 0 | 0 | 172.8 | 623.5 | 209.5097
8677 | 252.0928 | 1.4 | 43.1 | 242.4 | 75.1 | 126.0464 | 0 | 0 | 0 | 120.9 | 1123.7 | 141.9468
8678 | 236.4455 | 2.1 | 43.2 | 200.8 | 37.6 | 118.2227 | 0 | 0 | 0 | 124.9 | 957.1 | 160.4723
8679 | 241.7811 | 3.5 | 43.4 | 196.7 | 0 | 120.8905 | 0 | 0 | 0 | 159.2 | 363.3 | 203.6188
8680 | 324.8694 | 2.8 | 43.3 | 211.9 | 0 | 162.4347 | 0 | 0 | 0 | 158.8 | 444 | 135.3499
8681 | 364.9737 | 2.1 | 43.2 | 241.8 | 0 | 182.4869 | 0 | 0 | 0 | 134.6 | 495.3 | 139.8341
8682 | 260.8023 | 0.7 | 43 | 258.6 | 37.6 | 130.4011 | 0 | 0 | 0 | 86 | 1045 | 169.1977
8683 | 138.271 | 0 | 42.9 | 199 | 75.1 | 69.1355 | 0 | 0 | 0 | 29 | 1002.9 | 137.1537
8684 | 97.8884 | 0 | 42.9 | 164.6 | 75.1 | 48.9442 | 0 | 0 | 0 | 22.7 | 908.1 | 208.7184
8685 | 66.8512 | 0 | 42.9 | 184.1 | 75.1 | 33.4256 | 0 | 0 | 0 | 27.6 | 951.8 | 267.7494
8686 | 43.2125 | 0 | 42.9 | 198.6 | 93.9 | 21.6062 | 0 | 0 | 0 | 30.4 | 982.1 | 192.191
8687 | 40.32 | 0 | 0 | 80 | 0 | 20.16 | 0 | 0 | 0 | 32.5 | 429.6 | 147.4895
8688 | 41.9012 | 0 | 0 | 112.2 | 0 | 20.9506 | 0 | 0 | 0 | 34.3 | 522.7 | 116.9263
8689 | 42.9714 | 0 | 0 | 130.8 | 0 | 21.4857 | 0 | 0 | 0 | 36 | 551 | 108.2463
8690 | 41.1112 | 0 | 0 | 146.8 | 0 | 20.5556 | 0 | 0 | 0 | 37.8 | 576.4 | 79.2382
8691 | 42.3314 | 0 | 0 | 161.5 | 0 | 21.1657 | 0 | 0 | 0 | 39.4 | 601.8 | 76.4985
8692 | 42.9928 | 0 | 0 | 173.8 | 0 | 21.4964 | 0 | 0 | 0 | 40.5 | 623.4 | 77.5639
8693 | 41.9071 | 0 | 0 | 183 | 0 | 20.9536 | 0 | 0 | 0 | 40.9 | 640.9 | 114.2854
8694 | 39.6651 | 0 | 0 | 191.9 | 0 | 19.8326 | 0 | 0 | 0 | 42.3 | 655.9 | 124.474
8695 | 44.1602 | 0 | 42.9 | 373.3 | 56.3 | 22.0801 | 0 | 0 | 0 | 56.3 | 1274.1 | 119.4977
8696 | 56.3396 | 0 | 42.9 | 405.3 | 37.6 | 28.1698 | 0 | 0 | 0 | 56.8 | 1231.1 | 112.8436
8697 | 59.1658 | 0 | 42.9 | 394.5 | 0 | 29.5829 | 0 | 0 | 0 | 57.3 | 605 | 133.2999
8698 | 55.6658 | 0 | 42.9 | 357.5 | 0 | 27.8329 | 0 | 0 | 0 | 56.1 | 610.4 | 138.9632
8699 | 55.4984 | 0 | 42.9 | 279.9 | 0 | 27.7492 | 0 | 0 | 0 | 53.8 | 539.9 | 126.3514
8700 | 54.3939 | 0 | 42.9 | 204.4 | 0 | 27.1969 | 0 | 0 | 0 | 51.7 | 462.1 | 258.4645
8701 | 55.217 | 0 | 42.9 | 149.6 | 75.1 | 27.6085 | 0 | 0 | 0 | 49.9 | 912.6 | 123.6663
8702 | 53.487 | 0 | 42.9 | 109.5 | 37.6 | 26.7435 | 0 | 0 | 0 | 49.6 | 771.3 | 136.0825
8703 | 53.1489 | 0 | 42.9 | 102.5 | 0 | 26.5745 | 0 | 0 | 0 | 50 | 227.4 | 120.0778
8704 | 56.3213 | 0 | 42.9 | 119.8 | 0 | 28.1606 | 0 | 0 | 0 | 51 | 302.6 | 127.3069
8705 | 57.8086 | 0 | 42.9 | 157.5 | 0 | 28.9043 | 0 | 0 | 0 | 52.8 | 354.9 | 130.9998
8706 | 59.2727 | 0 | 42.9 | 179.2 | 37.6 | 29.6363 | 0 | 0 | 0 | 54 | 877.4 | 200.2906
8707 | 56.651 | 0 | 42.9 | 150.3 | 75.1 | 28.3255 | 0 | 0 | 0 | 52.2 | 806.6 | 226.0513
8708 | 43.9681 | 0 | 42.9 | 111.6 | 75.1 | 21.984 | 0 | 0 | 0 | 38.7 | 713.7 | 208.6403
8709 | 40.8419 | 0 | 42.9 | 129 | 75.1 | 20.4209 | 0 | 0 | 0 | 41.9 | 755.4 | 261.6088
8710 | 41.701 | 0 | 42.9 | 140.2 | 93.9 | 20.8505 | 0 | 0 | 0 | 42.7 | 774.6 | 228.3911
8711 | 40.4985 | 0 | 0 | 25.8 | 0 | 20.2493 | 0 | 0 | 0 | 43.6 | 258.2 | 158.5792
8712 | 40.708 | 0 | 0 | 51.5 | 0 | 20.354 | 0 | 0 | 0 | 44.2 | 339 | 128.3815
8713 | 40.6705 | 0 | 0 | 67.7 | 0 | 20.3353 | 0 | 0 | 0 | 45.3 | 360.5 | 102.4595
8714 | 39.5746 | 0 | 0 | 81.1 | 0 | 19.7873 | 0 | 0 | 0 | 46.5 | 379.4 | 91.1007
8715 | 43.5661 | 0 | 0 | 92.8 | 0 | 21.7831 | 0 | 0 | 0 | 47.5 | 397.4 | 89.3065
8716 | 42.5459 | 0 | 0 | 102.3 | 0 | 21.2729 | 0 | 0 | 0 | 48.3 | 412.2 | 82.6724
8717 | 43.6362 | 0 | 0 | 110.7 | 0 | 21.8181 | 0 | 0 | 0 | 49.8 | 426.4 | 78.4032
8718 | 41.9173 | 0 | 0 | 117.8 | 0 | 20.9587 | 0 | 0 | 0 | 50.6 | 433.8 | 93.7228
8719 | 43.3216 | 0 | 42.9 | 284.1 | 56.3 | 21.6608 | 0 | 0 | 0 | 66.5 | 989.9 | 89.0683
8720 | 59.1707 | 0 | 42.9 | 279.2 | 37.6 | 29.5854 | 0 | 0 | 0 | 67.2 | 956.1 | 94.3257
8721 | 66.8205 | 0 | 42.9 | 265.9 | 0 | 33.4103 | 0 | 0 | 0 | 65.8 | 395 | 139.7965
8722 | 65.3041 | 0 | 42.9 | 250.7 | 0 | 32.652 | 0 | 0 | 0 | 59.4 | 434.9 | 130.9028
8723 | 66.1756 | 0 | 42.9 | 227.8 | 0 | 33.0878 | 0 | 0 | 0 | 52.2 | 410.9 | 163.5254
8724 | 70.614 | 0 | 42.9 | 205.6 | 0 | 35.307 | 0 | 0 | 0 | 43.6 | 386.9 | 215.5053
8725 | 66.5208 | 0 | 42.9 | 194.9 | 75.1 | 33.2604 | 0 | 0 | 0 | 33.5 | 887.3 | 138.8305
8726 | 65.7941 | 0 | 42.9 | 179.9 | 37.6 | 32.897 | 0 | 0 | 0 | 29.4 | 811.4 | 155.2651
8727 | 63.0612 | 0 | 42.9 | 177.2 | 0 | 31.5306 | 0 | 0 | 0 | 28.3 | 271.9 | 172.5197
8728 | 64.8327 | 0 | 42.9 | 182.2 | 0 | 32.4163 | 0 | 0 | 0 | 29.9 | 334.7 | 140.6594
8729 | 66.4266 | 0 | 42.9 | 193.6 | 0 | 33.2133 | 0 | 0 | 0 | 34.8 | 358.1 | 144.0239
8730 | 66.4474 | 0 | 42.9 | 207.1 | 37.6 | 33.2237 | 0 | 0 | 0 | 37.1 | 893.8 | 152.1383
8731 | 67.6173 | 0 | 42.9 | 200.1 | 75.1 | 33.8087 | 0 | 0 | 0 | 36.8 | 839.9 | 161.5827
8732 | 47.8948 | 0 | 42.9 | 159 | 75.1 | 23.9474 | 0 | 0 | 0 | 26.2 | 746.2 | 242.7913
8733 | 43.63 | 0 | 42.9 | 171.3 | 75.1 | 21.815 | 0 | 0 | 0 | 30.4 | 787.2 | 179.0999
8734 | 42.0453 | 0 | 42.9 | 178.4 | 93.9 | 21.0227 | 0 | 0 | 0 | 32.3 | 806.7 | 170.6719
8735 | 39.9087 | 0 | 0 | 76.9 | 0 | 19.9544 | 0 | 0 | 0 | 33.9 | 277.7 | 119.0837
8736 | 43.6653 | 0 | 0 | 101.8 | 0 | 21.8326 | 0 | 0 | 0 | 35.2 | 360.1 | 97.6731
8737 | 42.5483 | 0 | 0 | 113.8 | 0 | 21.2742 | 0 | 0 | 0 | 36.9 | 389.6 | 77.5662
8738 | 41.0843 | 0 | 0 | 124.4 | 0 | 20.5421 | 0 | 0 | 0 | 39.2 | 414.7 | 81.0207
8739 | 41.3932 | 0 | 0 | 134.4 | 0 | 20.6966 | 0 | 0 | 0 | 42 | 438.8 | 78.2848
8740 | 41.2398 | 0 | 0 | 142.4 | 0 | 20.6199 | 0 | 0 | 0 | 44.6 | 458.1 | 75.6752
8741 | 42.9057 | 0 | 0 | 149.4 | 0 | 21.4528 | 0 | 0 | 0 | 46.1 | 475.4 | 80.8971
8742 | 41.9592 | 0 | 0 | 155.7 | 0 | 20.9796 | 0 | 0 | 0 | 47.4 | 488.3 | 78.1631
8743 | 56.8946 | 0 | 42.9 | 328.5 | 56.3 | 28.4473 | 0 | 0 | 0 | 63.5 | 1076.9 | 103.0599
8744 | 103.0486 | 0.7 | 43 | 384.3 | 37.6 | 51.5243 | 0 | 0 | 0 | 130.1 | 1041.6 | 119.8016
8745 | 210.3032 | 2.1 | 43.2 | 382.3 | 0 | 105.1516 | 0 | 0 | 0 | 138.9 | 459.3 | 123.5
8746 | 348.1146 | 3.5 | 43.4 | 394 | 0 | 174.0573 | 0 | 0 | 0 | 176.6 | 522.1 | 132.7883
8747 | 388.9735 | 3.5 | 43.4 | 386.2 | 0 | 194.4868 | 0 | 0 | 0 | 175.5 | 530.8 | 151.304
8748 | 371.2673 | 2.8 | 43.3 | 370.3 | 0 | 185.6337 | 0 | 0 | 0 | 149.3 | 537.6 | 154.1023
8749 | 363.3435 | 1.4 | 43.1 | 351.1 | 75.1 | 181.6718 | 0 | 0 | 0 | 108.3 | 1119.9 | 158.9423
8750 | 382.591 | 2.1 | 43.2 | 346.8 | 37.6 | 191.2955 | 0 | 0 | 0 | 114 | 1042.1 | 107.766
8751 | 430.5911 | 3.5 | 43.4 | 362.9 | 0 | 215.2956 | 0 | 0 | 0 | 145.1 | 460.6 | 192.3514
8752 | 417.6621 | 2.8 | 43.3 | 362.1 | 0 | 208.8311 | 0 | 0 | 0 | 144.2 | 538.3 | 198.9825
8753 | 358.5162 | 2.1 | 43.2 | 341.9 | 0 | 179.2581 | 0 | 0 | 0 | 122.2 | 547 | 197.6791
8754 | 263.5485 | 0.7 | 43 | 333.9 | 37.6 | 131.7742 | 0 | 0 | 0 | 79.1 | 1128.1 | 186.3891
8755 | 149.158 | 0 | 42.9 | 262.3 | 75.1 | 74.579 | 0 | 0 | 0 | 25.8 | 1079.8 | 182.3752
8756 | 82.1567 | 0 | 42.9 | 224.2 | 75.1 | 41.0784 | 0 | 0 | 0 | 20.7 | 978.3 | 229.5067
8757 | 53.3061 | 0 | 42.9 | 236.8 | 75.1 | 26.653 | 0 | 0 | 0 | 25.5 | 1019 | 205.6797
8758 | 42.3531 | 0 | 42.9 | 245 | 93.9 | 21.1765 | 0 | 0 | 0 | 28.2 | 1046.1 | 153.7472
8759 | 39.04 | 0 | 0 | 136.2 | 0 | 19.52 | 0 | 0 | 0 | 31 | 466.2 | 174.0564
8760 | 39.472 | 0 | 0 | 162.7 | 0 | 19.736 | 0 | 0 | 0 | 33.9 | 552.5 | 142.2557

## Conversion Techs
Technology name | Gas Boiler | Gas Boiler | RN HEX Out | HT-HP Plant | Air-Source Chiller | LT-DH HP DHW | LT-DH HP SP | Solar PV Roof | Oil Boiler | Oil Boiler | Air-Source HP | Air-Source HP | Cooling HEX | RN HEX In | DH HEX | DH HEX | Wood Boiler Plant
Capacity (kW)
Fixed investment cost (CHF) | 23494 | 0 | 0 | 623476 | 22000 | 23476 | 23476 | 8849 | 30175 | 0 | 45000 | 0 |  | 477000 |  |  | 658252
Variable investment cost (CHF/kW) | 274 | 0 | 300 | 938 | 800 | 538 | 538 | 1094 | 330 | 0 | 1800 | 0 | 500 | 300 | 300 | 0 | 929
Fixed O&M cost (CHF/year)
Fixed O&M cost (%/year) |  |  | 0.5 |  | 2 | 2 | 2 |  |  |  | 2 |  | 0.5 | 0.5 | 0.5 |  | 4
Variable O&M cost (CHF/kW/year) |  |  |  | 5 |  |  |  |  | 0.006 | 0
Variable O&M cost (CHF/kWh)
Input energy carrier | Gas | Gas | LT RN | Plant Wast Heat,Electricity | Electricity | Electricity,LT RN | Electricity,LT RN | Solar Roof | Oil | Oil | Electricity,Heat Ambient | Heat Ambient,Electricity | Electricity | Plant Wast Heat | HT DH | HT DH | Wood Pellets
Output energy carrier | Heat 30-40 °C | Heat 60-70 °C | Plant Waste Heat Export | HT DH | Cooling 10 - 20°C,Heat Ambient Export | Heat 60-70 °C | Heat 30-40 °C | Electricity | Heat 30-40 °C | Heat 60-70 °C | Heat 60-70 °C | Heat 30-40 °C | Cooling 10 - 20°C,LT RN | LT RN | Heat 60-70 °C | Heat 30-40 °C | HT DH
Output efficiency (%) | 98.00000 | 98.00000 | 100.00000 | 300.00000 | 200.00000,300.00000 | 250.00000 | 530.00000 | 20.00000 | 95.00000 | 95.00000 | 250.00000 | 400.00000 | 999.00000,1000.00000 | 100.00000 | 100.00000 | 100.00000 | 85.00000
Fixed input share (%) | 100.00000 | 100.00000 | 100.00000 | 100.00000,200.00000 | 100.00000 | 100.00000,150.00000 | 100.00000,430.00000 | 100.00000 | 100.00000 | 100.00000 | 100.00000,150.00000 | 100.00000,300.00000 | 1.00000 | 100.00000 | 100.00000 | 100.00000 | 100.00000
Lifetime (years) | 20 | 20 | 30 | 20 | 20 | 20 | 20 | 25 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 18
Maximum capacity (kW) | [13 empty] | 350
Minimum capacity (kW) | 50 | 50 |  | 5 | 5 | 5 | 5 | 10 | 50 | 50 | 5 | 5 | 5 |  |  |  | 50
Maximum Annual output (kWh/year)
Minimum Annual output (kWh/year)
Fixed Embodied CO2 (kg-CO2)
Variable Embodied CO2 (kg-CO2/kW)
Variable Embodied CO2 (kg-CO2/kWhOutput)
Variable Captured CO2 (kg-CO2/kWhInput)
Hubs | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Must Install | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N
At Least one Hub? | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N | N
Virtual technology | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seasonal operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology package
Database
Curtailment Limitation (%/kWp)
Time Varying Input Share?
Mutually Exclusive Group

## Storage Techs
Technology name | Generic Battery | Generic Borehole
Stored energy carrier | Electricity | LT RN
Capacity (kWh)
Fixed investment cost (CHF)
Variable investment cost (CHF/kWh) | 1200 | 2
Fixed O&M cost (CHF/year)
Fixed O&M cost (%/year)
Variable O&M cost (CHF/kWh/year) | 10
Lifetime (years) | 15 | 80
Maximum charging rate (%/hour) | 90 | 0.15
Maximum discharging rate (%/hour) | 90 | 0.15
Charging Efficiency (%) | 100 | 100
Discharging Efficiency (%) | 100 | 100
Standby loss (%/hour) | 0.001
Minimum SoC (%)
Maximum capacity (kWh) | 400
Minimum capacity (kWh)
Variable Embodied CO2 (kg-CO2/kWh)
Fixed Embodied CO2 (kg-CO2)
Hubs | 1 | 1
Must Install | N | N
At Least one Hub? | N | N
Technology package
Database
EV Plug-in Time
EV Plug-out Time
EV Plug-in Duration (Hours)
Driving Distance (kms)
EV SoC start (%)
EV Battery Size (kWh)
Maximum SoC (%)
EV Average kWh per km
EV Plug-in power (kW)
EV-battery? | N | N
Type of charging
Mutually Exclusive Group

## Network Techs
Technology name
Energy carrier
Network loss (%/m)
Fixed investment cost (CHF/m)
Variable investment cost (CHF/kW/m)
Fixed O&M cost (CHF/m/year)
Fixed O&M cost (%/m/year)
Variable O&M cost (CHF/kW/m/year)
Lifetime (years)
Maximum capacity (kW)
Minimum capacity (kW)
Variable Embodied CO2 (kg-CO2/kW/m)
Fixed Embodied CO2 (kg-CO2/m)
Database

## Network Path
Network Link ID
Network technology
Node 1
Node 2
Length (m)
Capacity (kW)
Must Install
Uni-directional flow? (Y/N)
Network Link GUID

## Custom Efficiencies
Conversion Technology | Energy Carrier | January | February | March | April | May | June | July | August | September | October | November | December
Gas Boiler | Heat 30-40 °C | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
Gas Boiler.1 | Heat 60-70 °C | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
RN HEX Out | Plant Waste Heat Export | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
HT-HP Plant | HT DH | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Air-Source Chiller | Cooling 10 - 20°C | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Air-Source Chiller | Heat Ambient Export | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
LT-DH HP DHW | Heat 60-70 °C | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
LT-DH HP SP | Heat 30-40 °C | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530
Solar PV Roof | Electricity | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Oil Boiler | Heat 30-40 °C | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Oil Boiler.1 | Heat 60-70 °C | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Air-Source HP | Heat 60-70 °C | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
Air-Source HP.1 | Heat 30-40 °C | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
Cooling HEX | LT RN | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Cooling HEX | Cooling 10 - 20°C | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999 | 999
RN HEX In | LT RN | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DH HEX | Heat 60-70 °C | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DH HEX.1 | Heat 30-40 °C | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Wood Boiler Plant | HT DH | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Custom Efficiencies Hourly
Conversion Technology
Energy Carrier

## Dynamic Tariff
Type
Energy carrier name
Dynamic Tariff Name
Price category
Price Dimension
Period

## Emission Profiles
Type
Energy carrier name
Emission Profile Name
Price Dimension
Period